## Add Data (hidden)
DO NOT EDIT | ADD / UPDATE DATA
Client Name | Client_name
Document Number | Document_No
Document_Revision | Document_Rev
IRS Revision | 0.1
Issue Month | September
Issue Year | 2019
Spec Revision Description | Issued for public review
Specification Number | S-703D
Specification Revision | 0.1
Suppl. Requirements No | S-703
Suppl. Requirements Descr. | Low Voltage Motors
Parent Standard Desc
Parent Standard Number | IEC 60034-1
Parent Standard Revision | Parent_Standard_Revision
Parent Standard Year | Parent_Standard_Year

## Guidance
S-703D Data Sheet for Low Voltage Three Phase Cage Induction Motors
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-703 Supplementary Specification to IEC 60034-1 Low Voltage Three Phase Cage Induction Motors
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specificaiton where relevant.
Default values (if applicable) are pre-populated in this data sheet, but may be modified as required by the user.
The Supplement sheet is is provided in an open format sheet for application of specific items not covered in the main part of the datasheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The datasheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.
IOGPS-703D Version 0.1
Public Review Draft

## Front & Preliminaries
|  |  |  | SPECIFICATION | September
|  |  |  | S-703D | 2019
Data Sheet for Low Voltage Three Phase Cage Induction Motors
Revision history
| VERSION | DATE | AMENDMENTS
| 0.1 | 16th September 2019 | Issued for public review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Project 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGPS-703D Version 0.1
Data Sheet for
Low Voltage Three Phase Cage Induction Motors
Foreword
This specification was prepared under a Joint Industry Programme 33 (JIP33) “Standardization of Equipment Specifications for Procurement” organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization for projects globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly approved specification, building on recognized industry and/or international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages, facilitating improved standardization of major projects across the globe. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focussed standardisation initiatives and provide step change benefits in the sector’s capital projects performance
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP’s Competition Law Guidelines (November 2014).
IOGPS-703D Version 0.1
Data Sheet for
Low Voltage Three Phase Cage Induction Motors
Introduction
The purpose of this equipment data sheet is to define buyer specific requirements for the supply of actuators for on-off valves, in accordance with IOGP S-703, for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This datasheet shall be used in conjunction with the supplementary requirements specification, information requirements specification (IOGP S-703L), quality requirements specification (IOGP S-703Q) which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet
IOGPS-703D Version 0.1
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Data Sheet
Row | [5 empty] | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  |  |  |  | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | General
6 |  | Manufacturer : |  | Input Data
7 |  | Model number : |  | Input Data
8 |  | Serial number : |  | Input Data
9 |  | Order status : |  | Select |  |  | Select | for enquiry | for purchase | for as-build
10 |  | Conformity Assessment System (CAS) level : |  | D |  |  | Select | A | B | C | D
11 |  | Frame size : |  | Select |  |  | Select | 56M | 63M | 71M | 80M | 90S | 90L | 100S | 100L | 112S | 112M | 132S | 132S | 132M | 160S | 160M | 160L | 180S | 180M | 180L | 200S | 200M | 200L | 225S | 225M | 250S | 250M | 280S | 280M | 315S | 315M | 355S | 355M | 355L | 400S | 400M | 400L
12 |  | Duty
13 | 4.1, 4.2.1, 4.2.10, 4.2.2, 4.2.3, 4.2.4, 4.2.5, 4.2.6, 4.2.7, 4.2.8, 4.2.9, 5.1, 5.3, 5.5.2 | Duty type : |  | S1 |  |  | Select | S1 | S9 | other
14 |  | Load drive : |  | Select |  |  | Select | direct | belt | gearbox | other
15 |  | Direction of rotation : |  | Select |  |  | Select | clockwise | counter-clockwise
16 |  | Rating
17 | 5.5.3, 5.5.3.1, 5.5.3.2, 5.8 | Rated output : |  | Select |  |  | Select | 0.12 | 0.18 | 0.25 | 0.37 | 0.55 | 0.75 | 1.1 | 1.5 | 2.2 | 3.7 | 5.5 | 7.5 | 11 | 15 | 18.5 | 22 | 30 | 37 | 45 | 55 | 75 | 90 | 110 | 132 | 160 | 200 | 250 | 315 | 335 | 355 | 275 | 400 | 425 | 450 | 475 | 500 | 530 | 560 | 600 | 630 | 670 | 710 | 750 | 800 | 850 | 900 | 950 | 1000 | other
18 |  | Current at rated output : | Input Data | A
19 |  | Site conditions
20 | 6.1 | Location Environment : |  | Select |  |  | Select | onshore – coastal | onshore – desert | onshore – inland | offshore – fixed | offshore – floating | marine (ship)
21 | 6.1, 6.2 | Altitude : | 1000 | m |  |  | Select | 1000 | other
22 | 5.5.3.1, 5.5.3.2, 6.1, 6.3 | Maximum ambient air temperature : | 40 | ºC |  |  | Select | 40 | 45 | 50 | other
23 | 6.1, 6.4 | Minimum ambient air temperature : | -15 | ºC |  |  | Select | -15 | -20 | -40 | -55 | other
24 | 6.6 | Transport and storage conditions : |  | within normal service conditions |  |  | Select | within normal service conditions | outwith normal service conditions - see comments box for details
25 | 6.6 | Longer periods of standstill : |  | No |  |  | Select | No | Yes
26 | 6.1, 6.3, 6.8 | Maximum relative humidity : | 100 | % |  |  | Select | 100 | 95 | 90 | other
27 | 6.9.1 | Machine ingress protection : |  | IP55 |  |  | Select | IP55 | IP56 | IP54 | IP44 | IP23 | other
28 | 6.1 | Impact protection : |  | IK08 |  |  | Select | IK08 | other
29 |  | Electrical operating conditions
30 | 7.3, 9.12.1.4, Figure 12, Table 1 | Supply voltage : | Select | V |  |  | Select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | other
31 | 7.3, Figure 12 | Supply frequency : | Select | Hz |  |  | Select | 50 | 60
32 | 7.2.1.1 | Total harmonic distortion : | 8 | % |  |  | Select | 8 | 10 | 5 | other
33 | 7.3, 9.12.1.4, Figure 12 | Minimum voltage limits : | Select | % |  |  | Select | -5 | -10 | -20 | other
34 | 7.3, 9.12.1.4, Figure 12 | Maximum voltage limits : | Select | % |  |  | Select | 5 | 10 | 20 | other
35 | 7.3, Figure 12 | Minimum frequency limits : | Select | % |  |  | Select | -2 | -5 | other
36 | 7.3, Figure 12 | Maximum frequency limits : | Select | % |  |  | Select | 2 | 3 | 5 | other
37 | 7.4 | System earthing : |  | TN-S |  |  | Select | TN-S | IT | TN-C | TN-C-S | TT | other
38 |  | Re-acceleration capability : |  | No |  |  | Select | No | Yes
39 | 9.3.1 | Occasional excess current : |  | No |  |  | Select | No | Yes (special condition to be agreed)
40 | 9.4.1 | High torque requirement : |  | No |  |  | Select | No | Yes (special condition to be agreed)
41 |  | Thermal performance
42 | 8.1 | Insulation class : |  | F |  |  | Select | F | H | other
43 | 8.1 | Temperature rise class : |  | B |  |  | Select | B | F | other
44 |  | Starting performance
45 | 9.12.1.1 | Starting designation : |  | NE |  |  | Select | NE | N | NY | NEY | H | HE | HY | HEY | other
46 | 9.5, Table 21 | Pull-up torque : | Input Data | N m
47 | 9.5 | Pull-up torque requirement : |  | 0.3 times the rated torque |  |  | Select | 0.3 times the rated torque | Other (special requirement to be agreed)
48 | 9.12.1.2, 9.12.1.3 | Locked-rotor current at 80% rated voltage : | Input Data | pu
49 | 9.12.1.2, 9.12.1.3 | Locked-rotor current at 100% rated voltage : | Input Data | pu
50 | Table 21 | Locked-rotor torque at 80% rated voltage : | Input Data | N m
51 | Table 21 | Locked-rotor torque at 100% rated voltage : | Input Data | N m
52 |  | Locked-rotor power factor : |  | Input Data
53 |  | Moment of inertia : | Input Data | kgm2
54 | 9.12.2.1, 9.12.2.2 | Hot consecutive starts : |  | 2 |  |  | Select | 2 | other
55 | 9.12.2.1, 9.12.2.2 | Cold consecutive starts : |  | 3 |  |  | Select | 3 | other
56 |  | Hot starting time : | Input Data | s
57 |  | Operating performance
58 | 9.6, Table 18 | Rated speed : | Input Data | r/min
59 | Table 21 | Full load torque : | Input Data | N m
60 | Table 21 | Breakdown torque : | Input Data | N m
61 |  | Efficiency at 100% rated output : | Input Data | %
62 |  | Efficiency at 75% rated output : | Input Data | %
63 |  | Efficiency at 50% rated output : | Input Data | %
64 |  | Power factor at 100% rated output : |  | Input Data
65 |  | Power factor at 75% rated output : |  | Input Data
66 |  | Power factor at 50% rated output : |  | Input Data
67 |  | Noise
68 | 9.13.1, 9.13.2, 9.13.3, 9.13.4 | Maximum noise limit : | as per IEC 60034-9 (not exceeding 90) | db (A) |  |  | Select | as per IEC 60034-9 (not exceeding 90) | 75 | 77 | 80 | other
69 |  | Maximum noise at no load : | Input Data | db(A)
70 |  | Maximum noise at rated load condition : | Input Data | db(A)
71 | 9.13.1, 9.13.2, 9.13.3, 9.13.4 | Noise type test report : |  | No |  |  | Select | No | Yes
72 |  | Machine construction
73 |  | Machine weight : | Input Data | kg
74 |  | Rotor
75 | 11.3.2.1, 11.3.2.2, 11.3.3.2 | Maximum vibration magnitude : |  | vibration grade A |  |  | Select | vibration grade A | vibration grade B
76 |  | Fan
77 | 11.3.3.1 | Fan impeller material : |  | GRP |  |  | Select | GRP | Steel fan | other
78 | 11.3.3.2 | Fan direction of rotation : |  | Select |  |  | Select | bi-directional, uni-directional clockwise | unidirectional counter-clockwise
79 |  | Terminal box
80 | 11.3.4.1 | Location : |  | Select |  |  | Select | top | right | left
81 | 6.9.1 | Ingress protection : |  | IP55 |  |  | Select | IP55 | IP56 | other
82 | 11.3.4.4, 11.3.4.6 | Line conductor terminal box cable gland entries : | Input Data | Input Data
83 |  | Large terminal box : |  | No |  |  | Select | No | Yes
84 |  | Bearings
85 | 11.3.5.1, 11.3.5.3 | D-end bearing type : |  | Input Data
86 | 11.3.5.1, 11.3.5.3 | N-end bearing type : |  | Input Data
87 | 11.3.5.2 | Internal clearance : |  | C3 |  |  | Select | C3 | other
88 | 11.3.5.1 | Lubrication specification : |  | Input Data
89 |  | Space heaters
90 | 11.3.6.1, 11.3.6.2, 11.3.6.3, 11.3.6.4, 11.3.6.5, 11.3.6.6 | Heater requirement : |  | no - unless advised by manufacturer |  |  | Select | no - unless advised by manufacturer | yes
91 | 7.3 | Supply voltage : | Select | V |  |  | Select | 100-120 | 200-240
92 | 11.9.3.2 | Separate terminal box : |  | Select |  |  | Select | No | Yes
93 |  | Mounting
94 | 11.4.1, 11.4.2 | Mounting : |  | Select |  |  | Select | IM B3 (IM 1001) | IM B5 (IM 3001) | IM V1 (IM 3011) | IM V6 (IM 1031) | other
95 |  | Cooling
96 | 11.5 | Cooling method : |  | IC4A1A1 |  |  | Select | IC4A1A1 | other
97 |  | Efficiency
98 | 11.6.1, 11.6.2 | Efficiency : |  | IE3 |  |  | Select | IE3 | IE2 | IE4 | IE1
99 |  | Vibration
100 | 11.3.5.4, 11.7 | Vibration monitoring : |  | none |  |  | Select | none | SPM nipples
101 | 11.3.2.1, 11.3.2.2 | Vibration level test report : |  | No |  |  | Select | No | Yes
102 |  | Surface finish
103 | 11.8.1, 11.8.2 | Surface protection corrosivity category : |  | Select |  |  | Select | C3 | C4 | C5 | Norsok M501 | other
104 | 11.8.3 | Surface protection durability category : |  | medium |  |  | Select | medium | high | very high.
105 |  | Surface finish : |  | manufacturer's standard |  |  | Select | manufacturer's standard | other
106 |  | Temperature monitoring
107 | 11.9.3.1, 11.9.3.2 | Winding temperature detection : |  | none |  |  | Select | none | PTC see comment | Pt100 see comment
108 |  | Machines intended for use with adjustable speed drives
109 | 11.9.1, 11.9.2 | Adjustable speed drive : |  | No |  |  | Select | No | Yes
110 | 15.3.1, 15.3.2 | ASD manufacturer : |  | Input Data
111 | 15.3.1, 15.3.2 | ASD model number : |  | Input Data
112 |  | Minimum operating speed : | Input Data | rpm
113 |  | Maximum operating speed : | Input Data | rpm
114 | 9.6 | Fine balancing above rated speed : |  | No |  |  | Select | No | Yes
115 | 9.7 | Overspeed testing required : |  | No |  |  | Select | No | Yes
116 |  | Machines intended for use in potentially explosive atmospheres
117 | 15.1.1, 15.1.2 | Hazardous area certifying body : |  | Select |  |  | Select | ATEX Directive, IECEx | EAC | none
118 | 15.1.1, 15.1.3 | Temperature group : |  | T3 |  |  | Select | T3 | T4 | T5 | T6 other
119 | 15.1.1, 15.1.3 | Gas group : |  | IIB |  |  | Select | IIB | II | IIC | IIB+H2
120 | 15.1.2, 15.1.3 | Equipment protection level : |  | Select |  |  | Select | EPL Ga | EPL Gb | EPL Gc | EPL Da | EPL Db | EPL Dc
121 | 15.1.4, 15.2.1 | Machine classification : |  | Select |  |  | Select | None | Ex db | Ex ec | Ex eb | Ex db eb
122 |  | Miscellaneous
123 |  | Provision for IoT hardware installation : |  | Select |  |  | Select | Yes | No
Public Review Draft
Public Review Draft
Note on C6: Confirm machine manufacturer
Note on C7: Confirm machine model number
Note on C8: Confirm machine model number
Note on C9: Advise order status, this shall allow both purchaser and manufacturer to more accurately define values as they become available.
Note on C10: Select CAS level as applied in S-703Q, Annex A
Note on C11: Confirm machine frame size according to IEC 60072-1
Note on C13: Advise duty type as defined in IEC-60034-1 Section 4.
Note on C14: Advise method of connection to load for which machine shall be rated. Consideration to be given to bearings where axial loading is in excess of standard bearing specification.
Note on C15: The direction of rotation shall be that of the shaft observed when facing the D-end with connection according to IEC 60034-8 Annex A.
Note on C17: Advise rated power output according to load requirements.
Note on C18: Confirm current which the machine requires whilst operating at rated torque and slip.
Note on C20: Advise location machine shall be situated as per the options available
Note on C21: Advise maximum altitude which machine shall be rated.
Note on C22: Advise maximum ambient air temperature which machine shall be rated.
Note on C23: Advise minimum ambient air temperature which machine shall be rated.
Note on C24: Manufacturer to provide details of where transportation and storage conditions are out with those detailed by the Purchaser as site conditions. The manufacturer take measures to ensure these do not affect the integrity of the machine.
Note on C25: Purchaser to advise when periods of standstill or storage or transport which exceed 6 months are anticipated, as described in IEC 60034-1 Section 6.6.
Note on C26: Advise maximum relative humidity, at maximum ambient air temperature defined in this data sheet, for which machine shall be rated.
Note on C27: Advise ingress protection value according to IEC 60034-5 for which machine shall be rated
Note on C28: Select IK code for impact protection with regards to impact energy according to IEC 62262
Note on C30: Advise supply voltage for which machine shall be rated for.
Note on C31: Advise supply frequency for which machine shall be rated for.
Note on C32: Advise potential total harmonic distortion prevalent in electrical supply for which machine shall be rated to operate.
Note on C33: Advise minimum voltage limits as a percentage of supply voltage for which machine shall be rated.
Note on C34: Advise maximum voltage limits as a percentage of supply voltage for which machine shall be rated
Note on C35: Advise minimum frequency limits as a percentage of supply frequency for which machine shall be rated.
Note on C36: Advise maximum frequency limits as a percentage of supply voltage for which machine shall be rated. Note "+5%" is as per IEC 61892 referring to stationary limits for island networks.
Note on C37: Advise method of earthing arrangement as described in IEC 60364
Note on C38: Advise whether supply has fast re-closing/bus transfer capability which causes machine to re-accelerate without coming to standstill.
Note on C39: Advise where the machine is likely to be exposed to occasional excess current. As described in IEC-60034-1 Section 9.3.1 this is where the excess current exceeds a few short periods during the life time of the machine.
Note on C40: Where motors intended for specific applications that require a torque higher than that described in IEC-60034-1 Section 9.4.1, special conditions shall be agreed between the purchaser and the manufacturer.
Note on C42: Advise insulation class of machine according to IEC 60085
Note on C43: Advise temperature rise class of machine according to IEC 60085
Note on C45: Advise starting designation according to IEC 60034-12 for which machine shall be rated.
Note on C46: Confirm the smallest steady-state asynchronous torque which the motor develops between zero speed and the speed which corresponds to the breakdown torque, when the motor is supplied at the rated voltage and frequency
Note on C47: The purchaser shall specify when special conditions allow the pull-up torque of the machine to be less than 0.3 times the rated torque, as per IEC 60034-1 Section 9.5
Note on C48: Confirm greatest steady-state r.m.s. current taken from the line with the motor held at rest, over all angular positions of its rotor, at 80% rated voltage and frequency, expressed as a per unit value of full load current (Is/In)
Note on C49: Confirm greatest steady-state r.m.s. current taken from the line with the motor held at rest, over all angular positions of its rotor, at 100% rated voltage and frequency, expressed as a per unit value of full load current (Is/In)
Note on C50: Confirm smallest measured torque the motor develops at its shaft and with the rotor locked, over all its angular positions, at rated frequency and 80% rated voltage.
Note on C51: Confirm smallest measured torque the motor develops at its shaft and with the rotor locked, over all its angular positions, at rated frequency and 100% rated voltage
Note on C52: Confirm power factor with the rotor locked, over all its angular positions, at rated voltage and frequency
Note on C53: Advise moment of inertia as defined in IEC 60034-1 Section 3
Note on C54: Advise the amount of starts in succession (coasting to rest between starts) from maximum ambient temperature the machine shall be capable of making whilst hot.
Note on C55: Advise the amount of starts in succession (coasting to rest between starts) from maximum ambient temperature the machine shall be capable of making whilst hot.
Note on C56: Confirm the maximum allowable duration of time for the machine to reach its rated speed at 100% rated voltage respectively whilst the machine is hot.
Note on C58: Confirm maximum speed which the rotor rotates whilst operating with rated voltage, frequency and at rated load.
Note on C59: Confirm maximum torque which the machine develops with rated voltage, frequency and field current.
Note on C60: Confirm maximum steady-state asynchronous torque which the motor develops without an abrupt drop in speed, when the motor is supplied at the rated voltage and frequency.
Note on C61: Confirm efficiency of machine whilst operating at 100% of its rated output value.
Note on C62: Confirm efficiency of machine whilst operating at 75% of its rated output value.
Note on C63: Confirm efficiency of machine whilst operating at 50% of its rated output value.
Note on C64: Confirm the cosine of the angle between active power and apparent power when the machine is operated at 100% rated power.
Note on C65: Confirm the cosine of the angle between active power and apparent power when the machine is operated at 75% rated power.
Note on C66: Confirm the cosine of the angle between active power and apparent power when the machine is operated at 50% rated power.
Note on C68: Maximum A-weighted sound power level, in dB(A), in accordance with IEC 60034-9 at no load.
Note on C69: Manufacturer declared A-weighted sound power level, in dB(A), in accordance with IEC 60034-9 at no load.
Note on C70: Manufacturer declared A-weighted sound power level, in dB(A), in accordance with IEC 60034-9 at rated load condition, calculated in accordance with IEC 60034-9 Table 3.
Note on C71: Purchaser to advise if noise type test report is required.
Note on C73: Confirm fully assembled weight of machine
Note on C75: Specify limits of maximum vibration magnitude defined in IEC 60034-14 Table 1.
Note on C77: Advise material from which fan impeller shall be constructed
Note on C78: Supplier to advise fan specification with regards to direction of rotation.
Note on C80: Advise location of terminal box.in accordance with IEC 60034-7
Note on C81: Advise ingress protection value according to IEC 60034-5 for which terminal box shall be rated
Note on C82: Confirm amount and size of cable gland entries in terminal box e.g. 1 x M32, 2 x M20
Note on C83: Advise where a larger than standard terminal box is necessary due to cables, larger than that anticipated in the standard terminal box specification, are required.
Note on C85: Confirm drive end bearing model number.
Note on C86: Confirm non-drive end bearing model number.
Note on C87: Advise internal clearance of bearing according to ISO 5753-1 Table 1. C3 refers to normal clearance as commonly used to avoid too little internal bearing clearance for low voltage motors.
Note on C88: Confirm approved lubrication specification for re-greasable bearings to be used when performing maintenance.
Note on C90: Default selection is that no space heaters shall be provided, unless advised by the manufacturer that space heaters are necessary at the defined site conditions.
Note on C91: Advise supply voltage for which heater shall be rated for.
Note on C92: Advise whether a separate terminal box is required for space heater power supply. Note: This option may not be available on certain frame sizes.
Note on C94: Advise mounting arrangement according to IEC 60034-7 for which machine shall be selected.
Note on C96: Advise machine cooling method as defined in IEC 60034-6.
Note on C98: Advise efficiency category according to IEC 60034-6 for which machine shall be rated.
Note on C100: Advise if there is a requirement for a vibration monitoring connection point to be provided.
Note on C101: Purchaser to advise if vibration test report is required.
Note on C103: Advise surface corrosivity category in accordance with ISO 12944-2 Section 5.1.1. Norsok M501 shall ensure it's requirements are achieved irrespective of ISO 12944.
Note on C104: Advise surface durabilityt category in accordance with ISO 12944-2 Section 5.5
Note on C105: Advise surface finish requirement with regards to colour.
Note on C107: Advise on requirement for embedded temperature detection in the stator windings
Note on C109: Advise whether the machine's speed shall be controlled by an adjustable speed drive.
Note on C110: Confirm manufacturer of ASD from which the machine shall be driven
Note on C111: Confirm model number of ASD from which the machine shall be driven.
Note on C112: Advise minimum operating speed for which the machine shall be rated in normal operation.
Note on C113: Advise maximum operating speed for which the machine shall be rated in normal operation.
Note on C114: Purchaser to advise if fine balancing of rotor shaft is required for high speed applications.
Note on C115: Advise when overspeed testing is required as per IEC 60034-1 Section 9.7
Note on C117: Advise which certification or notified body shall be accepted for machines to be located in a hazardous area.
Note on C118: Advise temperature group according to IEC 60079-0 for which machine shall be rated.
Note on C119: Advise gas group according to IEC 60079-0 for which machine shall be rated.
Note on C120: Advise equipment protection level (EPL) according to IEC 60079-14
Note on C121: Advise classification according to IEC 60079 for which machine shall be rated.
Note on C123: Where the supplier offers IoT hardware which shall be attached to the machine, mounting points and all other provisions shall be made to facilitate this. Note: This may be to allow the IoT system to be procured at a later date.

## Supplement
Row |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required.
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
54
55
56
60
61
62
Public Review Draft

## Backcover
Public Review Draft