## Guidance
S-718D Data Sheet for
Field Instruments - Electronic Transmitters
Pressure, Differential Pressure and Temperature
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-718 Supplementary Specification to ANSI/API Recommended Practice 551 Process Measurement.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) are pre-populated in this data sheet, but may be modified as required by the user.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.
IOGP S-718D Version 0.1
Public Review Draft

## Front & Preliminaries
|  |  |  | SPECIFICATION | October
|  |  |  | S-718D | 2019
Data Sheet for Field Instruments
Electronic Transmitters - Pressure,
Differential Pressure and Temperature
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | 9th October 2019 | Issued for 3rd Party Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Project 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-718D Version 0.1
S-718D Data sheet for
Field Instruments - Electronic Transmitters
Pressure, Differential Pressure and Temperature
Foreword
This specification was prepared under a Joint Industry Programme 33 (JIP33) “Standardization of Equipment Specifications for Procurement” organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization for projects globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly approved specification, building on recognized industry and/or international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages, facilitating improved standardization of major projects across the globe. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focussed standardisation initiatives and provide step change benefits in the sector’s capital projects performance
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP’s Competition Law Guidelines (November 2014).
IOGP S-718D Version 0.1
S-718D Data sheet for
Field Instruments - Electronic Transmitters
Pressure, Differential Pressure and Temperature
Introduction
The purpose of this equipment data sheet is to define buyer specific requirements for the supply of field instruments, in accordance with IOGP S-718, for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-718, information requirements specification IOGP S-718L and quality requirements specification IOGP S-718Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet
IOGP S-718D Version 0.1
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## General
Row | S-718D Data Sheet for Field Instruments - Electronic Transmitters Pressure, Differential Pressure and Temperature | [8 empty] | Issue
2 | Tag No. : |  | Insert Tag Number
3 | Service : |  | Insert Service Description | [7 empty] | Default
4 | Ref. Clause | Description | Requirement | [5 empty] | Additional notes
5 |  | Pressure Transmitter
6 |  | General
7 |  | Type : | [5 empty] | Input Data | Pressure transmitter (gauge pressure or absolute pressure)
8 |  | Tag number : | [5 empty] | Input Data | Fill up the unique tag number of the transmitter as indicated in P&ID
9 |  | Manufacturer : | [5 empty] | Input Data | Provide manufacturer's name after package evaluation, but prior to purchase order
10 |  | Model number : | [5 empty] | Input Data | Provide prior to purchase order
11 |  | Service description : | [5 empty] | Input Data | Operational purpose of this transmitter as indicated in P&ID
12 |  | P&ID number : | [5 empty] | Input Data | P&ID number where the transmitter is indicated
13 |  | Line/equipment number : | [5 empty] | Input Data | Piping, vessel or equipment where the transmitter is connected for measurement purpose
14 |  | Plant area : | [5 empty] | Input Data | Geographical area of the plant where the transmitter is installed.
15 |  | Hazardous area classification zone : | [5 empty] | Input Data | Define as per project hazardous area classification layout: example Zone 2
16 |  | Hazardous area classification gas group : | [5 empty] | Input Data | Define as per project hazardous area classification layout: example Gas Group IIA
17 |  | Hazardous area classification temperature class : | [5 empty] | Input Data | Define as per project hazardous area temperature class: example T3
18 |  | Min Ambient Temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
19 |  | Max Ambient Temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
20 |  | Process Conditions
21 |  | Process fluid : | [5 empty] | Input Data | Process fluid according to process data sheet
22 |  | Fluid state : | [5 empty] | Input Data | Input as per process data
23 |  | Viscosity : |  |  |  |  | Input Data | Select | Input as per process data |  | Select | cP | cS
24 |  | Specific gravity : | [5 empty] | Input Data | Input as per process data
25 |  | Minimum operating temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
26 |  | Normal operating temperature : |  |  |  |  | Input Data | Select | Normal operating temperature as per process data sheet |  | Select | °C | °F
27 |  | Maximum operating temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
28 |  | Design temperature : |  |  |  |  | Input Data | Select | Input as per process data |  | Select | °C | °F
29 |  | Minimum operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig | kPag
30 |  | Normal operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig
31 |  | Maximum operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig
32 | 3.5 | Design pressure : |  | Input Data | Select | to | Input Data | Select | Input minimum/maximum design pressure as per process data sheet; minimum design pressure will include full vacuum condition. |  | Select | barg | psig | Select | barg | psig
33 |  | Instrument Characteristics
34 | 3.3.1 | Calibrated range : |  | Input Data | Select | to | Input Data | Select | To cover the lower and upper operating pressure values (LRV and URV) measured by the transmitter, corresponding to 4 - 20 mA output signal. |  | Select | barg | psig | Select | barg | psig
35 | 5.4.3 | Accuracy : |  |  |  |  | Input Data | % | Accuracy as a percentage of specified span.
36 |  | Lower / upper range limits : |  | Input Data | Select | to | Input Data | Select | Instrument range selection to cover the minimum and the maximum design pressures. |  | Select | barg | psig | Select | barg | psig
37 | 5.3 | Overpressure protect to : | [5 empty] | Input Data | Overpressure protection provided by the transmitter in compliance to regulatory requirements such as the Pressure Equipment Directive (PED) for the EU region. N/A if not applicable.
38 |  | Element / Sensor
39 |  | Type : |  |  |  |  | Select | Select | To specify conventional diaphragm sensor or diaphragm seal type. Type of sensor technology example capacitance, inductance and piezoelectric etc. is not required. |  | Select | Conventional diaphragm | Select | Diaphragm seal
40 | 3.6.1 , 3.6.2 , 3.6.2 , 3.6.7 | Material, element (sensor) : | [5 empty] | Input Data | Material of diaphragm or bellow (wetted part). N/A if diaphragm seal type is selected.
41 | 3.6.2 , 3.6.2 , 3.6.7 | Material, socket (inlet port) : | [5 empty] | Input Data | Material of socket inlet port (wetted part). N/A if diaphragm seal type is selected.
42 |  | Material, sensor bolts / nuts : | [5 empty] | Input Data | Bolts and nuts material of the transmitter sensor (on the co-planar flange). N/A if diaphragm seal type is selected.
43 | 5.3 | Process connection type : | [5 empty] | Input Data | Transmitter connection at 2-valve manifold (NPT threaded) or flanged. N/A if diaphragm seal is selected.
44 | 5.3 | Process connection size : |  |  |  |  | Input Data | Select | Threaded connection size or flange size. N/A if diaphragm seal is selected. |  | Select | mm | in
45 | 5.3 | Process connection rating : |  |  |  |  | Input Data | Select | Input the flange rating as per piping specification. N/A if diaphragm seal is selected. |  | Select | lb | ANSI
46 | 3.6.5.2 , 3.6.5.3 | Sour service specification : | [5 empty] | Input Data | Specify NACE MR0175 if required or N/A for not applicable.
48 |  | Housing
49 |  | Weight : |  |  |  |  | Input Data | Select | Weight of the transmitter complete with co-planar manifold or remote diaphragm seal |  | Select | kg | lb
50 | 3.13.2 | Material : | [5 empty] | Input Data | Material of transmitter enclosure
51 | 3.13.3 | Cable entry : | [5 empty] | Input Data | Size of cable gland connection to the transmitter; 1/2-14 NPT or ISO M20 x 1.5
52 | 3.13.1 | Environmental protection : | [5 empty] | Input Data | Weather / ingress rating in IP or NEMA
53 | 3.13.4 | Ex protection : | [5 empty] | Input Data | Electrical protection for the specified hazardous area, example Ex ia, Ex d etc.
54 | 3.13.4 | Ex certification : | [5 empty] | Input Data | Electrical protection certification in accordance with testing requirements specified by ATEX, CSA, IECEx or FM.
55 |  | Protective coating : | [5 empty] | Input Data | Specify the required project painting and coating specification, "Mfr. Std." if manufacturer's standard, or "N/A" if painting is not required
57 |  | Transmitter
58 | 3.9.3 | Indicator : | [5 empty] | Input Data | Specify "integral LCD display", "remote indicator" or "N/A" if blind transmitter.
59 | 3.7.1 , 3.7.1 | Output signal : |  |  | Input Data | to | Input Data | mA | Normally 4 to 20 mA output signal or digital output signal such as fieldbus.
60 | 3.7.3 | Communication : | [5 empty] | Input Data | Normally HART protocol version 7, Foundation Fieldbus or Profibus.
61 | 3.8.1 | Supply voltage : |  |  |  |  | Input Data | V DC | Generally 24V DC loop power
62 |  | Consumption : |  |  |  |  | Input Data | mW | Power consumption of the transmitter in mW
63 |  | Load limitation : |  |  |  |  | Input Data | Ω | Resistance introduced into the loop by the transmitter
64 | 3.13.10 | SIL certificate requirement : | [5 empty] | Select | "Yes" for transmitters used in SIF loops. "No" for transmitters in other applications. |  | Select | Yes | No
65 | 5.4.4.2 | Transmitter response time : |  |  |  |  | Input Data | ms | Transmitter's response time from the moment of sensing pressure change till signal output. Generally within 1 sec unless otherwise specified for special applications such as HIPPS or compressor anti-surge control.
66 |  | Fail direction : |  |  |  |  | Select | Select | Specific requirement to specify the fail direction for transmitters. |  | Select | Fail high | Select | Fail low
67 | 3.13.9 | Vibration resistance : | [5 empty] | Select | Indicate if seismic effect and vibration resistance according to IEC 60770-1 is required. |  | Select | Yes | No
68 |  | Other : | [5 empty] | Input Data | Other requirement (if any)
69 |  | Chemical Seal
70 | 9.2 | Type : |  |  |  |  | Select | Select | "Close coupled" for direct mount or "remote seal" for installation on mounting stand with capillary. N/A if manifold and impulse tubing is selected. |  | Select | Close coupled | Select | Remote seal
71 | 3.6.2 , 3.6.5.2 , 3.6.5.3 , 3.6.7 | Material upper/lower part : | [5 empty] | Input Data | 316 SS or Hastelloy C-276 are standard, depending on the process fluids
72 |  | Material, bolts / nuts : | [5 empty] | Input Data | Bolts and nuts material of the chemical seal.
73 | 3.6.5.2 , 3.6.5.3 , 3.6.7 , 9.2.1 | Material, diaphragm : | [5 empty] | Input Data | Wetted part material to be suitable for process fluids requirement, normally 316 SS or Hastelloy C-276
74 | 9.2.4 | Fill fluid : | [5 empty] | Input Data | Silicon or glycerin are standard, subject to operating temperature of the process
75 | 9.2.3 | Capillary length : |  |  |  |  | Input Data | m | As required for remote installation of the pressure transmitter; N/A if direct mount
76 | 9.2.3 | Material capillary / armour : | [5 empty] | Input Data | To be suitable for the ambient conditions; N/A if direct mount
77 | 5.3 , 9.2.2 | Process connection size : |  |  |  |  | Input Data | Select | 1/2 inch for threaded connection, 2 inch or 3 inch for flanged connection |  | Select | in | mm
78 | 5.3 , 9.2.1 | Process connection type : | [5 empty] | Input Data | Threaded NPT or flanged RF
79 |  | Process connection rating : |  |  |  |  | Input Data | Select | Input the diaphragm flange rating as per piping specification. |  | Select | lb | ANSI
80 | 9.2.1 | Flushing ring : | [5 empty] | Select | Select "Yes" if required for cleaning and calibration; "No" if not required |  | Select | Yes | No
81 |  | Gold plating : | [5 empty] | Select | Select "Yes" if special gold plating on diaphragm surface is required (for hydrogen service); select "No" if not required. |  | Select | Yes | No
82 |  | Other : | [5 empty] | Input Data | Additional requirement (if any) such as "Extended diaphragm seal" to flush with the internal wall of vessel; N/A if none
83 |  | Manifold
84 | 3.13.7 | Manifold type : | [5 empty] | Input Data | "2 way" manifold valve is normally specified for pressure transmitter applications with tubing impulse line. N/A if chemical seal is selected.
85 |  | Connection size : |  |  |  |  | Input Data | Select | Normally 1/2 inch NPT, inlet male (M), outlet female (F) |  | Select | in | mm
86 |  | Outlet material : | [5 empty] | Input Data | Normally 316L SS minimum to meet process requirements
87 |  | Manufacturer : | [5 empty] | Input Data | Information shall be provided by supplier in his offer
88 |  | Model number : | [5 empty] | Input Data | Information shall be provided by supplier in his offer
89 |  | Process flange type : | [5 empty] | Input Data | Standard is "coplanar" flange
90 |  | Flange material : | [5 empty] | Input Data | Normally 316L SS minimum to meet process requirements
91 |  | O-ring : | [5 empty] | Input Data | O-ring material to meet specified process requirements; standard is "glass-filled PTFE"
92 |  | Accessories
93 |  | Mounting bracket : | [5 empty] | Select | "Yes" if remote mount; "No" if direct mount |  | Select | Yes | No
94 |  | Material, mounting bracket : | [5 empty] | Input Data | Normally 316L SS at ambient conditions; N/A if not required
95 | 3.8.3 | Electrical surge protector : | [5 empty] | Select | Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. |  | Select | Yes | No
96 | 3.13.8 | Sunshade : | [5 empty] | Select | Protection of transmitter against direct exposure to sun causing problems to its operation. |  | Select | Yes | No
97 |  | Other : | [5 empty] | Input Data | Other accessories (such as surge protection) to be added, if required
99 |  | Differential Pressure Transmitter
100 |  | General
101 |  | Type : | [5 empty] | Input Data | Select application type : differential pressure (DP), DP flow or DP level measurement.
102 |  | Tag number : | [5 empty] | Input Data | Fill up the unique tag number of the transmitter as indicated in P&ID
103 |  | Manufacturer : | [5 empty] | Input Data | Provide manufacturer's name after package evaluation, but prior to purchase order
104 |  | Model number : | [5 empty] | Input Data | Provide prior to purchase order
105 |  | Service description : | [5 empty] | Input Data | Operational purpose of this transmitter as indicated in P&ID
106 |  | P&ID number : | [5 empty] | Input Data | P&ID number where the transmitter is indicated
107 |  | Line/equipment number : | [5 empty] | Input Data | Piping, vessel or equipment where the transmitter is connected for measurement purpose
108 |  | Plant area : | [5 empty] | Input Data | Geographical area of the plant where the transmitter is installed.
109 |  | Hazardous area classification zone : | [5 empty] | Input Data | Define as per project hazardous area classification layout: example Zone 2
110 |  | Hazardous area classification gas group : | [5 empty] | Input Data | Define as per project hazardous area classification layout: example Gas Group IIA
111 |  | Hazardous area classification temperature class : | [5 empty] | Input Data | Define as per project hazardous area temperature class: example T3
112 |  | Min Ambient Temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
113 |  | Max Ambient Temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
114 |  | Process Conditions
115 |  | Process fluid : | [5 empty] | Input Data | Process fluid according to process data sheet
116 |  | Fluid state : | [5 empty] | Input Data | Input as per process data
117 |  | Minimum operating differential pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet. |  | Select | bar | psi | kPa
118 |  | Normal operating differential pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | bar | psi | kPa
119 |  | Maximum operating differential pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | bar | psi | kPa
120 |  | Viscosity : |  |  |  |  | Input Data | Select | Input as per process data |  | Select | cP | cS
121 | 7.3.2.2 | Upper density : |  |  |  |  | Input Data | kg/m³ | For DP level measurement only, to define the upper fluid density. N/A if not applicable.
122 | 7.3.2.2 | Lower density : |  |  |  |  | Input Data | kg/m³ | For DP level measurement only, to define the lower fluid density. N/A if not applicable.
123 |  | Specific gravity : | [5 empty] | Input Data | Input as per process data
124 |  | Minimum operating temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
125 |  | Normal operating temperature : |  |  |  |  | Input Data | Select | Normal operating temperature as per process data sheet |  | Select | °C | °F
126 |  | Maximum operating temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
127 |  | Design temperature : |  |  |  |  | Input Data | Select | Input as per process data |  | Select | °C | °F
128 |  | Minimum operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig | kPag
129 |  | Normal operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig
130 |  | Maximum operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig
131 |  | Design pressure : |  | Input Data | Select | to | Input Data | Select | Input minimum/maximum design pressure as per process data sheet; minimum design pressure will include full vacuum condition. |  | Select | barg | psig | Select | barg | psig
132 |  | Instrument Characteristics
133 |  | Calibrated DP range : |  | Input Data | Select | to | Input Data | Select | To cover the lower and upper operating differential pressure (DP) values (LRV and URV) measured by the transmitter, corresponding to 4 - 20 mA output signal. |  | Select | bar | psi | Select | bar | psi
134 |  | Accuracy of measured value : |  |  |  |  | Input Data | % | Accuracy as a percentage of specified span.
135 |  | Lower / upper range limits : |  | Input Data | Select | to | Input Data | Select | Instrument range selection to cover the minimum and the maximum design static pressures. |  | Select | barg | psig | Select | barg | psig
136 |  | Overpressure protect to : | [5 empty] | Input Data | Overpressure protection provided by the transmitter in compliance to regulatory requirements such as the Pressure Equipment Directive (PED) for the EU region. N/A if not applicable.
137 |  | Zero suppression / elevation : | [5 empty] | Input Data | For DP level measurement only to indicate the zero reference. Indicate "Suppression" , "Elevation" or "N/A".
138 |  | Element / Sensor
139 |  | Type : | [5 empty] | Select | To specify conventional diaphragm sensor or diaphragm seal type. |  | Select | conventional diaphragm | diaphragm seal
140 | 3.6.2 | Material, element (sensor) : | [5 empty] | Input Data | Material of diaphragm or bellow (wetted part). N/A if diaphragm seal type is selected.
141 | 3.6.2 | Material, socket (inlet port) : | [5 empty] | Input Data | Material of socket inlet port (wetted part). N/A if diaphragm seal type is selected.
142 |  | Material, sensor bolts / nuts : | [5 empty] | Input Data | Bolts and nuts material of the transmitter sensor (on the co-planar flange). N/A if diaphragm seal type is selected.
143 |  | Process connection type : | [5 empty] | Input Data | Transmitter connection at 2-valve manifold (NPT threaded) or flanged. N/A if diaphragm seal is selected.
144 |  | Process connection size : |  |  |  |  | Input Data | Select | Threaded connection size or flange size. N/A if diaphragm seal is selected. |  | Select | mm | in
145 |  | Process connection rating : |  |  |  |  | Input Data | Select | Input the flange rating as per piping specification. N/A if diaphragm seal is selected. |  | Select | lb | ANSI
146 |  | Sour service specification : | [5 empty] | Input Data | Specify NACE MR0175 if required or N/A for not applicable.
148 |  | Housing
149 |  | Weight : |  |  |  |  | Input Data | Select | Weight of the transmitter complete with co-planar manifold or remote diaphragm seal |  | Select | kg | lb
150 |  | Material : | [5 empty] | Input Data | Material of transmitter enclosure
151 |  | Cable entry : | [5 empty] | Input Data | Size of cable gland connection to the transmitter; 1/2-14 NPT or ISO M20 x 1.5
152 |  | Environmental protection : | [5 empty] | Input Data | Weather / ingress rating in IP or NEMA
153 |  | Ex protection : | [5 empty] | Input Data | Electrical protection for the specified hazardous area, example Ex ia, Ex d etc.
154 |  | Ex certification : | [5 empty] | Input Data | Electrical protection certification in accordance with testing requirements specified by ATEX, CSA, IECEx or FM.
155 |  | Protective coating : | [5 empty] | Input Data | Specify the required project painting and coating specification, "Mfr. Std." if manufacturer's standard, or "N/A" if painting is not required
157 |  | Transmitter
158 | 3.9.3 | Indicator : | [5 empty] | Input Data | Specify "integral LCD display", "remote indicator" or "N/A" if blind transmitter.
159 | 3.7.1 , 3.7.1 | Output signal : |  |  | Input Data | to | Input Data | mA | Normally 4 to 20 mA output signal or digital output signal such as fieldbus.
160 | 3.7.3 | Communication : | [5 empty] | Input Data | Normally HART protocol version 7, Foundation Fieldbus or Profibus.
161 | 3.8.1 | Supply voltage : |  |  |  |  | Input Data | V DC | Generally 24V DC loop power
162 |  | Consumption : |  |  |  |  | Input Data | mW | Power consumption of the transmitter in mW
163 |  | Load limitation : |  |  |  |  | Input Data | Ω | Resistance introduced into the loop by the transmitter
164 | 3.13.10 | SIL certificate requirement : | [5 empty] | Select | "Yes" for transmitters used in SIF loops. "No" for transmitters in other applications. |  | Select | Yes | No
165 |  | Transmitter response time : |  |  |  |  | Input Data | ms | Transmitter's response time from the moment of sensing pressure change till signal output. Generally within 1 sec unless otherwise specified for special applications such as HIPPS or compressor anti-surge control.
166 |  | Fail direction : | [5 empty] | Select | Specific requirement to specify the fail direction for transmitters. |  | Select | Fail high | Fail low
167 |  | Vibration resistance : | [5 empty] | Select | Indicate if seismic effect and vibration resistance according to IEC 60770-1 is required. |  | Select | Yes | No
168 |  | Other : | [5 empty] | Input Data | Other requirement (if any)
169 |  | Chemical Seal
170 |  | Type : | [5 empty] | Select | "Close coupled" for direct mount or "remote seal" for installation on mounting stand with capillary. N/A if manifold and impulse tubing is selected. |  | Select | Close coupled | Remote seal
171 |  | Material upper/lower part : | [5 empty] | Input Data | 316 SS or Hastelloy C-276 are standard, depending on the process fluids
172 |  | Material, bolts / nuts : | [5 empty] | Input Data | Bolts and nuts material of the chemical seal.
173 |  | Material, diaphragm : | [5 empty] | Input Data | Wetted part material to be suitable for process fluids requirement, normally 316 SS or Hastelloy C-276
174 |  | Fill fluid : | [5 empty] | Input Data | Silicon or glycerin are standard, subject to operating temperature of the process
175 |  | Capillary length : |  |  |  |  | Input Data | Select | As required for remote installation of the pressure transmitter; N/A if direct mount |  | Select | ft | m
176 |  | Material capillary / armour : | [5 empty] | Input Data | To be suitable for the ambient conditions; N/A if direct mount
177 |  | Process connection size : |  |  |  |  | Input Data | Select | 1/2 inch for threaded connection, 2 inch or 3 inch for flanged connection |  | Select | in | mm
178 |  | Process connection type : | [5 empty] | Input Data | Threaded NPT or flanged RF
179 |  | Process connection rating : |  |  |  |  | Input Data | Select | Input the diaphragm flange rating as per piping specification. |  | Select | lb | ANSI
180 |  | Flushing ring : | [5 empty] | Select | Select "Yes" if required for cleaning and calibration; "No" if not required |  | Select | Yes | No
181 | 7.3.2.3 | Extended diaphragm : | [5 empty] | Select | Extended diaphragm will be flushed with the inner wall of the vessel or pipe. To only specify when required. |  | Select | Yes | No
182 |  | Gold plating : | [5 empty] | Select | Select "Yes" if special gold plating on diaphragm surface is required (for hydrogen service); select "No" if not required. |  | Select | Yes | No
183 |  | Other : | [5 empty] | Input Data | Additional requirement (if any) such as "Extended diaphragm seal" to flush with the internal wall of vessel; N/A if none
184 |  | Manifold
185 |  | Manifold type : | [5 empty] | Input Data | "3 way" or "5 way" manifold valve is normally specified for differential pressure transmitter applications with tubing impulse line. N/A if chemical seal is selected.
186 |  | Connection size : |  |  |  |  | Input Data | Select | Normally 1/2 inch NPT, inlet male (M), outlet female (F) |  | Select | in | mm
187 |  | Outlet material : | [5 empty] | Input Data | Normally 316L SS minimum to meet process requirements
188 |  | Manufacturer : | [5 empty] | Input Data | Information shall be provided by supplier in his offer
189 |  | Model number : | [5 empty] | Input Data | Information shall be provided by supplier in his offer
190 |  | Process flange type : | [5 empty] | Input Data | Standard is "coplanar" flange
191 |  | Flange material : | [5 empty] | Input Data | Normally 316L SS minimum to meet process requirements
192 |  | O-ring : | [5 empty] | Input Data | O-ring material to meet specified process requirements; standard is "glass-filled PTFE"
193 |  | Accessories
194 |  | Mounting bracket : | [5 empty] | Select | "Yes" if remote mount; "No" if direct mount |  | Select | Yes | No
195 |  | Material, mounting bracket : | [5 empty] | Input Data | Normally 316L SS at ambient conditions; N/A if not required
196 | 3.8.3 | Electrical surge protector : | [5 empty] | Select | Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. |  | Select | Yes | No
197 |  | Sunshade : | [5 empty] | Select | Protection of transmitter against direct exposure to sun causing problems to its operation. |  | Select | Yes | No
198 |  | Other : | [5 empty] | Input Data | Other accessories (such as surge protection) to be added, if required
200 |  | Temperature Element / Transmitter / Thermowell
201 |  | General
202 |  | P&ID number : | [5 empty] | Input Data | P&ID number where the transmitter is indicated
203 |  | Line/equipment number : | [5 empty] | Input Data | Piping, vessel or equipment where the transmitter is connected for measurement purpose
204 |  | Service description : | [5 empty] | Input Data | Operational purpose of this transmitter as indicated in P&ID
205 |  | Plant area : | [5 empty] | Input Data | Geographical area of the plant where the transmitter is installed
206 |  | Hazardous area classification zone : | [5 empty] | Input Data | Define as per project hazardous area classification layout: example Zone 2.
207 |  | Hazardous area classification gas group : | [5 empty] | Input Data | Define as per project hazardous area classification layout: example Gas Group IIA.
208 |  | Hazardous area classification temperature class : | [5 empty] | Input Data | Define as per project hazardous area classification layout: example Temperature Class T3.
209 |  | Min Ambient Temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
210 |  | Max Ambient Temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
211 |  | Weight : |  |  |  |  | Input Data | kg | Weight of the complete assembly of temperature element, thermowell and transmitter.
212 |  | Process Conditions
213 |  | Fluid : | [5 empty] | Input Data | Input as per process data sheet
214 |  | Phase : | [5 empty] | Input Data | Input as per process data sheet
215 |  | Minimum Operating Temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
216 |  | Normal Operating Temperature : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | °C | °F
217 |  | Maximum Operating Temperature : |  |  |  |  | Input Data | Select | Fill in as per process data |  | Select | °C | °F
218 |  | Design temperature : |  | Input Data | Select | to | Input Data | Select | Input as per process data sheet |  | Select | °C | °F | Select | °C | °F
219 |  | Minimum operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig
220 |  | Normal operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig
221 |  | Maximum operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig
222 |  | Design pressure : |  | Input Data | Select | to | Input Data | Select | Input as per process data sheet |  | Select | barg | psig | Select | barg | psig
223 |  | Minimum fluid density : |  |  |  |  | Input Data | kg/m³ | Input as per process data sheet
224 |  | Normal fluid density : |  |  |  |  | Input Data | kg/m³ | Input as per process data sheet
225 |  | Maximum fluid density : |  |  |  |  | Input Data | kg/m³ | Input as per process data sheet
226 |  | Molecular weight : |  |  |  |  | Input Data | g/mol | Input as per process data sheet, for thermowell wake frequency calculation.
227 |  | Fluid viscosity : |  |  |  |  | Input Data | cP | Input as per process data sheet
228 |  | Minimum fluid velocity : |  |  |  |  | Input Data | m/s | Input as per process data sheet
229 |  | Normal fluid velocity : |  |  |  |  | Input Data | m/s | Input as per process data sheet
230 |  | Maximum fluid velocity : |  |  |  |  | Input Data | m/s | Input as per process data sheet
231 |  | Temperature element
232 |  | Tag number : | [5 empty] | Input Data | Fill up the unique tag number of the transmitter as indicated in P&ID
233 |  | Manufacturer : | [5 empty] | Input Data | Manufacturer of the temperature element
234 |  | Model number : | [5 empty] | Input Data | Input model number of the offered temperature element
235 | 4.4.4 | Type : | [5 empty] | Input Data | Input temperature element type example "RTD PT 100" or "Thermocouple type J".
236 | 4.3.2 | Design standard : | [5 empty] | Input Data | Example IEC 60751 or ASTM E1137 for RTD. IEC 61515 or ASTM E608 for thermocouple.
237 | 4.3.2 , 4.4.2 | Tolerance class : | [5 empty] | Input Data | Class A or Class B tolerances shall be defined as per the thermocouple or RTD relevant IEC standards.
238 | 4.3.3 | Element material : | [5 empty] | Input Data | To define the material of the selected temperature element.
239 | 4.3.2 , 4.4.3 | Sheath material : | [5 empty] | Input Data | Sheath material shall be suitable for the operating environment.
240 |  | Single / duplex configuration : | [5 empty] | Input Data | To define single or duplex element required.
241 |  | Outer diameter of element : |  |  |  |  | Input Data | Select | External diameter of the temperature element |  | Select | in | mm
242 |  | Length of element : |  |  |  |  | Input Data | Select | Input length of the temperature element. |  | Select | in | mm
243 |  | Connection type : | [5 empty] | Input Data | Type of connection between temperature element and thermowell.
244 |  | Connection size : |  |  |  |  | Input Data | Select | Size of connection between temperature element and thermowell. |  | Select | in | mm
246 |  | RTD
247 |  | Number of RTD wires : | [5 empty] | Input Data | To input 2, 3 or 4 RTD wires as per requirement.
248 |  | Resistance at 0 deg C : |  |  |  |  | Input Data | Ω | Input the resistance of the RTD element at 0 deg C, example 100 ohm for the PT100.
249 |  | Temperature coefficient (α) : |  |  |  |  | Input Data | Ω/°C/°F | Input for example α =.003902 for Platinum 100 ohms/0 °C as per USA industrial standard, or α =.003916 for Platinum 100 ohms/0 °C as per JIS C1604.
250 |  | Thermocouple
251 |  | Thermocouple tip : | [5 empty] | Input Data | Input "Grounded" or "Ungrounded".
252 |  | Wire gauge : |  |  |  |  | Input Data | Select | Supplier to provide the required thermocouple element wire size to meet the specified measurement temperature range. |  | Select | AWG | mm²
253 |  | Connection Head
254 |  | Housing type : | [5 empty] | Input Data | DIN type housing with chained cover for remote mounted transmitter; N/A for direct mounted transmitter.
255 |  | Enclosure material : | [5 empty] | Input Data | Material of the connection enclosure shall meet the specified environment
256 |  | Element connection nominal size : |  |  |  |  | Input Data | Select | Element connector to the thermowell , usually 1/2 in NPT. |  | Select | in | mm
257 |  | Cable entry : |  |  |  |  | Input Data | Select | Entry size for cable from temperature transmitter. Normally M20 X 1.5 or 1/2 in NPT. |  | Select | in | mm
259 |  | Transmitter
260 |  | Tag number : | [5 empty] | Input Data | Fill up the unique tag number of the transmitter as indicated in P&ID
261 |  | Manufacturer : | [5 empty] | Input Data | Manufacturer of the temperature transmitter
262 |  | Model number : | [5 empty] | Input Data | Input model number of the offered temperature transmitter
263 | 3.3.1 | Calibrated range : |  | Input Data | Select | to | Input Data | Select | Calibrated range to cover the minimum and maximum operating temperature measured by the transmitter corresponding to 4 - 20 mA output signal. |  | Select | °C | °F | Select | °C | °F
264 |  | Accuracy : |  |  |  | Input Data | % | of measured value (MV) | Accuracy as a percentage of the specified span.
265 | 3.9.3 | Indicator : | [5 empty] | Input Data | Integral LCD display or remote indicator
266 | 3.7.1 , 3.7.1 | Output signal : |  |  | Input Data | to | Input Data | mA | Normally 4 to 20 mA output signal
267 | 3.7.3 | Communication : | [5 empty] | Input Data | Specify the required protocol and version example HART protocol V7
268 | 3.8.1 | Supply voltage : |  |  |  |  | Input Data | V DC | Generally 24V DC loop power
269 |  | Consumption : |  |  |  |  | Input Data | mW | Power consumption of the transmitter in mW
270 |  | Load limitation : |  |  |  |  | Input Data | Ω | Resistance introduced into the loop by the transmitter
271 | 3.8.3 | Electrical surge protector : | [5 empty] | Select | Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. |  | Select | Yes | No
272 | 3.13.10 | SIL certificate requirement : | [5 empty] | Select | "Yes" for transmitters used in SIF loops. "No" for transmitters in other applications. |  | Select | Yes | No
273 |  | Transmitter response time : |  |  |  |  | Input Data | ms | Transmitter's response time from the moment of sensing pressure change till signal output. Generally within 1 sec unless otherwise specified for special applications such as HIPPS or compressor anti-surge control.
274 | 4.9 | Fail direction : | [5 empty] | Select | Specific requirement to specify the fail direction for transmitters. |  | Select | Fail high | Fail low
275 |  | Vibration resistance : | [5 empty] | Select | Indicate if seismic effect and vibration resistance according to IEC 60770-1 is required. |  | Select | Yes | No
276 |  | Cold junction compensation : | [5 empty] | Select | Cold junction compensation to be provided for thermocouple element. |  | Select | Yes | No
277 |  | Linearisation : | [5 empty] | Select | Linear output from the temperature transmitter as per industry standard tables such ASTM and NIST. |  | Select | Yes | No
278 |  | Special requirement : | [5 empty] | Input Data | Specific requirement for maintenance software, etc.
280 |  | Housing
281 |  | Weight : |  |  |  |  | Input Data | kg | Weight of the temperature transmitter.
282 | 3.13.2 | Material : | [5 empty] | Input Data | Material of transmitter enclosure
283 |  | Cable connection : |  |  |  |  | Input Data | mm² | Size of the termination for incoming signal wires
284 | 3.13.3 | Cable entry : |  |  |  |  | Input Data | Select | Size of cable gland connection to the transmitter. Normally ISO M20 X 1.5 or 1/2 in NPT. |  | Select | mm | in
285 | 3.13.1 | Environmental protection : | [5 empty] | Input Data | Ingress rating in IP or NEMA
286 | 3.13.4 | Ex protection : | [5 empty] | Input Data | Electrical protection for the specified hazardous area classification.
287 |  | Ex certification : | [5 empty] | Input Data | Electrical protection certification in accordance with testing requirements specified by ATEX, CSA, IECEx or FM.
288 |  | Protective coating : | [5 empty] | Input Data | Painting and coating specification
289 |  | Mounting : | [5 empty] | Input Data | Specify "Direct mount" - closed coupled / head mount, "DIN rail mount" - in panel, or "Remote mount" - field mounted on 2" pipe.
291 |  | Thermowell
292 |  | Tag number : | [5 empty] | Input Data | Fill up the unique tag number of the transmitter as indicated in P&ID
293 |  | Manufacturer : | [5 empty] | Input Data | Manufacturer of the thermowell
294 |  | Model number : | [5 empty] | Input Data | Input model number of the offered thermowell
295 |  | Nozzle schedule : | [5 empty] | Input Data | Nozzle schedule has to be defined to check the nozzle ID against thermowell OD for thermowell insertion.
296 |  | Insulation thickness : |  |  |  |  | Input Data | mm | Insulation material thickness of process pipe, vessel or equipment where the thermowell is connected.
297 |  | Construction
298 |  | Type : | [5 empty] | Input Data | Flanged, threaded or Van Stone type thermowell.
299 |  | Well design : | [5 empty] | Input Data | "Tapered", "straight" or "stepped" fabricated from bar stock.
300 | 3.6.2 , 3.6.2 , 3.6.7 , 4.2.5 , 4.2.5 , 4.2.5 | Material : | [5 empty] | Input Data | Material of thermowell is a wetted part and shall be suitable for the process fluids.
301 | 3.6.5.2 , 3.6.5.3 | Sour service specification : | [5 empty] | Input Data | Specify NACE MR0175 if required or N/A for not applicable
302 |  | Process connection type : | [5 empty] | Input Data | "NPT", "RF" or "RTJ".
303 |  | Process connection size : |  |  |  |  | Input Data | Select | Threaded connection size or flange size |  | Select | mm | in
304 |  | Process connection rating : |  |  |  |  | Input Data | Select | Input the flange rating as per piping specification. |  | Select | lb | ANSI
305 |  | Insertion length "U" : |  |  |  |  | Input Data | mm | Length measured from the bottom of the flange or threaded connection to the tip of the thermocouple assembly.
306 |  | Lagging extension length "T" : |  |  |  |  | Input Data | mm | Length measured from the bottom of the flange or threaded connection to the top of the thermowell assembly, including any nipple extension.
307 |  | Bore diameter : |  |  |  |  | Input Data | mm | Diameter of the hollow portion in the middle of the thermowell where temperature element is inserted.
308 |  | Outer diameter at tip : |  |  |  |  | Input Data | mm | External diameter at the bottom tip of the thermowell
309 |  | Outer diameter at support : |  |  |  |  | Input Data | mm | Outer diameter of thermowell at support shall be smaller than the process connection nozzle inner diameter.
310 |  | Wake frequency calculation : | [5 empty] | Select | Wake frequency calculation (as per ASME PTC 19.3 TW) is needed to check the strength of thermowell affected by process flow velocity. |  | Select | Yes | No
311 |  | Extension Assembly
312 |  | Extension length : |  |  |  |  | Input Data | Select | Additional nipple length required for extended head connection (e.g. due to pipe insulation) |  | Select | mm | in
313 |  | Nipple-union nominal size : |  |  |  |  | Input Data | Select | Size of the nipple-union connection at the thermowell. |  | Select | mm | in
314 |  | Nipple material : | [5 empty] | Input Data | Nipple material shall be suitable for the environment conditions; N/A if not required.
315 |  | Nipple pipe schedule : | [5 empty] | Input Data | Required pipe schedule of the nipple extension; N/A if not required.
316 |  | Accessories
317 |  | Mounting bracket : | [5 empty] | Input Data | Typically L-bracket and U-bolts are specified here.
318 |  | Material, mounting bracket : | [5 empty] | Input Data | Normally 316L SS at ambient conditions; N/A if not required
319 |  | Electrical surge protector : | [5 empty] | Select | Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. |  | Select | Yes | No
320 |  | Sunshade : | [5 empty] | Select | Protection of transmitter against direct exposure to sun causing problems to its operation. |  | Select | Yes | No
321 |  | Other : | [5 empty] | Input Data | Other accessories (such as surge protection) to be added, if required
322 |  | Orifice Plate Assembly
323 |  | Tag number : | [5 empty] | Input Data | Fill up the unique tag number of the orifice plate assembly as indicated in P&ID
324 |  | Service description : | [5 empty] | Input Data | Operational purpose of this orifice plate assembly as indicated in P&ID
325 |  | P&ID number : | [5 empty] | Input Data | P&ID number where the orifice plate assembly is indicated
326 |  | Line number : | [5 empty] | Input Data | Pipe line number where the orifice plate assembly is installed for measurement purpose
327 |  | Line size : |  |  |  |  | Input Data | Select | To input the pipe size as indicated in P&ID. |  | Select | mm | in
328 |  | Line ID : |  |  |  |  | Input Data | Select | Internal diameter of the pipe. |  | Select | mm | in
329 |  | Plant area : | [5 empty] | Input Data | Geographical area of the plant where the orifice plate assembly is installed
330 |  | Weight : |  |  |  |  | Input Data | kg | Weight of the transmitter complete with orifice assembly.
331 |  | Process Conditions
332 |  | Process fluid : | [5 empty] | Input Data | Process fluid according to process data sheet
333 |  | Fluid state : | [5 empty] | Input Data | Input as per process data
334 |  | Minimum flow : |  |  |  |  | Input Data |  | Input data as per process data sheet. Input data 1 =alue of flow. Input data 2 =ngineering unit.
335 |  | Normal flow : |  |  |  |  | Input Data |  | Input data as per process data sheet. Input data 1 =alue of flow. Input data 2 =ngineering unit.
336 |  | Maximum flow : |  |  |  |  | Input Data |  | Input data as per process data sheet. Input data 1 =alue of flow. Input data 2 =ngineering unit.
337 |  | Differential pressure at maximum flow : |  |  |  |  | Input Data | Select | Typical value (example 250 mbar, 500 mbar , etc.) used for orifice plate sizing. |  | Select | bar | psi | kPa
338 |  | Maximum allowable differential pressure : |  |  |  |  | Input Data | Select | Input value as per process data sheet. |  | Select | bar | psi | kPa
339 |  | Viscosity : |  |  |  |  | Input Data | Select | Input as per process data |  | Select | cP | cS
340 |  | Specific gravity : | [5 empty] | Input Data | Input as per process data
341 |  | Compressibility : | [5 empty] | Input Data | Input as per process data sheet.
342 |  | Specific heat ratio : | [5 empty] | Input Data | Input as per process data sheet.
343 |  | Normal operating temperature : |  |  |  |  | Input Data | Select | Normal operating temperature as per process data sheet |  | Select | °C | °F
344 |  | Base temperature : |  |  |  |  | Input Data | Select | Input reference temperature, typically 0 deg C or 15 deg C. |  | Select | °C | °F
345 |  | Design temperature : |  |  |  |  | Input Data | Select | Input as per process data |  | Select | °C | °F
346 |  | Normal operating pressure : |  |  |  |  | Input Data | Select | Input as per process data sheet |  | Select | barg | psig
347 |  | Base pressure : |  |  |  |  | Input Data |  | Provide base pressure value in Input data 1 and the corresponding engineering unit in Input data 2.
348 |  | Design pressure : |  | Input Data | Select | to | Input Data | Select | Input minimum/maximum design pressure as per process data sheet; minimum design pressure will include full vacuum condition. |  | Select | barg | psig | Select | barg | psig
Orifice Plate
349 |  | Orifice Plate and Holder
350 |  | Manufacturer : | [5 empty] | Input Data | Manufacturer of the orifice plate
351 |  | Model number : | [5 empty] | Input Data | Input model number of the offered orifice plate
352 | 6.2.1.5 | Standard : | [5 empty] | Input Data | As per orifice plate standards such as ISO 5167 or API MPMS Chapter 14.3
353 | 6.2.1.5 | Plate type : | [5 empty] | Input Data | Specify concentric, eccentric or quadrant edge type
354 | 3.6.2 , 3.6.5.2 , 3.6.5.3 , 3.6.7 , 6.2.1.5 | Material : | [5 empty] | Input Data | Material of orifice plate is a wetted part and shall be suitable for the process fluids.
355 | 6.2.1.5 | Plate thickness : |  |  |  |  | Input Data | mm | Supplier to input the final plate thickness after sizing calculations.
356 |  | Bore diameter : |  |  |  |  | Input Data | mm | Purchaser to provide estimated dimension, final diameter (within 2 decimal places) shall be input by supplier after sizing calculations.
357 |  | Plate outer diameter : |  |  |  |  | Input Data | mm | Outer diameter of the orifice plate inserted between flanges in accordance with Piping Class requirement.
358 | 6.2.1.1 | Beta ratio (d/D) : | [5 empty] | Input Data | Input the ratio of d/D after orifice sizing calculations.
359 | 6.2.1.4 | Differential pressure range : |  | Input Data | Select | to | Input Data | Select | Differential pressure range associated with the minimum and maximum flow rates of the fluid being measured. |  | Select | bar | psi | Select | bar | psi
360 |  | Pressure loss at full range : |  |  |  |  | Input Data | Select | To be provided by supplier after sizing calculations. |  | Select | bar | psi
361 | 6.2.1.5 | Vent / drain hole : | [5 empty] | Input Data | Input vent only, drain only or both; N/A if not required.
362 |  | Vent / drain hole size : |  |  |  |  | Input Data | Select | Define the size (diameter), if vent / drain hole is selected. N/A if not selected. |  | Select | mm | in
363 |  | Holder style : | [5 empty] | Input Data | Paddle type or others; N/A if not required.
364 |  | Stamping : | [5 empty] | Select | Tag number, orifice bore (d), nominal pipe size (D) and material to be stamped on the upstream side of the holder. |  | Select | Yes | No
365 |  | Other : | [5 empty] | Input Data | Specify any additional requirement.
366 |  | Orifice Flange
367 |  | Manufacturer : | [5 empty] | Input Data | Manufacturer of the orifice plate
368 |  | Flange code : | [5 empty] | Input Data | ASME B16.5 or others
369 | 3.6.2 , 3.6.2 , 3.6.5.2 , 3.6.5.3 , 3.6.7 | Material : | [5 empty] | Input Data | Material of orifice flange is a wetted part and shall be suitable for the process fluids.
370 |  | Material, bolts and nuts : | [5 empty] | Input Data | Purchaser to provide bolts and nuts material in accordance with piping class and material requirement.
371 |  | Gasket type : | [5 empty] | Input Data | Purchaser to provide the gasket type in accordance with piping class requirement.
372 | 3.6.4 | Material, gasket : | [5 empty] | Input Data | Purchaser to provide gasket material in accordance with piping class requirement.
373 |  | Flange size : |  |  |  |  | Input Data | mm | Purchaser to provide flange size in accordance with the pipe nominal diameter.
374 |  | Flange rating : | [5 empty] | Input Data | Purchaser to provide flange rating in accordance with piping class requirement.
375 |  | Flange facing : | [5 empty] | Input Data | Purchaser to provide flange facing in accordance with piping class requirement.
376 |  | Face to face dimension : |  |  |  |  | Input Data | mm | Face to face dimension to include orifice plate thickness and gasket thickness.
377 |  | Flange tap size : |  |  |  |  | Input Data | Select | Process connection for differential pressure transmitter, normally 1/2 in NPT. |  | Select | mm | in
378 |  | Tap type : | [5 empty] | Input Data | To specify "flange tap", "corner tap" or "N/A" for piping tap.
379 |  | Tap orientation : |  |  |  |  | Input Data | ° | Input the angle shift from the vertical position (12 o'clock). Typically 45 deg or 90 deg.
380 |  | Protective coating : | [5 empty] | Input Data | To specify protective coating in accordance with Painting and Coating specification; N/A if not required.
381 |  | Other : | [5 empty] | Input Data | To specify additional requirement, if any.
382 |  | Integral Orifice Assembly
383 |  | Manufacturer : | [5 empty] | Input Data | Manufacturer of the integral orifice assembly
384 |  | Model number : | [5 empty] | Input Data | Model number of the integral orifice assembly.
385 | 3.6.5.2 , 3.6.5.3 , 3.6.7 | Material : | [5 empty] | Input Data | Material of the integral orifice assembly is a wetted part and shall be suitable for the process fluids; N/A if not required.
386 |  | End connection type : | [5 empty] | Input Data | Type of connection between integral orifice assembly and line pipe.
387 |  | End connection nominal size : |  |  |  |  | Input Data | Select | Size of the connection between integral orifice assembly and the line pipe. |  | Select | mm | in
388 |  | End connection rating : |  |  |  |  | Input Data | Select | Input the rating requirement of the piping flange connection. |  | Select | lb | ANSI
389 | 6.2.1.6 | Face to face dimension : |  |  |  |  | Input Data | mm | Face to face dimension to include orifice assembly upstream and downstream straight length requirement.
390 |  | Tube inner diameter : |  |  |  |  | Input Data | Select | To input the inner diameter of the integral orifice assembly. |  | Select | mm | in
391 |  | Other : | [5 empty] | Input Data | Additional requirement, if any.
392 |  | Quick Change Fitting
393 |  | Manufacturer : | [5 empty] | Input Data | Manufacturer of the meter tube
394 |  | Model number : | [5 empty] | Input Data | Model number of the integral meter tube.
395 |  | Removal under line pressure : | [5 empty] | Select | Select "Yes" for senior orifice; or "No" for junior orifice or if not required. |  | Select | Yes | No
396 |  | Face to face dimension : |  |  |  |  | Input Data | mm | The end connection's face to face length of the entire fitting assembly.
397 |  | Inner diameter : |  |  |  |  | Input Data | Select | To input the inner diameter of the quick change fitting, |  | Select | mm | in
398 |  | End connection type : | [5 empty] | Input Data | Type of connection between quick change fitting and line pipe.
399 |  | End connection nominal size : |  |  |  |  | Input Data | Select | Size of the connection between quick change fitting and the line pipe. |  | Select | mm | in
400 |  | End connection rating : |  |  |  |  | Input Data | Select | Input the rating requirement of the piping flange connection. |  | Select | lb | ANSI
401 |  | Material, body : | [5 empty] | Input Data | Body material of the quick change fitting is a wetted part and shall be suitable for the process fluids; N/A if not required.
402 | 3.6.5.2 , 3.6.5.3 , 3.6.7 | Material, internals : | [5 empty] | Input Data | Input internals material of the quick change fitting: N/A if not required.
403 | 3.6.4 , 3.6.5.2 | Material, seal : | [5 empty] | Input Data | Input seal material of the quick change fitting; N/A if not required.
404 |  | Protective coating : | [5 empty] | Input Data | Input protective coating requirement as per Coating and Painting Specification; N/A if not required.
405 |  | Other : | [5 empty] | Input Data | Additional requirement, if any.
| DOCUMENT NUMBER : Insert Project Document Number |  | REV : Insert Project Document Rev
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Supplement
Row | S-718D Data Sheet for Field Instruments - Electronic Transmitters Pressure, Differential Pressure and Temperature |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
Public Review Draft

## Backcover
Public Review Draft