## Front & Preliminaries
|  |  |  | SPECIFICATION | March
|  |  |  | S-703D | 2020
Data Sheet for
Low Voltage Three Phase
Cage Induction Motors
Revision history
| VERSION | DATE | PURPOSE
| 1.0 | March 2020 | Issued for Publication
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-703D Version 1.0
Data sheet for
Low Voltage Three Phase
Cage Induction Motors
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
IOGP S-703D Version 1.0
Data Sheet for
Low Voltage Three Phase
Cage Induction Motors
Introduction
The purpose of this equipment data sheet is to define buyer specific requirements for the procurement of low voltage three phase cage induction motors, in accordance with IOGP S-703, for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-703, information requirements specification IOGP S-703L and quality requirements specification IOGP S-703Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet
IOGP S-703D Version 1.0

## Data Sheet Single-speed Motor
Row |  | S-703D Data Sheet for Data Sheet for Low Voltage Three Phase Cage Induction Motors Single-speed Motor |  |  |  | Issue
2 | Tag No. :
3 | Service : | [5 empty] | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | General
6 |  | Manufacturer : | Input Data
7 |  | Model number : | Input Data
8 |  | Serial number : | Input Data
9 |  | Order status : | Select |  |  |  | Select | for enquiry | for purchase | as-build
10 |  | Conformity Assessment System (CAS) level : | D |  |  |  | Select | A | B | C | D
11 |  | Frame size : | Input Data
12 |  | Duty
13 | 4.1, 4.2.1, 4.2.10, 4.2.2, 4.2.3, 4.2.4, 4.2.5, 4.2.6, 4.2.7, 4.2.8, 4.2.9, 5.1, 5.3, 5.5.2 | Duty type : | S1 |  |  |  | Select | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8 | S9 | S10
14 |  | Number of poles : | Select |  |  |  | Select | 2 pole | 4 pole | 6 pole | 8 pole | other
15 |  | Duty point shaft power : | Input Data | kW
16 |  | Direction of rotation : | Select |  |  |  | Select | clockwise | counter-clockwise
17 |  | Load drive : | Select |  |  |  | Select | direct | belt | gearbox | other
18 | 11.3.5.3, 11.3.5.4 | External radial loading on the motor shaft end : | Input Data | N
19 | 11.3.5.3, 11.3.5.4 | External axial loading on the motor shaft end : | Input Data | N
20 |  | Moment of inertia of the load (Jext) : | Input Data | kg·m²
21 |  | Rating
22 | 11.8.2, 5.5.3, 5.8 | Rated power output : | Input Data | kW
23 |  | Full load current (FLC) : | Input Data | A
24 |  | Site conditions
25 | 6.1 | Location environment : | Select |  |  |  | Select | onshore – coastal | onshore – desert | onshore – inland | offshore – fixed | offshore – floating | marine (ship) | interior location
26 | 6.1, 6.2 | Altitude : | 1000 | m |  |  | Select | 1000 | other
27 | 6.1, 6.3 | Maximum ambient air temperature : | 40 | °C |  |  | Select | 40 | 45 | 50 | other
28 | 6.1, 6.4 | Minimum ambient air temperature : | -15 | °C |  |  | Select | -15 | -20 | -40 | other
29 | 6.6 | Transport and storage conditions : | within defined site conditions |  |  |  | Select | within defined site conditions | outside defined site conditions - see comments box for details
30 | 6.6 | Standstill period : | ≤ 6 months |  |  |  | Select | ≤ 6 months | ≤ 9 months | ≤ 12 months | other
31 | 6.1, 6.3 | Maximum relative humidity : | 100 | % |  |  | Select | 100 | 95 | 90 | other
32 | 6.8.1 | Motor enclosure ingress protection : | IP55 |  |  |  | Select | IP55 | IP56 | IP54 | IP44 | IP23 | other
33 | 6.9 | Impact protection : | IK08 |  |  |  | Select | IK08 | IK09 | IK10
34 |  | Electrical operating conditions
35 |  | Motor rated voltage : | Select | V |  |  | Select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | other
36 |  | Motor rated frequency : | Select | Hz |  |  | Select | 50 | 60
37 | 7.3, 9.12.1.3, Figure 12 | Maximum operating voltage limit : | Select | % |  |  | Select | 10 | 6 | other
38 | 7.3, 9.12.1.3, Figure 12 | Minimum operating voltage limit : | Select | % |  |  | Select | -10 | other
39 | 7.3, Figure 12 | Maximum operating frequency limit : | Select | % |  |  | Select | 3 | 5 | other
40 | 7.3, Figure 12 | Minimum operating frequency limit : | Select | % |  |  | Select | -5 | other
41 | 7.2.1.1 | Power supply quality : | as per IEC 60034-1 section 7.2.1 |  |  |  | Select | as per IEC 60034-1 section 7.2.1 | class 1 as per 61000-2-4 | class 2 as per 61000-2-4 | class 3 as per 61000-2-4
42 |  | Thermal performance
43 | 8.1 | Thermal class : | F |  |  |  | Select | F | H
44 | 8.1 | Temperature rise class : | B |  |  |  | Select | B | F
45 |  | Starting performance
46 | 9.12.1.1 | Starting designation : | N |  |  |  | Select | N | NE | NY | NEY | H | HE | HY | HEY
47 | 9.5 | Pull-up torque : | Input Data | pu of FLT
48 | 9.12.1.2 | Declared locked rotor current tolerance : | 20 | % |  |  | Select | 20 | 10 | 0
49 | 9.12.1.2 | Declared locked-rotor current at 100% rated voltage : | Input Data | pu of FLC
50 | 9.12.1.2 | Declared locked-rotor current at 80% rated voltage : | Input Data | pu of FLC
51 | Table 21 | Declared locked-rotor torque at 100% rated voltage : | Input Data | N·m
52 | Table 21 | Declared locked-rotor torque at 80% rated voltage : | Input Data | N·m
53 |  | Declared locked-rotor power factor at 100% rated voltage : | Input Data
54 |  | Moment of inertia of the motor (Jm) : | Input Data | kg·m²
55 |  | Maximum permissible starting time at 100% rated voltage : | Input Data | s
56 |  | Maximum permissible starting time at 80% rated voltage : | Input Data | s
57 |  | Data for protection setting/power modelling : | Not required |  |  |  | Select | Not required | Required
58 |  | Operating performance
59 | 9.6, Table 18 | Rated full load speed : | Input Data | r/min
60 |  | Rated full load torque : | Input Data | N·m
61 |  | Rated breakdown torque : | Input Data | pu of FLT
62 | 9.14.1, 9.14.2 | Efficiency : | IE3 |  |  |  | Select | IE3 | IE2 | IE4 | IE1 | other
63 | 9.14.1, 9.14.2 | Efficiency at 100% rated output : | Input Data | %
64 |  | Efficiency at 75% rated output : | Input Data | %
65 |  | Efficiency at 50% rated output : | Input Data | %
66 |  | Power factor at 100% rated output : | Input Data | pu
67 |  | Power factor at 75% rated output : | Input Data | pu
68 |  | Power factor at 50% rated output : | Input Data | pu
69 |  | Noise
70 | 9.13.1, 9.13.2 | Purchaser maximum permissible noise limit : | as per IEC 60034-9 | db(A) |  |  | Select | as per IEC 60034-9 | 75 | 77 | 80 | other
71 | 9.13.1, 9.13.2 | Maximum declared motor sound power level at no-load : | Input Data | db(A)
72 | 9.13.1, 9.13.2 | Maximum expected motor sound power level at full load : | Input Data | db(A)
73 | 9.13.1, 9.13.2 | Noise level test of one motor from this order batch : | No |  |  |  | Select | No | Yes
74 |  | Machine construction
75 |  | Motor weight : | Input Data | kg
76 |  | Stainless steel fixings : | Select |  |  |  | Select | required | not required
77 |  | Rotor
78 | 11.3.2.2 | Maximum vibration magnitude : | grade A |  |  |  | Select | grade A | grade B
79 |  | Fan
80 | 11.3.3.1 | Fan impeller material : | GRP |  |  |  | Select | GRP | steel fan | other
81 | 11.3.3.2 | Fan direction of rotation : | Select |  |  |  | Select | bi-directional, uni-directional clockwise | unidirectional counter-clockwise
82 |  | Terminal box
83 |  | Location : | Select |  |  |  | Select | top | right | left | bottom
84 | 6.8.1 | Ingress protection of all terminal box(es) : | IP55 |  |  |  | Select | IP55 | IP56 | IP54 | IP44 | IP23 | other
85 | 11.3.4.3, 11.3.4.5 | Line conductor terminal box cable gland entries : | Input Data
86 |  | Line conductor cross-section area : | Select | mm² |  |  | Select | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | other
87 |  | Large terminal box : | not required |  |  |  | Select | not required | required
88 |  | Bearings
89 | 11.3.5.1, 11.3.5.3 | D-end bearing type : | Input Data
90 | 11.3.5.1, 11.3.5.3 | N-end bearing type : | Input Data
91 | 11.3.5.2 | Internal clearance : | C3 |  |  |  | Select | C3 | other
92 | 11.3.5.1 | Lubrication specification : | Input Data
93 |  | Space heaters
94 | 11.3.6.1 | Heater requirement : | not required - unless advised by manufacturer |  |  |  | Select | not required - unless advised by manufacturer | required
95 | 11.3.6.2 | Supply voltage : | Select | V |  |  | Select | 100-120 | 200-240
96 | 11.7.2 | Separate terminal box : | Select |  |  |  | Select | not required | required
97 | 11.3.6.5 | Warning label language : | Select |  |  |  | Select | English | other - see comment
98 |  | Mounting
99 | 11.4.1, 11.4.2 | Mounting arrangement : | Select |  |  |  | Select | IM B3 (IM 1001) | IM B5 (IM 3001) | IM V1 (IM 3011) | IM V6 (IM 1031) | IM V1 (IM 3015) | IM V6 (IM 1035). other
100 |  | Cooling
101 | 11.5 | Cooling method : | IC4A1A1 |  |  |  | Select | IC4A1A1 | other
102 |  | Vibration
103 | 11.3.5.5 | Vibration monitoring : | none |  |  |  | Select | none | SPM nipples
104 | 11.3.2.1, 11.3.2.2 | Vibration level test report : | not required |  |  |  | Select | not required | required
105 |  | Shock pulse monitoring connection : | Input Data
106 |  | Surface protection
107 | 11.6.1, 11.6.2 | Surface protection corrosivity category : | Select |  |  |  | Select | C3 | C4 | C5 | CX
108 | 11.6.3 | Surface protection durability category : | medium (M) 7 to 15 years, high (H) 15 to 25 years |  |  |  | Select | medium (M) 7 to 15 years, high (H) 15 to 25 years | very high (VH) +25 years
109 |  | Surface finish : | manufacturer's standard |  |  |  | Select | manufacturer's standard | Norsok M-501 system no.1 | Norsok M-501 system no. 2A | Norsok M-501 system no. 2B
110 |  | Paint colour : | Manufacturer's standard |  |  |  | Select | Manufacturer's standard | other
111 |  | Temperature monitoring
112 | 11.7.1, 11.7.2 | Winding temperature detection : | Select |  |  |  | Select | none | PTC - see comment | Pt100 - see comment
113 |  | Motors intended for use in potentially explosive atmospheres
114 |  | Motor to be rated for use in potentially explosive atmosphere : | Select |  |  |  | Select | no | yes
115 | 15.1.1, 15.1.2 | Hazardous area equipment certifying body : | Select |  |  |  | Select | ATEX Directive, IECEx | EAC | other
116 | 15.1.1, 15.1.3 | Temperature group : | T3 |  |  |  | Select | T3 | T4 | T5 | T6 | T1 | T2
117 | 15.1.1, 15.1.3 | Gas group : | IIB |  |  |  | Select | IIB | IIA | IIC
118 | 15.1.2, 15.1.3 | Equipment protection level : | Select |  |  |  | Select | EPL Ga | EPL Gb | EPL Gc,
119 | 15.1.4, 15.2.1 | Motor classification : | Select |  |  |  | Select | Ex db | Ex db eb | Ex eb | Ex ec
120 |  | Miscellaneous
121 |  | Provision for IoT hardware installation : | Select |  |  |  | Select | required | not required
Note on C6: Input motor manufacturer.
Note on C7: Input motor model number.
Note on C8: Input motor serial number.
Note on C9: Select order status.
Note on C10: Select CAS level as defined in S-703Q, Annex A. IOGP default is D. CAS level can be raised if more purchaser involvement is required.
Note on C11: Input motor frame size. IEC 60072-1 Table 1 defines preferred frame sizes for a.c. induction motors.
Note on C13: Input the duty type as defined in IEC-60034-1 Section 4. IOGP default is S1 for single-speed use. For converter-fed motors, duty S9 or S10 may be applicable, or an S1 duty motor, depending on the load profile.
Note on C14: Select the required number of magnetic poles. For 10 poles and above, select 'other' and enter the required number of poles in the additional comments.
Note on C15: Input the driven load maximum duty power requirement. This kW figure should include any sizing margins.
Note on C16: Select the direction of motor shaft rotation observed when facing the D-end (motor drive end). Default motor direction of rotation is clockwise, when connecting motor terminals U-V-W to supply L1-L2-L3.
Note on C17: Select method of power transfer to driven equipment. Assists with selection of bearings which may be potentially subjected to higher axial or radial loading.
Note on C18: Purchaser to input maximum anticipated radial loading on the shaft end for belt driven loads. Supplier to input maximum permissible radial loading if not defined by the Purchaser. Radial forces are those that are perpendicular to the motor shaft.
Note on C19: Purchaser to input maximum anticipated axial loading on the shaft end. Supplier to input maximum permissible axial loading if not defined by the Purchaser. Axial forces are those that are linear to (act along) the motor shaft.
Note on C20: Input the maximum moment of inertia of the load.
Note on C22: Input the motor shaft rated mechanical power output at the defined maximum ambient air temperature. IEC 60072 defines preferred primary series values.
Note on C23: Confirm the motor full load current whilst operating at rated voltage and rated frequency.
Note on C25: Select location motor shall be situated as per the options available.
Note on C26: Altitude above sea-level. IEC 60034-1 default is 1000 m. Modify 1000 m value only if the site conditions are higher than the IEC default.
Note on C27: IEC 60034-1 default is 40 °C. Modify 40°C value only if the site conditions are higher than the IEC default. 40 °C aligns with the IEC 70079 series default maximum ambient air temperature requirement.
Note on C28: IEC 60034-1 default is -15°C. Modify -15°C value only if the site conditions are lower than the IEC 60034-1 default. -20°C aligns with the IEC 70079 series default minimum ambient air temperature requirement.
Note on C29: Manufacturer to provide details of where transportation and storage conditions are out with those detailed by the Purchaser as site conditions. The manufacturer take measures to ensure these do not affect the integrity of the motor.
Note on C30: Purchaser to advise when periods of standstill or storage or transport which exceed 6 months are anticipated, as described in IEC 60034-1 Section 6.6.
Note on C31: Select the maximum relative humidity at the maximum ambient air temperature defined in this data sheet.
Note on C32: Select the ingress protection value according to IEC 60034-5. IOGP default is IP55 for 'totally enclosed' motors. NOTE: For interior (indoor) locations, the requirement for a degree of ingress protection lower than IP55 can be evaluated by the user.
Note on C33: Select the IK code for impact protection with regards to impact energy according to IEC 62262. IOGP default is IK08.
Note on C35: Select the supply voltage for which the motor shall be rated.
Note on C36: Select the supply frequency for which the motor shall be rated.
Note on C37: Select the maximum steady-state voltage limit as a percentage of supply voltage. IEC 60034-1 Figure 12 zone B upper Y boundary default is 1.10 pu (+10%). IEC 61892-1 Table 1 defines +6% limit voltage for offshore 'island' networks.
Note on C38: Select the minimum steady-state voltage limit as a percentage of supply voltage. IEC 60034-1 Figure 12 zone B lower Y boundary default is 0.90 pu (-10%).
Note on C39: Select the maximum steady-state frequency limit as a percentage of supply frequency. IEC 60034-1 Figure 12 zone B upper X boundary default is 1.03 pu (+3%). IEC 61892-1 Table 1 defines +5% limit frequency for offshore 'island' networks.
Note on C40: Select the minimum steady-state frequency limit as a percentage of supply frequency. IEC 60034-1 Figure 12 zone B lower X boundary default is 0.95 pu (-5%).
Note on C41: For single-speed motors, select the total harmonic distortion in the electrical supply for which the motor shall be rated.
Note on C43: Select the thermal class of the motor according to IEC 60085. IOGP default is class F.
Note on C44: Select the temperature rise class of motor according to IEC 60085. IOGP default is class B rise (for motors with class F insulation). For class H insulated motors (such as fire-water pump motors) the default is class F rise.
Note on C46: Select the motor starting designation according to IEC 60034-12. IOGP default designation is design N. Where requirements in accordance with IEC 60034-12 Table 2 cannot be achieved, design NE can be provided by the supplier.
Note on C47: Confirm the smallest steady-state asynchronous torque which the motor develops between zero speed and the speed which corresponds to the breakdown torque, when the motor is supplied at the rated voltage and frequency.
Note on C48: Confirm accepted tolerance for declared locked rotor current tolerance. Whilst the default is +20% as per IEC 60034-1 Table 21, it is acknowledged that some projects may require a more stringent value to be imposed.
Note on C49: Confirm greatest steady-state r.m.s. current taken from the line with the motor held at rest, over all angular positions, at 100% rated voltage and frequency, as a per unit value of full load current (Is/In) including positive tolerance.
Note on C50: Confirm greatest steady-state r.m.s. current taken from the line with the motor held at rest, over all angular positions, at 80% rated voltage and frequency, as a per unit value of full load current (Is/In) including positive tolerance.
Note on C51: Confirm the smallest measured torque the motor develops at its shaft and with the rotor locked, over all its angular positions, at rated voltage and frequency.
Note on C52: Confirm the smallest measured torque the motor develops at its shaft and with the rotor locked, over all its angular positions, at 80% rated voltage and rated frequency.
Note on C53: Confirm the power factor with the rotor locked, at rated voltage and frequency.
Note on C54: Confirm the motor moment of inertia as defined in IEC 60034-1 Clause 3.24.
Note on C55: Confirm the maximum allowable duration of time for the motor to reach its rated speed at 100% rated voltage whilst starting from 'hot'.
Note on C56: Confirm the maximum allowable duration of time for the motor to reach its rated speed at 80% rated voltage whilst starting from 'hot'.
Note on C57: Additional information may be requested to facilitate power system modelling and/or protection device configuration. Final application specific information requirements to be agreed between purchaser and supplier.
Note on C59: Confirm the steady-state asynchronous rotor speed whilst delivering 100% rated power.at the rated voltage and frequency. Note: Includes the slip of the motor at full load and at working temperature.
Note on C60: Confirm the steady-state asynchronous rotor torque whilst delivering 100% rated power.at the rated voltage and frequency.
Note on C61: Confirm the maximum steady-state asynchronous torque which the motor develops without an abrupt drop in speed, when the motor is supplied at the rated voltage and frequency.
Note on C62: Select the efficiency category (IE) according to IEC 60034-30. IOGP default for single-speed motors is IE3 (premium efficiency). IOGP default for converter-fed motors is IE2.
Note on C63: Confirm the efficiency of the motor whilst operating at 100% rated power.
Note on C64: Confirm the efficiency of the motor whilst operating at 75% rated power.
Note on C65: Confirm the efficiency of the motor whilst operating at 50% rated power.
Note on C66: Confirm the cosine of the angle between active power and apparent power when the motor is operated at 100% rated power.
Note on C67: The cosine of the angle between active power and apparent power when the motor is operated at 75% rated power.
Note on C68: Confirm the cosine of the angle between active power and apparent power when the motor is operated at 50% rated power.
Note on C70: Input the maximum permissible motor A-weighted sound power level at full load.
Note on C71: Confirm the manufacturer declared motor A-weighted sound power level at no-load when tested in accordance with IEC 60034-9.
Note on C72: Confirm the manufacturer expected A-weighted sound power level, in dB(A) for rated load condition, calculated in accordance with IEC 60034-9 Table 3.
Note on C73: Purchaser to advise if a batch specific noise test is required to be performed on one motor of the type defined in this data sheet. IOGP default is set at 'not required'.
Note on C75: Confirm the fully assembled weight of the motor.
Note on C76: Confirm where environmental factors require stainless steel nuts, bolts, washers and any other fixings are to be manufactured from stainless steel.
Note on C78: Input the required vibration grade as defined in IEC 60034-14 Table 1. IOGP default is grade A. Grade A applies to motors with no special vibration requirements. Grade B applies to motors with special vibration requirements.
Note on C80: Select the material from which fan impeller shall be constructed.
Note on C81: Confirm the fan blade configuration to meet the required noise levels.
Note on C83: Select the location of the motor line conductor terminal box as viewed from the D-end (drive end). The position of 'bottom' is only applicable to motors with a flange and with drains, as viewed from the D-end and with the drains at 6 o’clock.
Note on C84: Select the ingress protection method according to IEC 60034-5 for which all the terminal box(es) shall be rated.
Note on C85: Confirm the number and size of cable gland entries in main terminal box e.g. 1 x M32, 2 x M20. Where gland entry number and sizes are not confirmed by purchaser, the supplier shall confirm terminal box gland entry specification.
Note on C86: Where known, purchaser to confirm cross-section area of line conductor to be terminated in the terminal box. Where line conductor cross-section area is not known, the supplier shall confirm maximum connectable cross-section area capacity of terminal box.
Note on C87: Confirm where a larger than standard main terminal box is required due to supply cables larger than that accommodated by the manufacturers standard terminal box are anticipated.
Note on C89: Confirm the D-end (drive end) bearing model number.
Note on C90: Confirm the N-end (non-drive end) bearing model number.
Note on C91: Confirm the required internal clearance of bearing in accordance with ISO 5753-1 . C3 (group 3) refers to 'greater than normal' clearance as commonly used to avoid too little internal bearing clearance for low voltage motors.
Note on C92: Confirm the approved lubrication specification for re-greasable bearings.
Note on C94: IOGP default position is that no space heaters shall be provided, unless advised by the manufacturer that space heaters are necessary at the defined site conditions.
Note on C95: Input the supply voltage for which the heater shall be rated.
Note on C96: Confirm where a separate terminal box is required for the space heater power supply. Note: This option may not be available on smaller frame sizes.
Note on C97: Confirm the language for which the label, warning that heater terminals may be live when the motor is isolated, should be written. Where the language is other than English, this can be confirmed in the 'additional comments' section
Note on C99: Confirm the motor mounting arrangement in accordance with IEC 60034-7.
Note on C101: Confirm the motor cooling method in accordance with IEC 60034-6.
Note on C103: Confirm if there is a requirement for a vibration monitoring connection point to be provided.
Note on C104: Purchaser to advise if a batch specific vibration test is required to be performed on one motor of the type defined in this data sheet. IOGP default is set at 'not required'.
Note on C105: Where shock pulse monitoring connection points are to be provided, the purchaser shall confirm site connection type requirement.
Note on C107: Advise surface corrosivity category in accordance with ISO 12944-2 Section 5.1.1.
Note on C108: Advise surface durability category in accordance with ISO 12944-1 Section 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme.
Note on C109: Advise surface finish requirements.
Note on C110: Where standard manufacturer paint colour is unacceptable, confirm specific paint colour requirements in 'additional comments'.
Note on C112: Confirm requirement for embedded temperature detection in the stator windings, Use comments section to confirm device transition set-point.
Note on C114: Confirm whether the motor shall be rated for use in a potentially explosive atmosphere in accordance with IEC 60079
Note on C115: Confirm which certification or notified body shall be accepted for motors to be located in a hazardous area.
Note on C116: Confirm temperature group according to IEC 60079-0 for which machine shall be rated.
Note on C117: Confirm gas group according to IEC 60079-0 for which machine shall be rated.
Note on C118: Confirm equipment protection level (EPL) according to IEC 60079-14
Note on C119: Confirm classification according to IEC 60079 for which motor shall be rated.
Note on C121: Where the supplier offers IoT hardware which shall be attached to the motor, mounting points and all other provisions shall be made to facilitate this. Note: This may be to allow the IoT system to be procured at a later date.

## Data Sheet Converter-fed Motor
Row |  | S-703D Data Sheet for Data Sheet for Low Voltage Three Phase Cage Induction Motors Converter-fed Motor |  |  |  | Issue
2 | Tag No. :
3 | Service : | [5 empty] | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | General
6 |  | Manufacturer : | Input Data
7 |  | Model number : | Input Data
8 |  | Serial number : | Input Data
9 |  | Order status : | Select |  |  |  | Select | for enquiry | for purchase | as-build
10 |  | Conformity Assessment System (CAS) level : | D |  |  |  | Select | A | B | C | D
11 |  | Frame size : | Input Data
12 |  | Duty
13 | 4.1, 4.2.1, 4.2.10, 4.2.2, 4.2.3, 4.2.4, 4.2.5, 4.2.6, 4.2.7, 4.2.8, 4.2.9, 5.1, 5.3, 5.5.2 | Duty type : | S1 |  |  |  | Select | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8 | S9 | S10
14 |  | Number of poles : | Select |  |  |  | Select | 2 pole | 4 pole | 6 pole | 8 pole | other
15 |  | Duty point shaft power : | Input Data | kW
16 |  | Direction of rotation : | Select |  |  |  | Select | clockwise | counter-clockwise
17 |  | Load drive : | Select |  |  |  | Select | direct | belt | gearbox | other
18 | 11.3.5.3, 11.3.5.4 | External radial loading on the motor shaft end : | Input Data | N
19 | 11.3.5.3, 11.3.5.4 | External axial loading on the motor shaft end : | Input Data | N
20 |  | Moment of inertia of the load (Jext) : | Input Data | kg·m²
21 |  | Rating
22 | 11.8.2, 5.5.3, 5.8 | Rated power output : | Input Data | kW
23 |  | Full load current (FLC) : | Input Data | A
24 |  | Site conditions
25 | 6.1 | Location environment : | Select |  |  |  | Select | onshore – coastal | onshore – desert | onshore – inland | offshore – fixed | offshore – floating | marine (ship) | interior location
26 | 6.1, 6.2 | Altitude : | 1000 | m |  |  | Select | 1000 | other
27 | 6.1, 6.3 | Maximum ambient air temperature : | 40 | °C |  |  | Select | 40 | 45 | 50 | other
28 | 6.1, 6.4 | Minimum ambient air temperature : | -15 | °C |  |  | Select | -15 | -20 | -40 | other
29 | 6.6 | Transport and storage conditions : | within defined site conditions |  |  |  | Select | within defined site conditions | outside defined site service conditions - see comments box for details
30 | 6.6 | Standstill period : | ≤ 6 months |  |  |  | Select | ≤ 6 months | ≤ 9 months | ≤ 12 months | other
31 | 6.1, 6.3 | Maximum relative humidity : | 100 | % |  |  | Select | 100 | 95 | 90 | other
32 | 6.8.1 | Motor enclosure ingress protection : | IP55 |  |  |  | Select | IP55 | IP56 | IP54 | IP44 | IP23 | other
33 | 6.9 | Impact protection : | IK08 |  |  |  | Select | IK08 | IK09 | IK10
34 |  | Thermal performance
35 | 8.1 | Thermal class : | F |  |  |  | Select | F | H
36 | 8.1 | Temperature rise class : | B |  |  |  | Select | B | F
37 |  | Starting performance
38 |  | Moment of inertia of the motor (Jm) : | Input Data | kg·m²
39 |  | Data for protection setting/power modelling : | not required |  |  |  | Select | not required | required
40 |  | Operating performance
41 | 9.6, Table 18 | Rated full load speed : | Input Data | r/min
42 |  | Rated full load torque : | Input Data | N·m
43 |  | Rated breakdown torque : | Input Data | pu of FLT
44 | 9.14.1, 9.14.2 | Efficiency : | IE2 |  |  |  | Select | IE3 | IE2 | IE4 | IE1 | other
45 | 9.14.1, 9.14.2 | Efficiency at 100% rated output : | Input Data | %
46 |  | Power factor at 100% rated output : | Input Data | pu
47 |  | Noise
48 | 9.13.1, 9.13.2 | Purchaser maximum permissible noise limit : | as per IEC 60034-9 | db(A) |  |  | Select | as per IEC 60034-9 | 75 | 77 | 80 | other
49 | 9.13.1, 9.13.2 | Maximum declared motor sound power level at no-load : | Input Data | db(A)
50 | 9.13.1, 9.13.2 | Maximum expected motor sound power level at full load : | Input Data | db(A)
51 | 9.13.1, 9.13.2 | Noise level test of one motor from this order batch : | No |  |  |  | Select | No | Yes
52 |  | Machine construction
53 |  | Motor weight : | Input Data | kg
54 |  | Stainless steel fixings : | Select |  |  |  | Select | required | not required
55 |  | Rotor
56 | 11.3.2.2 | Maximum vibration magnitude : | grade A |  |  |  | Select | grade A | grade B
57 |  | Fan
58 | 11.3.3.1 | Fan impeller material : | GRP |  |  |  | Select | GRP | steel fan | other
59 | 11.3.3.2 | Fan direction of rotation : | Select |  |  |  | Select | bi-directional, uni-directional clockwise | unidirectional counter-clockwise
60 |  | Terminal box
61 |  | Location : | Select |  |  |  | Select | top | right | left | bottom
62 | 6.8.1 | Ingress protection of all terminal box(es) : | IP55 |  |  |  | Select | IP55 | IP56 | IP54 | IP44 | IP23 | other
63 | 11.3.4.3, 11.3.4.5 | Line conductor terminal box cable gland entries : | Input Data
64 |  | Line conductor cross-section area : | Select | mm² |  |  | Select | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | other
65 |  | Large terminal box : | not required |  |  |  | Select | not required | required
66 |  | Bearings
67 | 11.3.5.1, 11.3.5.3 | D-end bearing type : | Input Data
68 | 11.3.5.1, 11.3.5.3 | N-end bearing type : | Input Data
69 | 11.3.5.2 | Internal clearance : | C3 |  |  |  | Select | C3 | other
70 | 11.3.5.1 | Lubrication specification : | Input Data
71 |  | Space heaters
72 | 11.3.6.1 | Heater requirement : | not required - unless advised by manufacturer |  |  |  | Select | not required - unless advised by manufacturer | required
73 | 11.3.6.2 | Supply voltage : | Select | V |  |  | Select | 100-120 | 200-240
74 | 11.7.2 | Separate terminal box : | Select |  |  |  | Select | not required | required
75 | 11.3.6.5 | Warning label language : | Select |  |  |  | Select | English | other - see comment
76 |  | Mounting
77 | 11.4.1, 11.4.2 | Mounting arrangement : | Select |  |  |  | Select | IM B3 (IM 1001) | IM B5 (IM 3001) | IM V1 (IM 3011) | IM V6 (IM 1031) | IM V1 (IM 3015) | IM V6 (IM 1035). other
78 |  | Cooling
79 | 11.5 | Cooling method : | IC4A1A1 |  |  |  | Select | IC4A1A1 | other
80 |  | Vibration
81 | 11.3.5.5 | Vibration monitoring : | None |  |  |  | Select | None | SPM nipples
82 | 11.3.2.1, 11.3.2.2 | Vibration level test report : | not required |  |  |  | Select | not required | required
83 |  | Shock pulse monitoring connection : | Input Data
84 |  | Surface protection
85 | 11.6.1, 11.6.2 | Surface protection corrosivity category : | Select |  |  |  | Select | C3 | C4 | C5 | CX
86 | 11.6.3 | Surface protection durability category : | medium (M) 7 to 15 years, high (H) 15 to 25 years |  |  |  | Select | medium (M) 7 to 15 years, high (H) 15 to 25 years | very high (VH) +25 years
87 |  | Surface finish : | manufacturer's standard |  |  |  | Select | manufacturer's standard | Norsok M-501 system no.1 | Norsok M-501 system no. 2A | Norsok M-501 system no. 2B
88 |  | Paint colour : | Manufacturer's standard |  |  |  | Select | Manufacturer's standard | other
89 |  | Temperature monitoring
90 | 11.7.1, 11.7.2 | Winding temperature detection : | Select |  |  |  | Select | none | PTC - see comment | Pt100 - see comment
91 |  | Converter-fed motor data
92 | 15.3 | Converter manufacturer : | Input Data
93 | 15.3 | Converter model number : | Input Data
94 |  | Minimum operating speed : | Input Data | rpm
95 |  | Maximum operating speed : | Input Data | rpm
96 | 9.6 | Fine balancing above rated speed : | Not required |  |  |  | Select | Not required | Required
97 |  | Motors intended for use in potentially explosive atmospheres
98 |  | Motor to be rated for use in potentially explosive atmosphere : | Select |  |  |  | Select | no | yes
99 | 15.1.1, 15.1.2 | Hazardous area equipment certifying body : | Select |  |  |  | Select | ATEX Directive, IECEx | EAC | other
100 | 15.1.1, 15.1.3 | Temperature group : | T3 |  |  |  | Select | T3 | T4 | T5 | T6 | T1 | T2
101 | 15.1.1, 15.1.3 | Gas group : | IIB |  |  |  | Select | IIB | IIA | IIC
102 | 15.1.2, 15.1.3 | Equipment protection level : | Select |  |  |  | Select | EPL Ga | EPL Gb | EPL Gc,
103 | 15.1.4, 15.2.1 | Motor classification : | Select |  |  |  | Select | Ex db | Ex db eb | Ex eb | Ex ec
104 |  | Miscellaneous
105 |  | Provision for IoT hardware installation : | Select |  |  |  | Select | required | not required
Note on C6: Input motor manufacturer.
Note on C7: Input motor model number.
Note on C8: Input motor serial number.
Note on C9: Select order status.
Note on C10: Select CAS level as defined in S-703Q, Annex A. IOGP default is D. CAS level can be raised if more purchaser involvement is required.
Note on C11: Input motor frame size. IEC 60072-1 Table 1 defines preferred frame sizes for a.c. induction motors.
Note on C13: Input the duty type as defined in IEC-60034-1 Section 4. IOGP default is S1 for single-speed use. For converter-fed motors, duty S9 or S10 may be applicable, or an S1 duty motor, depending on the load profile.
Note on C14: Select the required number of magnetic poles. For 10 poles and above, select 'other' and enter the required number of poles in the additional comments.
Note on C15: Input the driven load maximum duty power requirement. This kW figure should include any sizing margins.
Note on C16: Select the direction of motor shaft rotation observed when facing the D-end (motor drive end). Default motor direction of rotation is clockwise, when connecting motor terminals U-V-W to supply L1-L2-L3.
Note on C17: Select method of power transfer to driven equipment. Assists with selection of bearings which may be potentially subjected to higher axial or radial loading.
Note on C18: Purchaser to input maximum anticipated radial loading on the shaft end for belt driven loads. Supplier to input maximum permissible radial loading if not defined by the Purchaser. Radial forces are those that are perpendicular to the motor shaft.
Note on C19: Purchaser to input maximum anticipated axial loading on the shaft end. Supplier to input maximum permissible axial loading if not defined by the Purchaser. Axial forces are those that are linear to (act along) the motor shaft.
Note on C20: Input the maximum moment of inertia of the load.
Note on C22: Input the motor shaft rated mechanical power output at the defined maximum ambient air temperature. IEC 60072 defines preferred primary series values.
Note on C23: Confirm the motor full load current whilst operating at rated voltage and rated frequency.
Note on C25: Select location motor shall be situated as per the options available.
Note on C26: Altitude above sea-level. IEC 60034-1 default is 1000 m. Modify 1000 m value only if the site conditions are higher than the IEC default.
Note on C27: IEC 60034-1 default is 40 °C. Modify 40°C value only if the site conditions are higher than the IEC default. 40 °C aligns with the IEC 70079 series default maximum ambient air temperature requirement.
Note on C28: IEC 60034-1 default is -15°C. Modify -15°C value only if the site conditions are lower than the IEC 60034-1 default. -20°C aligns with the IEC 70079 series default minimum ambient air temperature requirement.
Note on C29: Manufacturer to provide details of where transportation and storage conditions are out with those detailed by the Purchaser as site conditions. The manufacturer take measures to ensure these do not affect the integrity of the motor.
Note on C30: Purchaser to advise when periods of standstill or storage or transport which exceed 6 months are anticipated, as described in IEC 60034-1 Section 6.6.
Note on C31: Select the maximum relative humidity at the maximum ambient air temperature defined in this data sheet.
Note on C32: Select the ingress protection value according to IEC 60034-5. IOGP default is IP55 for 'totally enclosed' motors. NOTE: For interior (indoor) locations, the requirement for a degree of ingress protection lower than IP55 can be evaluated by the user.
Note on C33: Select the IK code for impact protection with regards to impact energy according to IEC 62262. IOGP default is IK08.
Note on C35: Select the thermal class of the motor according to IEC 60085. IOGP default is class F.
Note on C36: Select the temperature rise class of motor according to IEC 60085. IOGP default is class B rise (for motors with class F insulation). For class H insulated motors (such as fire-water pump motors) the default is class F rise.
Note on C38: Confirm the motor moment of inertia as defined in IEC 60034-1 Clause 3.24.
Note on C39: Additional information may be requested to facilitate power system modelling and/or protection device configuration. Final application specific information requirements to be agreed between purchaser and supplier.
Note on C41: Confirm the steady-state asynchronous rotor speed whilst delivering 100% rated power.at the rated voltage and frequency. Note: Includes the slip of the motor at full load and at working temperature.
Note on C42: Confirm the steady-state asynchronous rotor torque whilst delivering 100% rated power.at the rated voltage and frequency.
Note on C43: Confirm the maximum steady-state asynchronous torque which the motor develops without an abrupt drop in speed, when the motor is supplied at the rated voltage and frequency.
Note on C44: Select the efficiency category (IE) according to IEC 60034-30. IOGP default for single-speed motors is IE3 (premium efficiency). IOGP default for converter-fed motors is IE2.
Note on C45: Confirm the efficiency of the motor whilst operating at 100% rated power.
Note on C46: Confirm the cosine of the angle between active power and apparent power when the motor is operated at 100% rated power.
Note on C48: Input the maximum permissible motor A-weighted sound power level at full load.
Note on C49: Confirm the manufacturer declared motor A-weighted sound power level at no-load when tested in accordance with IEC 60034-9.
Note on C50: Confirm the manufacturer expected A-weighted sound power level, in dB(A) for rated load condition, calculated in accordance with IEC 60034-9 Table 3.
Note on C51: Purchaser to advise if a batch specific noise test is required to be performed on one motor of the type defined in this data sheet. IOGP default is set at 'not required'.
Note on C53: Confirm the fully assembled weight of the motor.
Note on C54: Confirm where environmental factors require stainless steel nuts, bolts, washers and any other fixings are to be manufactured from stainless steel.
Note on C56: Input the required vibration grade as defined in IEC 60034-14 Table 1. IOGP default is grade A. Grade A applies to motors with no special vibration requirements. Grade B applies to motors with special vibration requirements.
Note on C58: Select the material from which fan impeller shall be constructed.
Note on C59: Confirm the fan blade configuration to meet the required noise levels.
Note on C61: Select the location of the motor line conductor terminal box as viewed from the D-end (drive end). The position of 'bottom' is only applicable to motors with a flange and with drains, as viewed from the D-end and with the drains at 6 o’clock.
Note on C62: Select the ingress protection method according to IEC 60034-5 for which all the terminal box(es) shall be rated.
Note on C63: Confirm the number and size of cable gland entries in main terminal box e.g. 1 x M32, 2 x M20. Where gland entry number and sizes are not confirmed by purchaser, the supplier shall confirm terminal box gland entry specification.
Note on C64: Where known, purchaser to confirm cross-section area of line conductor to be terminated in the terminal box. Where line conductor cross-section area is not known, the supplier shall confirm maximum connectable cross-section area capacity of terminal box.
Note on C65: Confirm where a larger than standard main terminal box is required due to supply cables larger than that accommodated by the manufacturers standard terminal box are anticipated.
Note on C67: Confirm the D-end (drive end) bearing model number.
Note on C68: Confirm the N-end (non-drive end) bearing model number.
Note on C69: Confirm the required internal clearance of bearing in accordance with ISO 5753-1 . C3 (group 3) refers to 'greater than normal' clearance as commonly used to avoid too little internal bearing clearance for low voltage motors.
Note on C70: Confirm the approved lubrication specification for re-greasable bearings.
Note on C72: IOGP default position is that no space heaters shall be provided, unless advised by the manufacturer that space heaters are necessary at the defined site conditions.
Note on C73: Input the supply voltage for which the heater shall be rated.
Note on C74: Confirm where a separate terminal box is required for the space heater power supply. Note: This option may not be available on smaller frame sizes.
Note on C75: Confirm the language for which the label, warning that heater terminals may be live when the motor is isolated, should be written. Where the language is other than English, this can be confirmed in the 'additional comments' section
Note on C77: Confirm the motor mounting arrangement in accordance with IEC 60034-7.
Note on C79: Confirm the motor cooling method in accordance with IEC 60034-6.
Note on C81: Confirm if there is a requirement for a vibration monitoring connection point to be provided.
Note on C82: Purchaser to advise if a batch specific vibration test is required to be performed on one motor of the type defined in this data sheet. IOGP default is set at 'not required'.
Note on C83: Where shock pulse monitoring connection points are to be provided, the purchaser shall confirm site connection type requirement.
Note on C85: Advise surface corrosivity category in accordance with ISO 12944-2 Section 5.1.1.
Note on C86: Advise surface durability category in accordance with ISO 12944-1 Section 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme.
Note on C87: Advise surface finish requirements.
Note on C88: Where standard manufacturer paint colour is unacceptable, confirm specific paint colour requirements in 'additional comments'.
Note on C90: Confirm requirement for embedded temperature detection in the stator windings, Use comments section to confirm device transition set-point.
Note on C92: Confirm manufacturer of converter from which the machine shall be driven
Note on C93: Confirm model number of converter from which the machine shall be driven.
Note on C94: Input minimum operating speed for which the motor shall be rated in normal operation.
Note on C95: Input maximum operating speed for which the motor shall be rated in normal operation.
Note on C96: Purchaser to confirm if fine balancing of rotor shaft is required for high speed applications.
Note on C98: Confirm whether the motor shall be rated for use in a potentially explosive atmosphere in accordance with IEC 60079
Note on C99: Confirm which certification or notified body shall be accepted for motors to be located in a hazardous area.
Note on C100: Confirm temperature group according to IEC 60079-0 for which machine shall be rated.
Note on C101: Confirm gas group according to IEC 60079-0 for which machine shall be rated.
Note on C102: Confirm equipment protection level (EPL) according to IEC 60079-14
Note on C103: Confirm classification according to IEC 60079 for which motor shall be rated.
Note on C105: Where the supplier offers IoT hardware which shall be attached to the motor, mounting points and all other provisions shall be made to facilitate this. Note: This may be to allow the IoT system to be procured at a later date.

## Supplement
Row |  | S-703D Data Sheet for Low Voltage Three Phase Cage Induction Motors | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95

## Guidance
Data Sheet for
Low Voltage Three Phase
Cage Induction Motors
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-703 Supplementary Specification to IEC 60034-1 Low Voltage Three Phase Cage Induction Motors.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.
IOGP S-703D Version 1.0