## Front & Preliminaries
|  |  |  | SPECIFICATION | March
|  |  |  | S-703L | 2020
Information Requirements for
Low Voltage Three Phase
Cage Induction Motors
Revision history
| VERSION | DATE | PURPOSE
| 1.0 | March 2020 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-703L Version 1.0
S-703L Information Requirements for
Low Voltage Three Phase
Cage Induction Motors
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
IOGP S-703L Version 1.0
S-703L Information Requirements for
Low Voltage Three Phase
Cage Induction Motors
Introduction
The purpose of this information requirements specification (IRS) is to define Information requirements for the procurement of low voltage three phase cage induction motors, in accordance with IOGP S-703 for application in the petroleum and natural gas industries. This document defines the information requirements, including format, timing and purpose, for information to be provided by the manufacturer. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the supplementary requirements specification IOGP S-703, quality requirements specification IOGP S-703Q and equipment data sheet IOGP S-703D which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification
IOGP S-703L Version 1.0

## Supplier Instructions
[5 empty] | S-703L | Information Requirements for
Low Voltage Three Phase
Cage Induction Motors
Supplier Instructions
In response to Invitation To Tender (ITT)
Tenderers to submit information as defined in column E - 'Submit At Proposal' in 'Requirements' sheet, in accordance with ITT instructions
On award of contract
Specified Information requirements shall be submitted in accordance with contract information submission instructions. Suppliers to prepare and submit 'Supplier Master Information Schedule' (SMIS) incorporating information requirements in accordance with columns F - 'First Issue Post Purchase Order' in 'Requirements' sheet. Supplier to demonstrate compliance with each information requirement either by providing document number cross reference to the Requirement in 'Supplier Master Information Schedule' (SMIS) and, if specified in the Contract, using column J 'Fulfilled by Document Number(s)' in the IRS Requirements Sheet.
On completion of scope
Supplier to validate that the information delivered meets the IRS requirements either through cross reference to the deliverable type in a as-built version of the 'Supplier Master Information Schedule' SMIS and, if specified in the Contract, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in Requirement sheet populated with the specific document numbers issued to the Purchaser.
IRS Structure Contents
| 1 |  | 'Front & Preliminaries' Tab
The 'Front & Preliminaries ' tab includes an IOGP Front sheet for the IRS followed by Acknowledgements, a Disclaimer, Copyright Notice, Foreword and Introduction
| 2 |  | 'Supplier Instructions' Tab
This 'Supplier Instructions' tab provides instructions that Suppliers are to follow in response to this IRS.
S-703L Instructions and Guidance
| 3 |  | 'Requirements' Tab
The 'Requirements' tab lists the suite of information requirements that are to be supplied during tendering and following award of the purchase order to deliver the purchase order scope. The information requirements are grouped under three broad categories; Management information requirements: Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. Technical information requirements: Technical information developed by the supplier or their sub suppliers, during the design and development, acquisition, manufacture, assembly and testing of the contracted scope. Purchase Order Specific Information Requirements: Information requirements specified by individual owners-operators in addition to those specified by IOGP-JIP33 to meet specific operational, project or legislative requirements. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. "The 'Requirements' tab includes columns A to L, including Column A for the relevant requirement code and Column B for the Requirement for the different Information Requirements (Data, Documents and/or Models) to be provided by suppliers, based on the parent standard, IOGP Specification or the specified parent industry Standard. Condition Invoking Revoking Requirement Column C is included to allow any specific conditions to be identified that may require a additional deliverable(s). Typical Deliverable Column D is provided for Purchaser to identify the deliverable type that the information would typically appear within; this also allows the Purchaser's Requisitioning Engineers to group the various Information Requirements by Deliverable Type. Column E includes Submission Requirements (Yes or No) at Proposal, while columns F, G & H identify Issue Purpose (For Information or For Acceptance) and Durations (Period or Weeks/Months) for First Issue of the particular deliverable Post Purchase Order. Required As Built, Fulfilled by Document Number(s), Translation Required and Remarks columns I, J, K & L are also included. Definitions for each column are contained in the rows above the columns: Abbreviations used for various submission requirements in Column H are shown in table 3.1 below:
Table 3.1 - Information Submission Abbreviations
S-703L Instructions and Guidance
| 4 |  | 'Definitions' Tab
The 'Definitions' tab includes several columns A to F, including Column A for the relevant Code & Column B for the Requirement for the different Information (Data, Documents and/or Models) Requirements to be provided by Suppliers, all copied from the 'Requirements' tab. Column C includes a full description of the Information Requirement based on the Parent Standard, IOGP Specification or an Industry Standard. Column D gives a reference to the Parent Standard, IOGP Specification or an Industry Standard that the Information requirement is identified in. Column E identifies the Requirement format as listed in Table 9.1 below. Column F relates the CFIHOS discipline document type that could be used to classify the document having this IRS content. Definitions for each column are contained in the rows above the columns:
| 5 |  | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various tabs of this workbook.
| Buyer |  |  | Organisation placing a Contract or Purchase Order with Supplier for equipment or services on project; may be alternatively referred to as 'User' or 'Purchaser'
| CFIHOS |  |  | Capital Facilities Information Hand Over Specification
| Company |  |  | Project Operating Entity or the organisation Contractor is under contract to
| Contractor |  |  | Project Contractor responsible for procuring equipment.
| Information |  |  | Data, Documents and/or Models
| IRS |  |  | Information Requirements Specification
| PO |  |  | Purchase Order
| QRS |  |  | Quality Requirements Specification
| SMIS |  |  | Supplier Master Information Schedule
| Supplier |  |  | Organisation supplying equipment or services to Company and/or Contractor on project; may alternatively be referred to as "Vendor", "Seller" or “Manufacturer”.
| 6 |  | CFIHOS
The Information Requirements are also classified according to document classification published in v1.4 of Capital Facilities Information Hand Over Specification (CFIHOS). The objective of CFIHOS is to create a common information standards across the process industries. Further information on CFIHOS can be found at:
https://uspi.nl/index.php/projects/frameworks-methodologies/136-cfihos
S-703L Instructions and Guidance
| 7 |  | Document Metadata
Typical Metadata for Information Deliverables to be provided by Suppliers is shown in Table 7.1 below
Table 7.1 - Supplier Deliverable Metadata
S-703L Instructions and Guidance
| 8 |  | Deliverable Formats
The format of the relevant Information Deliverable to be submitted by Supplier for Buyer/Contractor is to be as described in table 8.1 below. Where required to be ‘As Built’, deliverables are to be updated and handed over in the native format.
Table 8.1 – Deliverable Formats
S-703L Instructions and Guidance

## Requirements
S-703L Information Requirements for Low Voltage Three Phase Cage Induction Motors
Requirements
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement based on the description in the Parent Standard, IOGP Specification or an Industry Standard Information Requirement Title.
C | Condition Invoking Requirement - describes special condition(s) under which the Information Requirement is required; e.g.. service offshore and weight greater than 1 tonne means information is required. NB: if blank, always required
D | Typical Deliverable - Purchaser to advise the short description of the Information Deliverable that would typically include this Information Requirement
E | Submit With Proposal - Yes or No, where ‘Yes' means the Information Requirement is required to be submitted with Suppliers Proposal or 'No' is not required
F, G & H | First Issue Post Purchase Order - issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the Information Requirement and Period defined after Purchase Order placement
I | Required As Built - Yes or No, where ‘Yes' means the Information Requirement is required to be 'As Built' on completion or delivery of equipment or 'No' is not required 'As Built'
J | Fulfilled by Information Deliverable Number(s) – identifies which Information Requirement(s) listed in the Supplier Master Information Schedule (SMIS) addresses the Purchasers requirements. NB; it should be noted that one Information Deliverable can fulfil more than one Information Requirement.
K | Translation Required -Yes or No, where 'Yes' means the Information Requirement should be translated into a language(s) (to be advised) other than English and 'No' means to be provided in English
L | Remarks - may include bid clarification questions & decisions (specify author & date)
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Requirements
S703-IR-1 | Supplier master information schedule |  | Information Deliverables List | No | For Acceptance |  | WAO | Yes |  | No
S703-IR-4 | Quality plan | Required for CAS A and B as per S703-Q | Quality Plan | No | - |  | - | - |  | -
S703-IR-6 | Inspection and test plan | Required for CAS A and B as per S703-Q | Inspection and Test Plan (ITP) | No | - |  | - | - |  | -
S703-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No |  | No
S703-IR-8 | Non-conformance records |  | Nonconformance History | No | For Acceptance |  | WAO | No |  | -
S703-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | WAO | Yes |  | No
Technical Information Requirements
S703-IR-19 | General arrangement drawing |  | General arrangement diagram | Yes | For Information |  | WAO | No |  | No | Preliminary with proposal
S703-IR-22 | Termination diagram | Where purchaser cable terminations are required in addition to that of the line conductors. | Termination diagram | No | For Information |  | WAO | No
S703-IR-20 | Single-speed motor performance curves | To be provided motors for single-speed use with a rated power output â‰¥100 kW. | Motor performance curve | Yes | For Information |  | WAO | No |  |  | Provides the user with confirmation that the motor is capable of meeting the torque requirements of the driven load.
S703-IR-40 | Converter-fed motors performance curves | Where purchaser confirms the motor is converter-fed. | Motor performance curve | Yes | For Information |  | WAO | No |  |  | Provides the user with confirmation that the motor is capable of meeting the torque requirements of the driven load.
S703-IR-33 | Routine test procedure | Required only where tests in addition to those stated in IEC 60034-1 Table 16 have been specified by the purchaser in the data sheet | Test procedure | No | For Information |  | WPTT | No
S703-IR-24 | Routine test report | Required for CAS A, B, and C as per S703-Q | Test report | No | - |  | - | - |  | -
S703-IR-29 | Type test report | Required for CAS A and B as per S703-Q | Type test report | No | - |  | - | - |  | -
S703-IR-37 | Noise type test report | Required for CAS A, B and C | Noise type test report | No | - |  | WPTD | No
S703-IR-39 | Vibration test report | Required for CAS A, B and C | Vibration level test report | No | - |  | WPTD | No
S703-IR-41 | Data for protection setting/power modelling | Data for protection setting/power modelling requested in the datasheet | Data for protection setting/power modelling | No | For Information |  | WAO | No |  |  | Provides the user with the information required to ensure the upstream system configuration is specified accordingly.
S703-IR-42 | Equivalent circuit diagram | Converter-fed motor with a frame size greater than 315 | Equivalent circuit diagram | No | For Information |  | WAO | No |  |  | Provides the user with the basic elements resistance, inductance, and capacitance in a simple arrangement such that motor performance can be evaluated for network modelling.
S703-IR-35 | Installation, operation and maintenance manual |  | Installation, operation and maintenance manual | No | For Information |  | WAO | No |  | No | Provides the user with information and guidance to ensure the equipment is utilized as per manufacturer's intent.
S703-IR-26 | Electrical hazardous area equipment certification |  | Ex certification | No | For Information |  | WAO | No |  | No
S703-IR-30 | Declaration of conformity |  | Declaration of conformity | No | For Information |  | WPTD | No |  | No
S703-IR-44 | IOGP S-703D Data Sheet |  | Data Sheet | Yes | For Acceptance |  | WAO | Yes |  | No | Preliminary information should be provided with proposal.
Purchase Order Specific Information Requirements

## Definitions
S-703L Information Requirements for Low Voltage Three Phase Cage Induction Motors
Definitions
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement that would typically provide the Information required, based on the description in the Parent Standard, IOGP Specification or an Industry Standard Title.
C | Description - an excerpt from the Parent Standard, IOGP Specification or Industry Standard.
D | Reference - reference to the Parent Standard, IOGP Specification or Industry Standard that the Information Deliverable is identified in.
E | Format - defines the required format of the relevant Information Requirement to be submitted by Supplier for Buyer/Contractor for information and acceptance as shown in Table 9.1 of Instructions Tab and selected from pick list.
F | CFIHOS Discipline Document Type Code - the CFIHOS discipline document type that could be used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Requirements
S703-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. | API 671, 13.1.1 | Native | CFIHOS-70000099
S703-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] | Contract Requirement | PDF
S703-IR-6 | Inspection and test plan | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. | Contract Requirement | PDF | CFIHOS-70000180
S703-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. | Contract Requirement, 6.6 | PDF | CFIHOS-70000154
S703-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. | Contract Requirement | PDF | CFIHOS-70000226
S703-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout | Contract Requirement | PDF | CFIHOS-70000389
Technical Information Requirements
S703-IR-19 | General arrangement drawing | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing shall contain reference to main specifications and standards. For equipment / components the drawing may include cross sectional views. Document may contain the following information: • Main dimensions • Interface connections • Weight • Centre of gravity • Withdrawal/installation and maintenance space. • Installation and mounting details • Lifting arrangement | 11.1, 11.3.1.1, 11.3.1.3, 11.3.2.3, 11.3.3.3, 11.3.4.1, 11.3.4.3, 6.8.2 | PDF | CFIHOS-70000153
S703-IR-22 | Termination diagram | A diagram for equipment, panels, junction boxes, etc. identifies all connections and cable terminations at input/output rails. Required for removal/hook up purposes and modifications. To include vendor interfaces. | 11.3.4.2 | PDF | CFIHOS-70000330
S703-IR-20 | Single-speed motor performance curves | Motor performance curve shall include the following information: • Torque curve from 0 to 100% synchronous speed at 80% rated voltage expressed as a percentage of rated torque. • Torque curve from 0 to 100% synchronous speed at 100% rated voltage expressed as a percentage of rated torque. • Current curve from 0 to 100% synchronous speed at 80% rated voltage expressed as a percentage of rated current. • Current curve from 0 to 100% synchronous speed at 100% rated voltage expressed as a percentage of rated current. • Torque curve of the load from 0 to 100% synchronous speed expressed as a percentage of rated torque. |  | PDF
S703-IR-40 | Converter-fed motors performance curves | Provide motor performance curves for quadrant operation specified in the datasheet and as per IEC 61800-2: 2015 Table 4, Section 4.3.3.2 and Figure 8. |  | PDF
S703-IR-33 | Routine test procedure | Procedure documenting the manufacturers recommended testing activities and acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Procedure to define test set-up and test equipment. | 9.2, Table 16, Table 17 | PDF
S703-IR-24 | Routine test report | This document records and documents all results from the activities performed in routine tests in accordance with IEC 60034-1 Section 9. Mandatory content of information: - Date of testing; - Signature of person responsible for test; - Object identification (type, series number, etc.). - Measured values; - Statement of compliance. Optional content of information: - Test equipment / instruments used; - Reference to test procedure. | 9.2, Table 16, Table 17 | PDF
S703-IR-29 | Type test report | A document which provides a summary of tests of one or more machine made to a certain design to show that the design meets certain specifications. The report will include the specific year and edition of the IEC used to perform the type test for all discrete functional units provided. This shall include: Winding resistance - cold in accordance with IEC 60034-1 Table 16 Locked rotor current test in accordance with EC 60034-1 Table 21 Temperature rise test in accordance with IEC 60034-1 Section 8 Full load test in accordance with IEC 60034-1 Section 8 Breakdown torque test in accordance with EC 60034-1 Table 21 No-load test in accordance with IEC 60034-1 Table 16 Open circuit secondary induced voltage at standstill in accordance with IEC 60034-1 Table 16 Withstand voltage test in accordance with IEC 60034-1 Table 16 | 8.1, 11.3.6.3, 9.12.1.1, 9.12.1.2, 9.12.1.3, 9.13.1, 9.13.2, Table 21 | PDF
S703-IR-37 | Noise type test report | A type test report detailing noise performance in accordance with IEC 60034-9. | 9.13.1, 9.13.2 | PDF
S703-IR-39 | Vibration test report | Vibration level test report stating maximum vibration levels of machine as defined in IEC 60034-14 | 11.3.2.1, 11.3.2.2 | PDF
S703-IR-41 | Data for protection setting/power modelling | Additional information to facilitate power system modelling and/or protection device configuration. Final application specific information requirements to be agreed between purchaser and supplier. |  | PDF
S703-IR-42 | Equivalent circuit diagram | A function diagram providing information on the electric and magnetic behaviour of the motor. This shall apply the conventions for electric and magnetic circuits as specified in IEC 60375. See IEC TS 60034-25 Table 3 for electrical parameters to be included in the T-equivalent circuit diagram. |  | PDF
S703-IR-35 | Installation, operation and maintenance manual | The user of the product shall be provided with information regarding normal and safe operation/functioning. As appropriate, this should be completed by information regarding automatic and remote controlled products, exceptional functions/situations, indications to be observed, protection of persons and instructions for fault detection. Description of methods of installing a piece of equipment. The instruction material shall contain applicable information relating to the product itself as follows : Installation: • Installation refers to the mounting, setting, erection, etc. Operation: • detailed description of the product, its fittings, its guards and/or protective devices; • comprehensive range of applications for which the product is intended, taking into account variations of the original machine if appropriate; • warnings about reasonably foreseeable misuse; • instructions for setting and adjustment; • instructions for re-starting after an intervention; • diagrams showing the main functions of the product and especially the safety functions; • description of the initial operations required to bring the product to full working performance, with details of checks, methods of setting adjustable controls and what the setting should be; • maintenance tasks within the capability of the user during normal use; • identification and treatment of malfunctions; • details of any techniques that are likely to be new to users, for example with regard to information technologies; • storage and preservation of the product when not in use. Maintenance: The document shall include descriptions for both hardware and software regarding preventive maintenance, fault detection, fault diagnosis and fault isolation, rectification of faults and system operation. The instructions should include information concerning: • the nature and frequency of inspections; • safety precautions and warnings for maintenance carried out on running or live equipment; • information for fault diagnosis and identification; • instructions for repairs and adjustments; • description of built-in diagnostic systems to aid fault finding, when applicable; • drawings and diagrams enabling maintenance personnel to carry out their task rationally (especially fault-finding tasks); • regular checking of warning devices; • description of all predictable tasks performed at specific intervals to be consolidated in the form of maintenance schedules and, if necessary, master schedules; • the name, address, telephone number, etc. of the supplier or others from whom technical assistance can be obtained. |  | PDF | CFIHOS-70000228
S703-IR-26 | Electrical hazardous area equipment certification | Attestation issued by a recognised notified body e.g. ATEX Directive, IECEx, EAC, certifying that a type test has satisfied specified criteria to enable that equipment to be used in a potentially explosive atmosphere. | 11.3.3.1, 15.1.1, 15.1.2, 15.1.3, 15.1.4, 15.2.1, 15.2.2, 6.8.2 | PDF | CFIHOS-70000160
S703-IR-30 | Declaration of conformity | Declares conformance with all standards relating to the machine in it's region of use, and its duty as defined by the purchaser in the data sheet. | 1.1 | PDF
S703-IR-44 | IOGP S-703D Data Sheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document will IOGP S-703D with supplier fields populated. | 11.3.3.2, 11.3.5.1, 11.3.5.2, 11.3.5.3, 9.14.1, 9.14.2, 9.5 | Native | CFIHOS-70000416
Purchase Order Specific Information Requirements

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col K
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
WAO
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code |  | WAD | Weeks After Delivery
|  |  |  | Hard Copy |  |  | WAI | Weeks After Inspection
|  |  |  | Native |  |  | WAO | Weeks After Order
|  |  |  | PDF |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | Intelligent Vector (CAD) |  |  | WAT | Weeks After Test
|  |  |  | Multi media (Film) |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | Raster Image (Bitmap) |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | Structured Data (MS Apps) |  |  | WPTT | Weeks Prior To Test
Technical Publication (Text)
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: