## Front & Preliminaries
|  |  |  | SPECIFICATION | November
|  |  |  | S-718L | 2021
Information Requirements for
Basic Process Measurement Instruments
Revision history
| VERSION | DATE | PURPOSE
| 0.3 | November 2021 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-718L Information Requirements for
Basic Process Measurement Instruments
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
S-718L Information Requirements for
Basic Process Measurement Instruments
Introduction
The purpose of this information requirements specification (IRS) is to define information requirements for the procurement of basic process measurement instruments in accordance with IOGP S-718 for application in the petroleum and natural gas industries. The IRS defines the information requirements, including format, timing and purpose, for information to be provided by the supplier. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the specification (IOGP S-718), procurement data sheet (IOGP S-718D) and quality requirements specification (IOGP S-718Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Instructions
S-718L Information Requirements for
Basic Process Measurement Instruments
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS Structure Contents
| 1 | 'Front & Preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes / No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information Submission Abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS .
Column K — 'Translation Required' (Yes / No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable Formats
Column F — 'CFIHOS Discipline Document Type Code' relates to the CFIHOS discipline document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3 below. Metadata listed below are as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The document master to which this revision is related |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification |  |  | The Export Control Rule that is applicable for the document revision (e.g., ECCN, EAR). |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
| Security classification |  |  | Indicates internal Owner-Operator access restriction applicable for the document |  |  | TBA
Table 3 — Supplier Deliverable Metadata
Public Review Draft
Public Review Draft
Copy for SC Approval
Public Review Draft
Public Review Draft

## Requirements
S-718L Information Requirements for Basic Process Measurement Instruments
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Information Deliverable Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S718-IR-1 | Supplier master information schedule |  | Information Deliverables List | Yes | For Acceptance |  | - | - |  | -
S718-IR-2 | Delivery schedule |  | Delivery/Production Schedule | Yes | For Acceptance |  | - | - |  | -
S718-IR-3 | Progress report |  | Progress Report | No | For Information |  | - | - |  | -
S718-IR-4 | Quality plan | Required for CAS A, CAS B, CAS C | Quality Plan | - | - |  | - | - |  | -
S718-IR-6 | Inspection and test plan for complete package |  | Inspection and Test Plan (ITP) | No | For Information |  | - | - |  | -
S718-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | - | - |  | -
S718-IR-8 | Non-conformance records |  | Non-conformance records | No | For Acceptance |  | - | - |  | -
S718-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | - | - |  | -
S718-IR-70 | Obsolescence Management Plan |  | Obsolescence Management Plan | Yes | For Acceptance |  | - | - |  | -
Technical Information Deliverables
S718-IR-23 | Instrument Calculations (Wake frequency calculations) |  | Instrument Calculations | Yes | For Acceptance |  | - | - |  | -
S718-IR-59 | Instrument Calculations (other) |  | Instrument calculations | No | For Acceptance |  | - | - |  | -
S718-IR-22 | General arrangement diagram |  | General Arrangement Diagram | No | For Acceptance |  | - | - |  | -
S718-IR-24 | Electrical Connection diagram |  | Connection Diagram | No | For Acceptance |  | - | - |  | -
S718-IR-36 | Certificate of conformance |  | Certificate Of Conformance | No | For Information |  | - | - |  | -
S718-IR-35 | Declaration of conformity |  | Declaration Of Conformity | No | For Information |  | - | - |  | -
S718-IR-33 | Hazardous area certificate (type) |  | Hazardous Area Certificate (Type) | Yes | For Acceptance |  | - | - |  | -
S718-IR-34 | Safety Integrity Level (SIL) Certificate |  | Safety Integrity Level (SIL) Certificate | Yes | For Acceptance |  | - | - |  | -
S718-IR-50 | Safety manual |  | Safety Manual | No | For Information |  | - | - |  | -
S718-IR-32 | Calibration certificate |  | Calibration Certificate | No | For Acceptance |  | - | - |  | -
S718-IR-39 | Spare part list |  | Spare Part List | Yes | For Acceptance |  | - | - |  | -
S718-IR-27 | Installation manual |  | Installation Manual | No | For Information |  | - | - |  | -
S718-IR-29 | Operating manual |  | Operating Manual | No | For Information |  | - | - |  | -
S718-IR-28 | Maintenance manual |  | Maintenance Manual | No | For Information |  | - | - |  | -
S718-IR-44 | Manufacturers record book |  | Manufacturer Record Book (MRB) | No | For Acceptance |  | - | - |  | -
S718-IR-55 | Instrument List |  | Instrument List | Yes | For Information |  | - | - |  | -
S718-IR-57 | Configuration file |  | Configuration file | No | For Acceptance |  | - | - |  | -
S718-IR-58 | Hook Up Diagram |  | Hook Up Diagram | No | For Acceptance |  | - | - |  | -
S718-IR-64 | Non Destructive Examination (NDE) Personnel Qualification | Required for CAS A, CAS B | Non Destructive Examination (NDE) Personnel Qualification | - | - |  | - | - |  | -
S718-IR-25 | Pressure Test Procedure |  | Pressure Test Procedure | No | For Acceptance |  | - | - |  | -
S718-IR-61 | Painting And Coating Procedure |  | Painting And Coating Procedure | No | For Acceptance |  | - | - |  | -
S718-IR-66 | Factory Acceptance Test (FAT) Procedure |  | Factory Acceptance Test (FAT) Procedure | No | For Acceptance |  | - | - |  | -
S718-IR-62 | Handling, shipping, storage and preservation procedure | Required for CAS A, CAS B | Handling, shipping and storage procedure | - | - |  | - | - |  | -
S718-IR-80 | Non Destructive Test Procedure |  | Non Destructive Test Procedure | No | For Information |  | - | - |  | -
S718-IR-43 | Non-Destructive Examination (NDE) Report | Required for CAS A, CAS B | Non-Destructive Examination (NDE) Report | - | - |  | - | - |  | -
S718-IR-30 | Pressure Test Report |  | Pressure Test Report | No | For Acceptance |  | - | - |  | -
S718-IR-41 | Positive Material Identification (PMI) Records |  | Positive Material Identification (PMI) Records | No | For Acceptance |  | - | - |  | -
S718-IR-54 | Coating Report | Required for CAS A, CAS B | Painting And Coating Inspection Records | - | - |  | - | - |  | -
S718-IR-72 | Factory Acceptance Test (FAT) Records |  | Factory Acceptance Test (FAT) Records | No | For Acceptance |  | - | - |  | -
S718-IR-67 | Application Software |  | Application Software | No | For Information |  | - | - |  | -
S718-IR-68 | Cyber Security Documentation |  | Cyber Security Documentation | No | For Acceptance |  | - | - |  | -
S718-IR-69 | Supplier Datasheet |  | Manufacturer Datasheet | Yes | For Acceptance |  | - | - |  | -
S718-IR-75 | Manufacturer's product catalog or product data sheet |  | Manufacturer Datasheet | Yes | For Information |  | - | - |  | -
S718-IR-76 | Material traceability for pressure-containing parts exposed to sour service to ISO 15156/17945 all parts. | Required for CAS A, CAS B | Materials Inspection Certificate (3.1) | - | - |  | - | - |  | -
S718-IR-77 | Material traceability for pressure-containing parts, traceable to the unique serial number. | Required for CAS A, CAS B | Materials Inspection Certificate (3.1) | - | - |  | - | - |  | -
S718-IR-78 | Material compliance for pressure retaining parts. | Required for CAS A, CAS B | Materials Test Report (2.2) | - | - |  | - | - |  | -
S718-IR-79 | Positive Material Identification (PMI) Procedure |  | Positive Material Identification (PMI) Procedure | No | For Acceptance |  | - | - |  | -
Purchase Order Specific Information Requirements
-
Public Review Draft
Public Review Draft
Public Review Draft

## Definitions
S-718L Information Requirements for Basic Process Measurement Instruments
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Discipline Document Type Code — CFIHOS discipline document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Deliverables
S718-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S718-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by [vendor/sub-vendors]. Schedule details typically** include; a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [vendor's] standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S718-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S718-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. API Specification Q1, ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] |  | PDF
S718-IR-6 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. |  | PDF | CFIHOS-70000180
S718-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. |  | PDF | CFIHOS-70000154
S718-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S718-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout | 5.1.1, 5.1.2, 5.1.3, 6.1.1, 6.1.2, 6.1.3, 7.1.1, 7.1.2, 7.1.3, 8.1.1, 8.1.2, 8.1.3, Table 1, Table 2, Table 3, Table 5, Table 6, Table 7 | PDF | CFIHOS-70000389
S718-IR-70 | Obsolescence Management Plan | The supplier to submit an obsolescence management plan in accordance with IEC 62402. The plan will provide milestone dates such as end of production (EOP) and also predicted end of supply. 1. Plan to present relevant obsolescence activities, and strategies to minimise obsolescence during design. 2. Contents. - Authorities and resources responsible for developing, reviewing and maintaining the plan. - Scope: >items being considered. >length of each items lifecycle >the organisations obsolescence management policy >the customer or end user requirements. 3. Objectives e.g. data acquisition, strategies to minimise, monitoring | 4.2.1 | PDF
Technical Information Deliverables
S718-IR-23 | Instrument Calculations (Wake frequency calculations) | This calculation shall support verification of Thermowell in accordance with ASME PTC 19.3 TW and this specification. Sizing calculations shall need to provide: - the code that it is based on - all the data that is input - Outputs and how the results are to be interpreted. Note: - collars are outside scope and would require special dispensation - It shall also state the governing case, since a calculation could be done at operating and pass but in emergency conditions it could fail.. - Calculations are to be strictly aligned with ASME PTC 19.3 TW. Any design requirements falling outside this code would require special dispensation from the purchaser. - Thermowell geometries not covered by ASME PTC 19.3 TW shall be evaluated for strength by alternative methods such as finite element analysis (FEA) or computational fluid dynamics (CFD) | 6.1.1 | Native
S718-IR-59 | Instrument Calculations (other) | This calculation shall include but not be limited to: - calculate the performance of the complete assembly e.g. in the case of diaphragm seals this would include materials, fill fluid selection and calculated range, response time and zero offset. - flow meters shall not cause flashing or cavitation at any position in the line. - In liquid applications, the pressure profile across the vortex meter shall not result in cavitation under any operating condition - Gold plating. Pressure diaphragm seals to demonstrate when hydrogen present the level of thickness required. Sizing calculations shall need to provide: - the code that it is based on - all the data that is input - Outputs and how the results are to be interpreted. Required calculations shall be agreed at point of purchase order, but in general calculations shall confirm compliance to sizing against stated codes and also compliance with declared performance figures as stated in the datasheet. | 5.1.4, 7.2.5, 8.1.5, Table 1, Table 4, Table 8 | PDF
S718-IR-22 | General arrangement diagram | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing contains reference to main specifications and standards For equipment / components the drawing may include cross sectional views. Document generally contains the following information as a minimum: • Main dimensions • Material selection for all components. • Interface connections • Weight • Installation and mounting details • Tolerance of main/critical dimensions including all elements to be machined. | 4.1.3.10, 4.1.3.3, 4.1.6, 4.3.1.1.2, 4.3.1.2.1, 4.3.1.2.2, 4.3.1.3.1, 4.3.1.3.2, 4.3.1.4.1, 4.3.3.2, 4.3.3.3, 4.3.3.4, 4.3.3.5, 4.3.3.6, 4.3.4.1, 4.3.4.2, 4.4.1.3, 4.5.3, 5.2.1, 5.2.2, 5.2.3, 5.2.4, 5.2.7, 5.3.1, 5.3.2, 5.3.3, 5.3.4, 5.3.5, 5.3.6, 6.1.5, 6.1.7, 6.1.8, 6.1.9, 6.2, 6.3.1, 6.3.2, 7.1.4, 7.2.1, 7.2.2, 7.2.3, 7.2.4, 7.2.6, 7.3.1.1, 7.3.2.1, 7.3.2.3, 7.4, 8.2.1, 8.2.2, 8.2.5, 8.2.6, 8.2.7, 8.2.8, 8.2.9, 8.3 | PDF | CFIHOS-70000153
S718-IR-24 | Electrical Connection diagram | Diagram providing information about the physical connections among components or units. Mandatory content of information: - Conductor or cable type information (e.g. recognized type designation, catalogue or part number, material, construction, size, insulation, voltage rating, colour, number of conductors, other technical data); - Reference designation or conductor or cable number; - Identification or representation of the connected objects (e.g. reference and/or terminal designation). Optional content of information: - Instruction for or methods of laying, routing, termination, attachment, twisting, screening, etc. - Length of connection - Signal designation and/or technical data about the signal - Special classification or information | 4.1.3.8, 4.1.3.9, 6.3.2 | PDF | CFIHOS-70000055
S718-IR-36 | Certificate of conformance | A statement of conformity where attestation is performed by the person or body that is independent of the person or organization that provides the object, and of user interests in that object (third party). Includes confirmation of compliance with EMC and IP ratings. | 4.2.2 | PDF | CFIHOS-70000013
S718-IR-35 | Declaration of conformity | Declaration that contains sufficient information to enable an recipient of the declaration of conformity to identify the issuer of the declaration, the object of the declaration, the standards and other specified requirements with which conformity is declared, and the person signing for and on behalf of the issuer of the declaration of conformity (first party). Mandatory content of information: Please refer to ISO/IEC 17000, clause 5.5 and ISO/IEC 17050-1:2004. | 1.1, 1.3 | PDF
S718-IR-33 | Hazardous area certificate (type) | Attestation issued by a recognised independent authority certifying that a type test has satisfied the specified standards; e.g. ATEX, BASEEFA, PTB, UL, CSA, NEMA, EX, etc. Examples of ratings include Intrinsically Safe and Explosion Proof. To include any special requirements for safe use, barrier/isolator to be used, etc. | 4.3.4.1 | PDF | CFIHOS-70000160
S718-IR-34 | Safety Integrity Level (SIL) Certificate | SIL certification by an independent and internationally recognized organization to IEC 61508, and documentation including product safety manual shall be supplied for safety function transmitters. | 4.1.4 | PDF
S718-IR-50 | Safety manual | This document is referenced in the SIL certificate and shall be provided. This document shall provide input to Safety Analysis Report. This document shall include necessary performance data according to authority regulations. | 4.1.4 | PDF
S718-IR-32 | Calibration certificate | Certification of calibration results to ISO 17025 or equivalent, including Common requirements for reports (clause ISO 17025, 7.8.2) and, a) the measurement uncertainty of the measurement result presented in the same unit as that of the measurand or in a term relative to the measurand (e.g. percent); quantity value including unit of measurement and a measurement uncertainty. b) the conditions (e.g. environmental) under which the calibrations were made that have an influence on the measurement results; c) a statement identifying how the measurements are methodologically traceable (see ISO 17025, Annex A); d) the results before and after any adjustment or repair, if available; e) where relevant, a statement of conformity with requirements or specifications (see ISO 17025, 7.8.6); f) where appropriate, opinions and interpretations (see ISO 17025, 7.8.7). Where applicable the following to be provided: - calibration factors - initial factory calibration - meter zeroing | 6.1.4, 7.3.3 | PDF | CFIHOS-70000415
S718-IR-39 | Spare part list | Table containing list items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for commissioning, start-up and operations. Mandatory content of information: – Item reference number; – Quantity; – Part number or global identifier (together with manufacturer / supplier); – Part name. Optional content of information: – Type designation; – Specifying technical data; – Descriptive technical data; – Mass, dimensions; – Reference to document; – Remark. | 4.2.1 | Native | CFIHOS-70000374
S718-IR-27 | Installation manual | Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. NOTE: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand alone document. | 4.1.1, 5.1.1, 5.1.2, 5.1.3, 6.1.1, 6.1.2, 6.1.3, 7.1.1, 7.1.2, 7.1.3, Table 1, Table 2, Table 3 | PDF | CFIHOS-70000181
S718-IR-29 | Operating manual | Description of methods of operating a piece of equipment or process unit, including but not limited to instructions, procedures, drawings, tables, etc. for the operation -stop, start, and emergency shutdown. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. NOTE: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand alone document. | 4.1.2.1 | PDF | CFIHOS-70000228
S718-IR-28 | Maintenance manual | Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package supplier. NOTE: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand alone document. | 7.3.1.1, 8.2.3, 8.2.5 | PDF | CFIHOS-70000206
S718-IR-44 | Manufacturers record book | Detailed information/description for the documents to be included in MRB as agreed between Purchaser and Vendor: Shall include but not be limited to documents Recording Compliance With Statutory and/or Local Regulations, and inspection and testing results / reports for all the testing (e.g. Mill tests on Material, production test coupon results, NDE, NDE personnel qualification, impact test, Heat treatment, leak testing etc.) carried out at Vendor/Sub-Vendor shop and at mill. | 4.2.1, 4.2.2, 4.4.1.1, 4.4.1.2, 4.4.1.3, 4.4.2.1, 4.4.2.2 | PDF
S718-IR-55 | Instrument List | an authoritative collection of values with a relationship to instrumentation. The columns of this collection is specified and controlled. Also known as Instrument Index | 4.1.2.2 | PDF | CFIHOS-70000418
S718-IR-57 | Configuration file | Supplier to provide the full list of configuration fields available for each transmitter type. Default fields to be completed for each tagged instrument including HART tag and descriptor. Vendor specific configuration files e.g. FDT, DTM to be the latest versions. Configuration to be compliant with NAMUR NE 107 which provides guidance on grouping the diagnostic data into four types to assist the operators with simplification and standardisation of information: • Check function: low severity; the signal is temporarily invalid, such as when a technician forces the device output in a loop test • Maintenance required: low severity; valid signal but function may drop or cease soon, as you see at the end of a pH sensor's lifetime • Out of specification: medium severity; device is running beyond its setup, permissible range, or other specifications • Failure: high severity device has an invalid signal due to malfunction in a sensor, instrument, or actuator NAMUR NE 107 is a widely used industry standard for grouping diagnostic data thus supports the effort for standardisation. Eliminates alarm-flooding and reduces offline analysis of data. Supports reduction in maintenance activities. Files to be compliant with NAMUR NE-43 which is a standard used to define the abnormal signal levels for 4-20 mA type output signals for example the PCS and Safety Instrumented System (SIS) detects instrument fault when the signal is less than 3.7 mA or above 20.8 mA. Note: The fault detection threshold should be determined for the control system so as to avoid alarm burst resulting from toggling in and out of fault threshold current between device and control system. Additionally device failure mode shedding shall be developed and implemented in the host control system. | 4.1.2.2, 7.3.2.2 | Native
S718-IR-58 | Hook Up Diagram | a diagram which may show the instrument impulse, pneumatic and electronic connections, pipe work, valves, fittings, flanges and support details with associated material take-off list. Used for removal/hook up purposes and modifications. Synonym: Installation details. | 5.3.2 | PDF | CFIHOS-70000167
S718-IR-64 | Non Destructive Examination (NDE) Personnel Qualification | Records demonstrating competence of NDE personnel in accordance with recognised certification program ASNT or ISO | 4.4.2.1, 4.4.2.2 | PDF
S718-IR-25 | Pressure Test Procedure | A procedure documenting specific steps to conduct inspection of an asset/object. Typically details boundaries of the test, isolations, method of pressurization, required hold intervals etc. Includes hydrostatic, pneumatic, vacuum and leak test/examinations | 4.4.1.1, 4.4.1.2 | PDF | CFIHOS-70000286
S718-IR-61 | Painting And Coating Procedure | Verification of manufacturers compliance with surface protection and coating requirements. This document provides a procedure for coating operator to ensure repeatability and formalism and hence prove the quality of the coating work. This document details the work process and how the defined requirements to surface treatment, application and quality control shall be met. A procedure may cover wet paint, powder coating, or metallic coatings. The document shall include reference to applied standards and the information about revision of the applied standard. | 4.3.2.1, 4.3.2.2, 4.3.2.3 | PDF | CFIHOS-70000384
S718-IR-66 | Factory Acceptance Test (FAT) Procedure | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document shall include all testing activities and their acceptance criteria according to applicable standards, specifications and requirements,. to document the condition of the equipment as tested from factory. Test set-up and test equipment is shall be defined. Suppliers standard (routine) test procedures should be used as far as possible | 4.1.2.2, 4.1.2.4, 4.1.3.6, 4.4.1.3, 6.1.4, 8.4.1 | PDF
S718-IR-62 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. |  | PDF | CFIHOS-70000154
S718-IR-80 | Non Destructive Test Procedure | This document is a part of the Quality Assurance Plan, and herein the Quality Assurance work process and verification. This document provides a procedure for NDT operator to ensure repeatability and formalism and hence prove the quality of the NDT work. Document describing how to perform NDT (i.e. MT, PT, RT, UT, VT or ET) for a given object, including acceptance criteria and reporting. FALSE) | 4.4.2.1, 4.4.2.2 | PDF | CFIHOS-70000227
S718-IR-43 | Non-Destructive Examination (NDE) Report | A document containing data which records compliance with specified procedure. Documents containing records of performed NDT (in typical NDT methods e.g. MT, PT, RT, UT, ET and VT). | 4.4.2.1, 4.4.2.2 | PDF
S718-IR-30 | Pressure Test Report | A report recording duration and results of hydro static, pneumatic, and leak test examinations. Typically includes a pressure chart to demonstrate satisfactory results | 4.4.1.1 | PDF | CFIHOS-70000287
S718-IR-41 | Positive Material Identification (PMI) Records | Result of Positive Material Identification testing to a defined procedure (i.e. ASTM E1086) confirming material subject to PMI are of the specified material grade. Note: • PMI results do not constitute material certification; • Requirement only covers pressure containing parts. | 4.3.1.1.1, 4.3.1.2.1 | PDF
S718-IR-54 | Coating Report | This document is used for verification of compliance with surface protection and coating requirements. Document containing records of performed surface protection and coating work. | 4.3.2.1, 4.3.2.2, 4.3.2.3 | PDF
S718-IR-72 | Factory Acceptance Test (FAT) Records | The FAT report will be used to verify that the equipment has been tested according to FAT procedure. The FAT report will be used for acceptance of the equipment delivery This document shall include all testing activities and their acceptance criteria according, , in accordance with the FAT procedure, to applicable standards, specifications and requirements,. to document the condition of the equipment as tested from factory. Test set-up and test equipment is shall be defined. | 4.1.1, 4.1.2.1, 4.1.2.3 | PDF
S718-IR-67 | Application Software | A computer program designed for a specific task or use. The software is considered as centrally procured and would form an Annex to the purchase order if required. | 4.2.1 | PDF | CFIHOS-70000012
S718-IR-68 | Cyber Security Documentation | This document shall contribute to gather all required information to perform an overall risk and vulnerability assessment of the final installation. Document definition: The Cyber Security document is intended to identify threats and risks related to information security of industrial automation and control systems that the equipment shall have countermeasures against to avoid damaging consequences. The documentation shall include: - A list of all relevant hardware components in the scope of supply. - A list of all physical ports (Ethernet, USB etc.) on each hardware - A list of all logical interfaces on the physical ports. - A list of all IP addresses - A list of all software components installed on the hardware components e.g. operating system. This document will be treated as confidential. This document should also provide information according to Norsok T-101 requirements of a cyber security vulnerability assessment. | 4.1.5.1, 4.1.5.2, 4.1.5.3, 4.1.5.4 | PDF
S718-IR-69 | Supplier Datasheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document shall provide information on technical data and characteristics about material, products or systems and their environment for proper implementation. This data sheet should include supplier completed data from IOGP S-718D. As a minimum the following additional fields should be provided: Flow meter, coriolis: Flow range, Instrument range minimum, Instrument range maximum, Turndown, Flow meter, magnetic: Maximum operating temperature, Maximum operating pressure, Flow range, Electrode type, Estimated electrode life, Power supply, Coil excitation type- ac or dc, Coil excitation frequency, Instrument range minimum, Instrument range maximum, Turndown Flow element, orifice: Plate diameter, Accuracy, Drain or vent hole diameter, Flow full scale Flow meter, ultrasonic: Number of paths/chords, Number of transducers, Path angle relative to flow, Path length, Maximum operating temperature, Maximum operating pressure, Flow range, Tube size, Transducer cable material, Transducer cable gland material, Instrument range minimum, Instrument range maximum Flow element, venturi: Cylindrical entrance section length, Conical convergent section length, Conical convergent section angle, Throat diameter, Throat section length, Conical divergent section length, Conical divergent section angle, Accuracy, Discharge coefficient Flowmeter, vortex: Face to face length, Bluff body material, Bluff body width, Insertion type, Insertion length, Pressure sensor material, Pressure sensor gasket, Operating Reynolds number range, Maximum operating viscosity, Maximum operating temperature, Maximum operating pressure, Flow range, Cable length, Instrument range minimum, Instrument range maximum Level, magnetic gauge: Minimum working pressure, Maximum working pressure, Minimum working temperature, Maximum working temperature Level, radar non-contact: Insertion depth (dielectric rod), Microwave output power, Operating frequency, Minimum dielectric, Antenna pressure range, Antenna temperature range, Level offset (tank bottom), Beam angle, Beam spread range, Instrument range minimum, Instrument range maximum, Calibration range minimum, Calibration range maximum, Body rating, Cooling extension, Cooling extension length Level, guided wave: Probe diameter, Prove sheath, Probe maximum viscosity, Upper fluid minimum thickness, Upper fluid dielectric limits, Lower fluid dielectric limits, Blocking distance, Level offset (tank bottom), Instrument range minimum, Instrument range maximum, Body rating Level, hydrostatic: Element type, Pressure element type, Over range limit, Allowable temperature, Maximum temperature, Maximum pressure Pressure, transmitter: Element type, Pressure element type, Over range limit, Allowable temperature, Maximum temperature, Maximum pressure, Blocking distance Pressure, differential: Element type, Pressure element type, Over range limit, Allowable temperature, Maximum temperature, Maximum pressure Temperature, transmitter: Thermal shock, TW coating, TW treatment, TW finish, TW back-up flange, TW weldolet fitting, TW stamping | 4.1.1, 4.1.2.3, 4.1.3.7, 4.1.6, 4.2.1, 4.2.2, 4.3.1.1.5, 4.3.1.2.3, 4.3.1.4.1, 5.1.5, 6.1.6, 7.1.5, 7.3.1.2, 8.1.4 | PDF | CFIHOS-70000416
S718-IR-75 | Manufacturer's product catalog or product data sheet | A document that defines the product features, functional description operating and ambient conditions, decoding details of the quoted model, performance capabilities, dimensional details, weights, design and testing standards and interface details that fulfil the purchasers technical requirements. | 4.1.3.1, 4.1.3.11, 4.1.3.4, 4.1.3.5, 4.3.1.3.3, 5.1.5, 5.3.7, 5.3.8, 6.1.6, 7.1.5, Table 8 | PDF | CFIHOS-70000416
S718-IR-76 | Material traceability for pressure-containing parts exposed to sour service to ISO 15156/17945 all parts. | A document with test results based on specific inspection and testing, issued by the Manufacturer and validated by the Manufacturer's authorised inspection representative independent of the manufacturing department. NOTE: see ISO/IEC 17000, clause 5.5 and ISO 10474 / EN 10204. | 4.1.1, 4.3.1.2.1, 4.3.1.2.2 | PDF | CFIHOS-70000412
S718-IR-77 | Material traceability for pressure-containing parts, traceable to the unique serial number. | A document with test results based on specific inspection and testing, issued by the Manufacturer and validated by the Manufacturer's authorised inspection representative independent of the manufacturing department. NOTE: see ISO/IEC 17000, clause 5.5 and ISO 10474 / EN 10204. | 4.1.1 | PDF | CFIHOS-70000412
S718-IR-78 | Material compliance for pressure retaining parts. | A document in which the supplier declares that the products supplied are in compliance with the requirements of the PO, and in which test results are supplied based on non-specific inspection and testing NOTE: see ISO/IEC 17000, clause 5.5 and ISO 10474 / EN 10204. | 4.4.1.1 | PDF | CFIHOS-70000412
S718-IR-79 | Positive Material Identification (PMI) Procedure | Procedure describing the method for material identification by elemental analysis. Following API RP 578 - Guidelines for a Material Verification Program (MVP) for New and Existing Assets. | 4.1.1 | PDF
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Back Cover
Month XXXX
Public Review Draft

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
Intelligent Vector (CAD)
Multi media (Film)
Raster Image (Bitmap)
Structured Data (MS Apps)
Technical Publication (Text)
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell:
Public Review Draft