## Front & Preliminaries
|  |  |  | SPECIFICATION | November
|  |  |  | S-718D | 2021
Procurement Data Sheets for
Basic Process Measurement Instruments
Revision history
| VERSION | DATE | PURPOSE
| 0.3 | November 2021 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-718D Data Sheets for
Basic Process Measurement Instruments
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
S-718D Data Sheets for
Basic Process Measurement Instruments
Introduction
The purpose of these procurement data sheets is to define purchaser specific requirements for the procurement of basic process measurement instruments in accordance with IOGP S-718 for application in the petroleum and natural gas industries. The procurement data sheets provide project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheets to define scope and technical requirements for enquiry and purchase of the equipment.
These procurement data sheet shall be used in conjunction with the specification (IOGP S-718), information requirements specification (IOGP S-718L) and quality requirements specification (IOGP S-718Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Flow Transmitter, Coriolis
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Flow Transmitter, Coriolis | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
21 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
22 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
23 | 4.3.1.1.2, 4.3.1.2.1 | Bolt pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
24 | 4.3.1.2.1 | Nut pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
25 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
26 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
27 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
28 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
29 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
30 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
31 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
32 |  | Equipment / line conditions
33 |  | Upstream / high-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
34 | 7.2.1 | Upstream / high-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
35 |  | Upstream / high-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
36 |  | Upstream / high-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
37 |  | Upstream / high-side connection orientation : | input data |  | input data
38 |  | Upstream / high-side material type : | input data |  | input data
39 |  | Downstream / low-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
40 |  | Downstream / low-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
41 |  | Downstream / low-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
42 |  | Downstream / low-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
43 |  | Downstream / low-side connection orientation : | input data |  | input data
44 |  | Downstream / low-side material type : | input data |  | input data
45 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
46 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
47 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
48 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
49 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
50 |  | Operating conditions
51 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
52 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
53 |  | Process fluid corrosive compounds : | input data |  | input data
54 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
55 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
56 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kpaa
57 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
58 |  | Minimum operating velocity : | input data | m/s | input data | m/s
59 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
60 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
61 |  | Minimum operating liquid specific gravity : | input data |  | input data
62 |  | Minimum operating liquid specific gravity at standard conditions : | input data |  | input data
63 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
64 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
65 |  | Minimum operating vapour compressibility factor : | input data |  | input data
66 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
67 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
68 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
69 |  | Normal operating velocity : | input data | m/s | input data | m/s
70 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
71 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
72 |  | Normal operating liquid specific gravity : | input data |  | input data
73 |  | Normal operating liquid specific gravity at standard conditions : | input data |  | input data
74 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
75 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
76 |  | Normal operating vapour compressibility factor : | input data |  | input data
77 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
78 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
79 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
80 |  | Maximum operating velocity : | input data | m/s | input data | m/s
81 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
82 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
83 |  | Maximum operating liquid specific gravity : | input data |  | input data
84 |  | Maximum operating liquid specific gravity at standard conditions : | input data |  | input data
85 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
86 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
87 |  | Maximum operating vapour compressibility factor : | input data |  | input data
88 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
89 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
90 |  | Maximum recoverable pressure drop : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH₂O
91 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH₂O
92 |  | Body/element/sensor
93 |  | Body/element/sensor manufacturer model number : | input data |  | input data
94 | 7.2.2, 7.3.2.3 | Body material : | input data |  | input data
95 |  | Coriolis tube material : | input data |  | input data
96 |  | Coriolis tube type : | select |  | select | [5 empty] | select | bent | straight
97 |  | Flange material : | input data |  | input data
98 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in
99 |  | Body flange connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
100 |  | Body flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF
101 |  | Body flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
102 |  | Coriolis flowtube type : | input data |  | input data
103 |  | Coriolis outer casing material : | input data |  | input data
104 |  | Coriolis outer casing burst pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
105 |  | Transmitter
106 |  | Transmitter manufacturer model number. : | input data |  | input data
107 |  | Transmitter enclosure material : | input data |  | input data
108 |  | Transmitter location : | integrated |  | integrated | [5 empty] | select | integrated | remote
109 |  | Transmitter connecting cables : | no |  | no | [5 empty] | select | yes | no
110 |  | Transmitter connecting cable length : | input data | select | input data | select |  |  |  |  | select | m | ft
111 |  | Transmitter connecting cable quantity : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4
112 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
113 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | V AC | V DC
114 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | yes | no | not applicable
115 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
116 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
117 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
118 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
119 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
120 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
121 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
122 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
123 |  | Performance
124 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
125 |  | Uncertainty : | input data |  | input data
126 |  | Repeatability : | input data | % | input data | %
127 | 4.2.2 | Vibration : | input data |  | input data
128 |  | Accessories
129 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
130 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Declaration of the units to be used either select "normal" or "standard".
Note on C19: Temperature to be used for base units.
Note on C20: Pressure to be used to support the base units.
Note on C21: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C22: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C23: Bolting material for pressure retaining applications as detailed in IOGP S-563.
Note on C24: Populate the nut material in line with IOGP S-563.
Note on C25: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C26: Ingress protection rating in IP or NEMA.
Note on C27: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C28: Code to be followed for the hazardous area classification.
Note on C29: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C30: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C31: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C33: Selection of the pipe schedule in accordance with the pipe specification.
Note on C34: Process line size to be declared to support sizing and selection by the supplier.
Note on C35: Pressure rating of the system connected.
Note on C36: Instrument process connection to be compatible with that declared by the purchaser.
Note on C37: Orientation of the inlet to the instrument or insertion point.
Note on C38: Material for the instrument to connect to on the upstream face.
Note on C39: Selection of the pipe schedule in accordance with the pipe specification.
Note on C40: Process line size downstream to be declared to support sizing and selection by the supplier.
Note on C41: Pressure rating of the system connected.
Note on C42: Process connection to the system.
Note on C43: Orientation of the inlet or insertion point of the instrument.
Note on C44: Material for the instrument to connect to on the downstream face.
Note on C45: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C46: This figure should be the minimum design pressure of the system installed into.
Note on C47: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C48: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C49: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C51: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C52: Confirm whether it is a liquid or vapour phase.
Note on C53: Free field to input any corrosive elements in the process stream
Note on C54: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C55: Purchaser to declare if the instrument would see a vacuum.
Note on C56: Vapour pressure of the flowing fluid
Note on C57: Operating mass flow rate of the system to which it is installed at the minimum sizing case.
Note on C58: Operating velocity of the system at the minimum sizing case.
Note on C59: Temperature of the process at the minimum sizing case.
Note on C60: Differential pressure of the process at the minimum sizing case.
Note on C61: Specific gravity of the process fluid at the min sizing case
Note on C62: Liquid SG at standard conditions at the minimum sizing case.
Note on C63: Viscosity of the process fluid at minimum sizing conditions
Note on C64: Vapour molecular weight of the process fluid at minimum sizing conditions
Note on C65: Vapour compressibility factor at minimum sizing conditions
Note on C66: Vapour actual density at minimum sizing conditions
Note on C67: Vapour viscosity at minimum sizing conditions.
Note on C68: Normal operating flow rate of the system to which it is installed
Note on C69: Operating velocity of the system at the normal sizing case.
Note on C70: Temperature of the process at the minimum sizing case.
Note on C71: Pressure of the process for the normal operating case.
Note on C72: Specific gravity of the process fluid at the normal sizing case
Note on C73: Liquid SG at standard conditions at the normal sizing case.
Note on C74: Viscosity of the process fluid at the normal sizing case.
Note on C75: Vapour molecular weight of the process fluid at normal sizing conditions.
Note on C76: Vapour compressibility factor at normal sizing conditions.
Note on C77: Vapour actual density at normal sizing conditions.
Note on C78: Vapour viscosity at normal sizing conditions.
Note on C79: Operating mass flow rate of the system to which it is installed at maximum sizing case.
Note on C80: Operating velocity of the system at the maximum sizing case.
Note on C81: Temperature of the process at the minimum sizing case.
Note on C82: Pressure of the process for the maximum operating case.
Note on C83: Specific gravity of the process fluid at the maximum sizing case.
Note on C84: Liquid SG at standard conditions at the maximum sizing case.
Note on C85: Viscosity of the process fluid at maximum sizing conditions.
Note on C86: Vapour molecular weight of the process fluid at maximum sizing conditions.
Note on C87: Vapour compressibility factor at maximum sizing conditions.
Note on C88: Vapour actual density at minimum sizing conditions.
Note on C89: Vapour viscosity at maximum sizing conditions.
Note on C90: Purchaser to declare the maximum pressure drop that can be catered for across the meter at any point in the flow range.
Note on C91: Input the value as per process data sheet.
Note on C93: Supplier to specify model number of body/element/sensor.
Note on C94: The material of main instrument body is a wetted part and should be suitable for the process fluids.
Note on C95: The material for the tube to be compatible with process conditions and mechanical response requirements.
Note on C96: Confirmation whether the tube is bent or straight.
Note on C97: Input the flange material to be compatible with process conditions, fluid and process connection.
Note on C98: Input the selected instrument body size.
Note on C99: Size of the connection to the process line or equipment.
Note on C100: Flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C101: Flange rating to match the rating of the system to which it is connected.
Note on C102: Flowtube type to be declared
Note on C103: Input Material of the outer casing surrounding the tubes.
Note on C104: Confirmation of the burst pressure that the casing is designed to.
Note on C106: Model number for transmitter only.
Note on C107: Material offered to meet the minimum requirements.
Note on C108: Confirm whether a single integrated assembly or a transmitter to be remotely mounted. Default value : integrated
Note on C109: are external cables required for connection between sensor and transmitter housing or are they integral Default value : no
Note on C110: Provide the length of cable to support routing from the flow meter body to the transmitter housing.
Note on C111: Supplier to advise the number of cables needed between the body and transmitter head.
Note on C112: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C113: External power supply to the flow transmitter to be stated, if loop powered the input "N/A".
Note on C114: Select "yes" if isolated from power supply; "no" if not isolated from power supply, "not applicable" if unit is loop powered hence not applicable. Default value : not applicable
Note on C115: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C116: Communication protocol for the transmitter. Default value : HART
Note on C117: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C118: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C119: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C120: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C121: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C122: Highest value of the measured variable that a device can be adjusted to measure.
Note on C124: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C125: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C126: Repeatabiily of the instrument selected in accordance with the guidelines set out in IEC 62828 series
Note on C127: Vibration to be selected in accordance with the requirements of IEC 62828-1 table 4, typical value is "10 to 1000 Hz with 0,15mm peak amplitude and 20m/s²".
Note on C129: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C130: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Flow Transmitter, Magnetic
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Flow Transmitter, Magnetic | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
21 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
22 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
23 | 4.3.1.1.2, 4.3.1.2.1 | Bolt pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
24 | 4.3.1.2.1 | Nut pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
25 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
26 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
27 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
28 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
29 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
30 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
31 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
32 |  | Equipment / line conditions
33 |  | Upstream / high-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
34 | 7.2.1 | Upstream / high-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
35 |  | Upstream / high-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
36 |  | Upstream / high-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
37 |  | Upstream / high-side connection orientation : | input data |  | input data
38 |  | Upstream / high-side material type : | input data |  | input data
39 |  | Downstream / low-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
40 |  | Downstream / low-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
41 |  | Downstream / low-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
42 |  | Downstream / low-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
43 |  | Downstream / low-side connection orientation : | input data |  | input data
44 |  | Downstream / low-side material type : | input data |  | input data
45 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
46 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
47 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
48 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
49 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
50 |  | Operating conditions
51 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
52 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
53 |  | Process fluid corrosive compounds : | input data |  | input data
54 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
55 |  | Process fluid conductivity : | input data | µS | input data | µS
56 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
57 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kpaa
58 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
59 | 7.3.3 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
60 |  | Minimum operating velocity : | input data | m/s | input data | m/s
61 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
62 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
63 |  | Minimum operating liquid specific gravity : | input data |  | input data
64 |  | Minimum operating liquid specific gravity at standard conditions : | input data |  | input data
65 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
66 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
67 |  | Minimum operating vapour compressibility factor : | input data |  | input data
68 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
69 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
70 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
71 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
72 |  | Normal operating velocity : | input data | m/s | input data | m/s
73 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
74 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
75 |  | Normal operating liquid specific gravity : | input data |  | input data
76 |  | Normal operating liquid specific gravity at standard conditions : | input data |  | input data
77 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
78 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
79 |  | Normal operating vapour compressibility factor : | input data |  | input data
80 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
81 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
82 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
83 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
84 |  | Maximum operating velocity : | input data | m/s | input data | m/s
85 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
86 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
87 |  | Maximum operating liquid specific gravity : | input data |  | input data
88 |  | Maximum operating liquid specific gravity at standard conditions : | input data |  | input data
89 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
90 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
91 |  | Maximum operating vapour compressibility factor : | input data |  | input data
92 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
93 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
94 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH₂O
95 |  | Body/element/sensor
96 |  | Body/element/sensor manufacturer model number : | input data |  | input data
97 | 7.2.2, 7.3.2.3 | Body material : | input data |  | input data
98 |  | Flange material : | input data |  | input data
99 | 7.3.2.1 | Liner material : | input data |  | input data
100 |  | Coil cover material : | input data |  | input data
101 | 4.3.1.3.1 | Termination box material : | input data |  | input data
102 | 7.3.2.3 | Electrode type : | input data |  | input data
103 | 7.3.2.3 | Electrode material : | input data |  | input data
104 |  | Minimum conductivity : | input data |  | input data
105 |  | Grounding ring : | select |  | select | [5 empty] | select | yes | no
106 | 7.3.2.3 | Grounding ring material : | input data |  | input data
107 |  | Lining protector : | select |  | select | [5 empty] | select | yes | no
108 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in
109 |  | Body flange connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
110 |  | Body flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF
111 |  | Body flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
112 |  | Transmitter
113 |  | Transmitter manufacturer model number. : | input data |  | input data
114 |  | Transmitter enclosure material : | input data |  | input data
115 |  | Transmitter location : | integrated |  | integrated | [5 empty] | select | integrated | remote
116 |  | Transmitter connecting cables : | no |  | no | [5 empty] | select | yes | no
117 |  | Transmitter connecting cable length : | input data | select | input data | select |  |  |  |  | select | m | ft
118 |  | Transmitter connecting cable quantity : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4
119 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
120 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | V AC | V DC
121 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | yes | no | not applicable
122 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
123 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
124 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
125 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
126 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
127 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
128 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
129 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
130 |  | Performance
131 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
132 |  | Uncertainty : | input data |  | input data
133 |  | Repeatability : | input data | % | input data | %
134 | 4.2.2 | Vibration : | input data |  | input data
135 |  | Accessories
136 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
137 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Declaration of the units to be used either select "normal" or "standard".
Note on C19: Temperature to be used for base units.
Note on C20: Pressure to be used to support the base units.
Note on C21: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C22: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C23: Bolting material for pressure retaining applications as detailed in IOGP S-563.
Note on C24: Populate the nut material in line with IOGP S-563.
Note on C25: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C26: Ingress protection rating in IP or NEMA.
Note on C27: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C28: Code to be followed for the hazardous area classification.
Note on C29: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C30: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C31: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C33: Selection of the pipe schedule in accordance with the pipe specification.
Note on C34: Process line size to be declared to support sizing and selection by the supplier.
Note on C35: Pressure rating of the system connected.
Note on C36: Instrument process connection to be compatible with that declared by the purchaser.
Note on C37: Orientation of the inlet to the instrument or insertion point.
Note on C38: Material for the instrument to connect to on the upstream face.
Note on C39: Selection of the pipe schedule in accordance with the pipe specification.
Note on C40: Process line size downstream to be declared to support sizing and selection by the supplier.
Note on C41: Pressure rating of the system connected.
Note on C42: Process connection to the system.
Note on C43: Orientation of the inlet or insertion point of the instrument.
Note on C44: Material for the instrument to connect to on the downstream face.
Note on C45: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C46: This figure should be the minimum design pressure of the system installed into.
Note on C47: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C48: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C49: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C51: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C52: Confirm whether it is a liquid or vapour phase.
Note on C53: Free field to input any corrosive elements in the process stream
Note on C54: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C55: Free field for the purchaser to declare the conductivity of the process fluid
Note on C56: Purchaser to declare if the instrument would see a vacuum.
Note on C57: Vapour pressure of the flowing fluid
Note on C58: Operating mass flow rate of the system to which it is installed at the minimum sizing case.
Note on C59: Operating volumetric flow rate of the system at mimimum sizing case
Note on C60: Operating velocity of the system at the minimum sizing case.
Note on C61: Temperature of the process at the minimum sizing case.
Note on C62: Differential pressure of the process at the minimum sizing case.
Note on C63: Specific gravity of the process fluid at the min sizing case
Note on C64: Liquid SG at standard conditions at the minimum sizing case.
Note on C65: Viscosity of the process fluid at minimum sizing conditions
Note on C66: Vapour molecular weight of the process fluid at minimum sizing conditions
Note on C67: Vapour compressibility factor at minimum sizing conditions
Note on C68: Vapour actual density at minimum sizing conditions
Note on C69: Vapour viscosity at minimum sizing conditions.
Note on C70: Normal operating flow rate of the system to which it is installed
Note on C71: Operating volumetric flow rate of the system at normalsizing case
Note on C72: Operating velocity of the system at the normal sizing case.
Note on C73: Temperature of the process at the minimum sizing case.
Note on C74: Pressure of the process for the normal operating case.
Note on C75: Specific gravity of the process fluid at the normal sizing case
Note on C76: Liquid SG at standard conditions at the normal sizing case.
Note on C77: Viscosity of the process fluid at the normal sizing case.
Note on C78: Vapour molecular weight of the process fluid at normal sizing conditions.
Note on C79: Vapour compressibility factor at normal sizing conditions.
Note on C80: Vapour actual density at normal sizing conditions.
Note on C81: Vapour viscosity at normal sizing conditions.
Note on C82: Operating mass flow rate of the system to which it is installed at maximum sizing case.
Note on C83: Operating volumetric flow rate of the system at maximum sizing case.
Note on C84: Operating velocity of the system at the maximum sizing case.
Note on C85: Temperature of the process at the minimum sizing case.
Note on C86: Pressure of the process for the maximum operating case.
Note on C87: Specific gravity of the process fluid at the maximum sizing case.
Note on C88: Liquid SG at standard conditions at the maximum sizing case.
Note on C89: Viscosity of the process fluid at maximum sizing conditions.
Note on C90: Vapour molecular weight of the process fluid at maximum sizing conditions.
Note on C91: Vapour compressibility factor at maximum sizing conditions.
Note on C92: Vapour actual density at minimum sizing conditions.
Note on C93: Vapour viscosity at maximum sizing conditions.
Note on C94: Input the value as per process data sheet.
Note on C96: Supplier to specify model number of body/element/sensor.
Note on C97: The material of main instrument body is a wetted part and should be suitable for the process fluids.
Note on C98: Input the flange material to be compatible with process conditions, fluid and process connection.
Note on C99: If required state the liner material.
Note on C100: Specify the external cover material surrounding the wiring coils.
Note on C101: Specify the material for JB mounted on the flow body (used to terminate the coils).
Note on C102: Input the electrode type.
Note on C103: Input the electrode material that is in contact with the process medium.
Note on C104: Minimum conductivity of the process fluid that the electrodes are able to measure.
Note on C105: Supplier to advise whether a grounding ring is needed for correct operation of the mag flow meter.
Note on C106: If a grounding ring is required by supplier the material is to be stated.
Note on C107: Supplier to advise whether a lining protector is needed to protect sensor from abrasive fluids.
Note on C108: Input the selected instrument body size.
Note on C109: Size of the connection to the process line or equipment.
Note on C110: Flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C111: Flange rating to match the rating of the system to which it is connected.
Note on C113: Model number for transmitter only.
Note on C114: Material offered to meet the minimum requirements.
Note on C115: Confirm whether a single integrated assembly or a transmitter to be remotely mounted. Default value : integrated
Note on C116: are external cables required for connection between sensor and transmitter housing or are they integral Default value : no
Note on C117: Provide the length of cable to support routing from the flow meter body to the transmitter housing.
Note on C118: Supplier to advise the number of cables needed between the body and transmitter head.
Note on C119: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C120: External power supply to the flow transmitter to be stated, if loop powered the input "N/A".
Note on C121: Select "yes" if isolated from power supply; "no" if not isolated from power supply, "not applicable" if unit is loop powered hence not applicable. Default value : not applicable
Note on C122: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C123: Communication protocol for the transmitter. Default value : HART
Note on C124: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C125: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C126: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C127: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C128: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C129: Highest value of the measured variable that a device can be adjusted to measure.
Note on C131: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C132: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C133: Repeatabiily of the instrument selected in accordance with the guidelines set out in IEC 62828 series
Note on C134: Vibration to be selected in accordance with the requirements of IEC 62828-1 table 4, typical value is "10 to 1000 Hz with 0,15mm peak amplitude and 20m/s²".
Note on C136: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C137: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Flow Element, Orifice
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Flow Element, Orifice | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Instrumentation type : | select |  | select | [5 empty] | select | restriction orifice | orifice plate (square edge concentric) | orifice plate (conical entrance) | orifice plate (quarter circle) | orifice plate (eccentric) | restriction orifice paddle type | orifice plate paddle type (square edge concentric) | orifice plate paddle type (conical entrance) | orifice plate paddle type (quarter circle) | orifice plate paddle type (eccentric) | orifice plate paddle type (square edge concentric) | orifice plate paddle type (conical entrance) | orifice plate paddle type (quarter circle) | orifice plate paddle type (eccentric)
5 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
6 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
7 | 4.1.2.2 | Tag number : | input data |  | input data
8 |  | Tag description : | input data |  | input data
9 |  | Manufacturer : | input data |  | input data
10 |  | Assembly model number : | input data |  | input data
11 |  | Equipment manufacturer serial number : | input data |  | input data
12 |  | Project country : | input data |  | input data
13 |  | Project region : | input data |  | input data
14 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
15 |  | P&ID number : | input data |  | input data
16 |  | Line or equipment number : | input data |  | input data
17 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
19 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
20 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
21 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
22 |  | Equipment / line conditions
23 |  | Upstream / high-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
24 | 7.2.1 | Upstream / high-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
25 |  | Upstream / high-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
26 |  | Upstream / high-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
27 |  | Upstream / high-side connection orientation : | input data |  | input data
28 |  | Upstream / high-side material type : | input data |  | input data
29 |  | Downstream / low-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
30 |  | Downstream / low-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
31 |  | Downstream / low-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
32 |  | Downstream / low-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
33 |  | Downstream / low-side connection orientation : | input data |  | input data
34 |  | Downstream / low-side material type : | input data |  | input data
35 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
36 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
37 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
38 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
39 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
40 | 7.2.4 | Insulation thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
41 |  | Operating conditions
42 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
43 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
44 |  | Process fluid corrosive compounds : | input data |  | input data
45 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
46 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
47 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kpaa
48 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
49 | 7.3.3 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
50 |  | Minimum operating velocity : | input data | m/s | input data | m/s
51 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
52 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
53 |  | Minimum operating liquid specific gravity : | input data |  | input data
54 |  | Minimum operating liquid specific gravity at standard conditions : | input data |  | input data
55 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
56 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
57 |  | Minimum operating vapour compressibility factor : | input data |  | input data
58 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
59 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
60 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
61 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
62 |  | Normal operating velocity : | input data | m/s | input data | m/s
63 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
64 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
65 |  | Normal operating liquid specific gravity : | input data |  | input data
66 |  | Normal operating liquid specific gravity at standard conditions : | input data |  | input data
67 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
68 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
69 |  | Normal operating vapour compressibility factor : | input data |  | input data
70 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
71 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
72 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
73 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
74 |  | Maximum operating velocity : | input data | m/s | input data | m/s
75 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
76 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
77 |  | Maximum operating liquid specific gravity : | input data |  | input data
78 |  | Maximum operating liquid specific gravity at standard conditions : | input data |  | input data
79 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
80 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
81 |  | Maximum operating vapour compressibility factor : | input data |  | input data
82 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
83 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
84 |  | Maximum recoverable pressure drop : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH₂O
85 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH₂O
86 |  | Body/element/sensor
87 | 7.2.2, 7.3.2.3 | Body material : | input data |  | input data
88 |  | Pressure differential at maximum flow : | input data | select | input data | select |  |  |  |  | select | mbar | inH2O
89 |  | Orifice bore diameter : | input data | select | input data | select |  |  |  |  | select | mm | in
90 |  | Beta ratio (d/D) : | input data |  | input data
91 |  | Differential pressure minimum range : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
92 |  | Differential pressure maximum range : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
93 |  | Orifice vent or drain hole : | not applicable |  | not applicable | [5 empty] | select | vent only | drain only | both | not applicable
94 |  | Orifice plate thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
95 |  | Quick change fitting
96 |  | Manufacturer : | input data |  | input data
97 |  | Manufacturer model number : | input data |  | input data
98 |  | Quick change fitting rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
99 |  | Removal under line pressure : | yes |  | yes | [5 empty] | select | yes | no
100 |  | Pressure containing material : | input data |  | input data
101 |  | Internals material : | input data |  | input data
102 |  | O-ring material : | input data |  | input data
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Select the instrument type (technology) to be purchased
Note on C5: Code compliance to be for the region where the instrument is to be installed.
Note on C6: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C7: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C8: A functional description of the tag.
Note on C9: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C10: Input the model number of the offered instrument assembly / unit.
Note on C11: Unique identification number for the equipment as prescribed by the supplier.
Note on C12: Name assigned by ISO to the country, in ISO 3166-1.
Note on C13: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C14: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C15: P&ID number where the orifice plate assembly is indicated
Note on C16: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C17: Fill in as per process data
Note on C18: Fill in as per process data
Note on C19: Declaration of the units to be used either select "normal" or "standard".
Note on C20: Temperature to be used for base units.
Note on C21: Pressure to be used to support the base units.
Note on C23: Selection of the pipe schedule in accordance with the pipe specification.
Note on C24: Process line size to be declared to support sizing and selection by the supplier.
Note on C25: Pressure rating of the system connected.
Note on C26: Instrument process connection to be compatible with that declared by the purchaser.
Note on C27: Orientation of the inlet to the instrument or insertion point.
Note on C28: Material for the instrument to connect to on the upstream face.
Note on C29: Selection of the pipe schedule in accordance with the pipe specification.
Note on C30: Process line size downstream to be declared to support sizing and selection by the supplier.
Note on C31: Pressure rating of the system connected.
Note on C32: Process connection to the system.
Note on C33: Orientation of the inlet or insertion point of the instrument.
Note on C34: Material for the instrument to connect to on the downstream face.
Note on C35: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C36: This figure should be the minimum design pressure of the system installed into.
Note on C37: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C38: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C39: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C40: Insulation material thickness of the process pipe, vessel or equipment where the thermowell or orifice plate is connected.
Note on C42: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C43: Confirm whether it is a liquid or vapour phase.
Note on C44: Free field to input any corrosive elements in the process stream
Note on C45: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C46: Purchaser to declare if the instrument would see a vacuum.
Note on C47: Vapour pressure of the flowing fluid
Note on C48: Operating mass flow rate of the system to which it is installed at the minimum sizing case.
Note on C49: Operating volumetric flow rate of the system at mimimum sizing case
Note on C50: Operating velocity of the system at the minimum sizing case.
Note on C51: Temperature of the process at the minimum sizing case.
Note on C52: Differential pressure of the process at the minimum sizing case.
Note on C53: Specific gravity of the process fluid at the min sizing case
Note on C54: Liquid SG at standard conditions at the minimum sizing case.
Note on C55: Viscosity of the process fluid at minimum sizing conditions
Note on C56: Vapour molecular weight of the process fluid at minimum sizing conditions
Note on C57: Vapour compressibility factor at minimum sizing conditions
Note on C58: Vapour actual density at minimum sizing conditions
Note on C59: Vapour viscosity at minimum sizing conditions.
Note on C60: Normal operating flow rate of the system to which it is installed
Note on C61: Operating volumetric flow rate of the system at normalsizing case
Note on C62: Operating velocity of the system at the normal sizing case.
Note on C63: Temperature of the process at the minimum sizing case.
Note on C64: Pressure of the process for the normal operating case.
Note on C65: Specific gravity of the process fluid at the normal sizing case
Note on C66: Liquid SG at standard conditions at the normal sizing case.
Note on C67: Viscosity of the process fluid at the normal sizing case.
Note on C68: Vapour molecular weight of the process fluid at normal sizing conditions.
Note on C69: Vapour compressibility factor at normal sizing conditions.
Note on C70: Vapour actual density at normal sizing conditions.
Note on C71: Vapour viscosity at normal sizing conditions.
Note on C72: Operating mass flow rate of the system to which it is installed at maximum sizing case.
Note on C73: Operating volumetric flow rate of the system at maximum sizing case.
Note on C74: Operating velocity of the system at the maximum sizing case.
Note on C75: Temperature of the process at the minimum sizing case.
Note on C76: Pressure of the process for the maximum operating case.
Note on C77: Specific gravity of the process fluid at the maximum sizing case.
Note on C78: Liquid SG at standard conditions at the maximum sizing case.
Note on C79: Viscosity of the process fluid at maximum sizing conditions.
Note on C80: Vapour molecular weight of the process fluid at maximum sizing conditions.
Note on C81: Vapour compressibility factor at maximum sizing conditions.
Note on C82: Vapour actual density at minimum sizing conditions.
Note on C83: Vapour viscosity at maximum sizing conditions.
Note on C84: Purchaser to declare the maximum pressure drop that can be catered for across the meter at any point in the flow range.
Note on C85: Input the value as per process data sheet.
Note on C87: The material of main instrument body is a wetted part and should be suitable for the process fluids.
Note on C88: DP ranges generally to be 0 to 250 mbar (0 to 100 in H2O). However, if approved by the company engineer, it can also be one from, 0 to 50 mbar (0 to 20 in H2O), 0 to 100 mbar (0 to 50 in H2O, note, not 40 in H2O), 0 to 500 mbar (0 to 200 in H2O)
Note on C89: Purchaser to provide estimated dimension. Supplier to input the final diameter after approval of the sizing calculations.
Note on C90: Input the ratio of d/D after orifice sizing calculations.
Note on C91: Differential pressure range associated with the minimum flow rates of the fluid being measured.
Note on C92: Differential pressure range associated with the maximum flow rates of the fluid being measured.
Note on C93: Select "vent only", "drain only" or "both"; select "N/A" if not required. Default value : not applicable
Note on C94: Follow the recommendations from ISO 5167-2 to ensure the minimum thickness is met. Default value : mm
Note on C96: The manufacturer can be 3rd party supply
Note on C97: Model number for quick change fitting assembly.
Note on C98: Rating of quick change fitting unit to be supplied
Note on C99: Select "yes" for change of orifice without interruption to service, select "no" if the isolation and depressurization of the holder is required. Default value : yes
Note on C100: All components subject to the line pressure e.g. body, bonnet.
Note on C101: Input the internals material of the quick change fitting, input "N/A" if not required.
Note on C102: O-ring material to meet the specified process requirements, and if ED then relevant type.

## Flow Transmitter, Ultrasonic
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Flow Transmitter, Ultrasonic | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Instrumentation type : | select |  | select | [5 empty] | select | ultrasonic flowmeter (multi-path inline) | ultrasonic flowmeter (clamp-on)
5 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
6 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
7 | 4.1.2.2 | Tag number : | input data |  | input data
8 |  | Tag description : | input data |  | input data
9 |  | Manufacturer : | input data |  | input data
10 |  | Assembly model number : | input data |  | input data
11 |  | Equipment manufacturer serial number : | input data |  | input data
12 |  | Project country : | input data |  | input data
13 |  | Project region : | input data |  | input data
14 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
15 |  | P&ID number : | input data |  | input data
16 |  | Line or equipment number : | input data |  | input data
17 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
19 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
20 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
21 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
22 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
23 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
24 | 4.3.1.1.2, 4.3.1.2.1 | Bolt pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
25 | 4.3.1.2.1 | Nut pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
26 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
27 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
28 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
29 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
30 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
31 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
32 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
33 |  | Equipment / line conditions
34 |  | Upstream / high-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
35 | 7.2.1 | Upstream / high-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
36 |  | Upstream / high-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
37 |  | Upstream / high-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
38 |  | Upstream / high-side connection orientation : | input data |  | input data
39 |  | Upstream / high-side material type : | input data |  | input data
40 |  | Downstream / low-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
41 |  | Downstream / low-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
42 |  | Downstream / low-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
43 |  | Downstream / low-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
44 |  | Downstream / low-side connection orientation : | input data |  | input data
45 |  | Downstream / low-side material type : | input data |  | input data
46 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
47 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
48 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
49 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
50 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
51 |  | Operating conditions
52 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
53 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
54 |  | Process fluid corrosive compounds : | input data |  | input data
55 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
56 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
57 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kpaa
58 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
59 | 7.3.3 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
60 |  | Minimum operating velocity : | input data | m/s | input data | m/s
61 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
62 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
63 |  | Minimum operating liquid specific gravity : | input data |  | input data
64 |  | Minimum operating liquid specific gravity at standard conditions : | input data |  | input data
65 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
66 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
67 |  | Minimum operating vapour compressibility factor : | input data |  | input data
68 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
69 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
70 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
71 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
72 |  | Normal operating velocity : | input data | m/s | input data | m/s
73 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
74 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
75 |  | Normal operating liquid specific gravity : | input data |  | input data
76 |  | Normal operating liquid specific gravity at standard conditions : | input data |  | input data
77 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
78 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
79 |  | Normal operating vapour compressibility factor : | input data |  | input data
80 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
81 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
82 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
83 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
84 |  | Maximum operating velocity : | input data | m/s | input data | m/s
85 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
86 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
87 |  | Maximum operating liquid specific gravity : | input data |  | input data
88 |  | Maximum operating liquid specific gravity at standard conditions : | input data |  | input data
89 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
90 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
91 |  | Maximum operating vapour compressibility factor : | input data |  | input data
92 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
93 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
94 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH₂O
95 |  | Body/element/sensor
96 |  | Body/element/sensor manufacturer model number : | input data |  | input data
97 | 7.2.2, 7.3.2.3 | Body material : | input data |  | input data
98 |  | Flange material : | input data |  | input data
99 |  | Ultrasonic technology type : | select |  | select | [5 empty] | select | doppler | time of flight
100 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in
101 |  | Body flange connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
102 |  | Body flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF
103 |  | Body flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
104 |  | Ultrasonic transducer material : | input data |  | input data
105 | 4.3.1.4.1, 4.3.1.4.2 | O-ring material : | input data |  | input data
106 |  | Transmitter
107 |  | Transmitter manufacturer model number. : | input data |  | input data
108 |  | Transmitter enclosure material : | input data |  | input data
109 |  | Transmitter location : | integrated |  | integrated | [5 empty] | select | integrated | remote
110 |  | Transmitter connecting cables : | no |  | no | [5 empty] | select | yes | no
111 |  | Transmitter connecting cable length : | input data | select | input data | select |  |  |  |  | select | m | ft
112 |  | Transmitter connecting cable quantity : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4
113 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
114 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | V AC | V DC
115 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | yes | no | not applicable
116 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
117 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
118 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
119 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
120 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
121 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
122 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
123 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
124 |  | Performance
125 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
126 |  | Uncertainty : | input data |  | input data
127 |  | Repeatability : | input data | % | input data | %
128 | 4.2.2 | Vibration : | input data |  | input data
129 |  | Accessories
130 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
131 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Select the instrument type (technology) to be purchased
Note on C5: Code compliance to be for the region where the instrument is to be installed.
Note on C6: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C7: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C8: A functional description of the tag.
Note on C9: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C10: Input the model number of the offered instrument assembly / unit.
Note on C11: Unique identification number for the equipment as prescribed by the supplier.
Note on C12: Name assigned by ISO to the country, in ISO 3166-1.
Note on C13: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C14: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C15: P&ID number where the orifice plate assembly is indicated
Note on C16: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C17: Fill in as per process data
Note on C18: Fill in as per process data
Note on C19: Declaration of the units to be used either select "normal" or "standard".
Note on C20: Temperature to be used for base units.
Note on C21: Pressure to be used to support the base units.
Note on C22: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C23: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C24: Bolting material for pressure retaining applications as detailed in IOGP S-563.
Note on C25: Populate the nut material in line with IOGP S-563.
Note on C26: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C27: Ingress protection rating in IP or NEMA.
Note on C28: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C29: Code to be followed for the hazardous area classification.
Note on C30: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C31: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C32: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C34: Selection of the pipe schedule in accordance with the pipe specification.
Note on C35: Process line size to be declared to support sizing and selection by the supplier.
Note on C36: Pressure rating of the system connected.
Note on C37: Instrument process connection to be compatible with that declared by the purchaser.
Note on C38: Orientation of the inlet to the instrument or insertion point.
Note on C39: Material for the instrument to connect to on the upstream face.
Note on C40: Selection of the pipe schedule in accordance with the pipe specification.
Note on C41: Process line size downstream to be declared to support sizing and selection by the supplier.
Note on C42: Pressure rating of the system connected.
Note on C43: Process connection to the system.
Note on C44: Orientation of the inlet or insertion point of the instrument.
Note on C45: Material for the instrument to connect to on the downstream face.
Note on C46: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C47: This figure should be the minimum design pressure of the system installed into.
Note on C48: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C49: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C50: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C52: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C53: Confirm whether it is a liquid or vapour phase.
Note on C54: Free field to input any corrosive elements in the process stream
Note on C55: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C56: Purchaser to declare if the instrument would see a vacuum.
Note on C57: Vapour pressure of the flowing fluid
Note on C58: Operating mass flow rate of the system to which it is installed at the minimum sizing case.
Note on C59: Operating volumetric flow rate of the system at mimimum sizing case
Note on C60: Operating velocity of the system at the minimum sizing case.
Note on C61: Temperature of the process at the minimum sizing case.
Note on C62: Differential pressure of the process at the minimum sizing case.
Note on C63: Specific gravity of the process fluid at the min sizing case
Note on C64: Liquid SG at standard conditions at the minimum sizing case.
Note on C65: Viscosity of the process fluid at minimum sizing conditions
Note on C66: Vapour molecular weight of the process fluid at minimum sizing conditions
Note on C67: Vapour compressibility factor at minimum sizing conditions
Note on C68: Vapour actual density at minimum sizing conditions
Note on C69: Vapour viscosity at minimum sizing conditions.
Note on C70: Normal operating flow rate of the system to which it is installed
Note on C71: Operating volumetric flow rate of the system at normalsizing case
Note on C72: Operating velocity of the system at the normal sizing case.
Note on C73: Temperature of the process at the minimum sizing case.
Note on C74: Pressure of the process for the normal operating case.
Note on C75: Specific gravity of the process fluid at the normal sizing case
Note on C76: Liquid SG at standard conditions at the normal sizing case.
Note on C77: Viscosity of the process fluid at the normal sizing case.
Note on C78: Vapour molecular weight of the process fluid at normal sizing conditions.
Note on C79: Vapour compressibility factor at normal sizing conditions.
Note on C80: Vapour actual density at normal sizing conditions.
Note on C81: Vapour viscosity at normal sizing conditions.
Note on C82: Operating mass flow rate of the system to which it is installed at maximum sizing case.
Note on C83: Operating volumetric flow rate of the system at maximum sizing case.
Note on C84: Operating velocity of the system at the maximum sizing case.
Note on C85: Temperature of the process at the minimum sizing case.
Note on C86: Pressure of the process for the maximum operating case.
Note on C87: Specific gravity of the process fluid at the maximum sizing case.
Note on C88: Liquid SG at standard conditions at the maximum sizing case.
Note on C89: Viscosity of the process fluid at maximum sizing conditions.
Note on C90: Vapour molecular weight of the process fluid at maximum sizing conditions.
Note on C91: Vapour compressibility factor at maximum sizing conditions.
Note on C92: Vapour actual density at minimum sizing conditions.
Note on C93: Vapour viscosity at maximum sizing conditions.
Note on C94: Input the value as per process data sheet.
Note on C96: Supplier to specify model number of body/element/sensor.
Note on C97: The material of main instrument body is a wetted part and should be suitable for the process fluids.
Note on C98: Input the flange material to be compatible with process conditions, fluid and process connection.
Note on C99: Select the technology used for the ultrasonic measurement.
Note on C100: Input the selected instrument body size.
Note on C101: Size of the connection to the process line or equipment.
Note on C102: Flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C103: Flange rating to match the rating of the system to which it is connected.
Note on C104: Transducer holder material and supporting components.
Note on C105: O-ring material (pressure containing) to meet the specified process requirements and if elastomeric decompression type then relevant type e.g. transducer o-ring on ultrasonic, seal between pressure capsule and diaphragm.
Note on C107: Model number for transmitter only.
Note on C108: Material offered to meet the minimum requirements.
Note on C109: Confirm whether a single integrated assembly or a transmitter to be remotely mounted. Default value : integrated
Note on C110: are external cables required for connection between sensor and transmitter housing or are they integral Default value : no
Note on C111: Provide the length of cable to support routing from the flow meter body to the transmitter housing.
Note on C112: Supplier to advise the number of cables needed between the body and transmitter head.
Note on C113: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C114: External power supply to the flow transmitter to be stated, if loop powered the input "N/A".
Note on C115: Select "yes" if isolated from power supply; "no" if not isolated from power supply, "not applicable" if unit is loop powered hence not applicable. Default value : not applicable
Note on C116: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C117: Communication protocol for the transmitter. Default value : HART
Note on C118: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C119: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C120: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C121: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C122: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C123: Highest value of the measured variable that a device can be adjusted to measure.
Note on C125: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C126: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C127: Repeatabiily of the instrument selected in accordance with the guidelines set out in IEC 62828 series
Note on C128: Vibration to be selected in accordance with the requirements of IEC 62828-1 table 4, typical value is "10 to 1000 Hz with 0,15mm peak amplitude and 20m/s²".
Note on C130: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C131: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Flow Element, Venturi
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Flow Element, Venturi | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
21 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
22 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
23 | 4.3.1.1.2, 4.3.1.2.1 | Bolt pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
24 | 4.3.1.2.1 | Nut pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
25 |  | Equipment / line conditions
26 |  | Upstream / high-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
27 | 7.2.1 | Upstream / high-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
28 |  | Upstream / high-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
29 |  | Upstream / high-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
30 |  | Upstream / high-side connection orientation : | input data |  | input data
31 |  | Upstream / high-side material type : | input data |  | input data
32 |  | Downstream / low-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
33 |  | Downstream / low-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
34 |  | Downstream / low-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
35 |  | Downstream / low-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
36 |  | Downstream / low-side connection orientation : | input data |  | input data
37 |  | Downstream / low-side material type : | input data |  | input data
38 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
39 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
40 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
41 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
42 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
43 |  | Operating conditions
44 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
45 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
46 |  | Process fluid corrosive compounds : | input data |  | input data
47 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
48 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
49 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kpaa
50 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
51 | 7.3.3 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
52 |  | Minimum operating velocity : | input data | m/s | input data | m/s
53 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
54 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
55 |  | Minimum operating liquid specific gravity : | input data |  | input data
56 |  | Minimum operating liquid specific gravity at standard conditions : | input data |  | input data
57 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
58 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
59 |  | Minimum operating vapour compressibility factor : | input data |  | input data
60 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
61 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
62 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
63 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
64 |  | Normal operating velocity : | input data | m/s | input data | m/s
65 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
66 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
67 |  | Normal operating liquid specific gravity : | input data |  | input data
68 |  | Normal operating liquid specific gravity at standard conditions : | input data |  | input data
69 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
70 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
71 |  | Normal operating vapour compressibility factor : | input data |  | input data
72 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
73 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
74 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
75 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
76 |  | Maximum operating velocity : | input data | m/s | input data | m/s
77 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
78 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
79 |  | Maximum operating liquid specific gravity : | input data |  | input data
80 |  | Maximum operating liquid specific gravity at standard conditions : | input data |  | input data
81 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
82 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
83 |  | Maximum operating vapour compressibility factor : | input data |  | input data
84 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
85 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
86 |  | Maximum recoverable pressure drop : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH₂O
87 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH₂O
88 |  | Body/element/sensor
89 |  | Body/element/sensor manufacturer model number : | input data |  | input data
90 | 7.2.2, 7.3.2.3 | Body material : | input data |  | input data
91 |  | Flange material : | input data |  | input data
92 |  | Venturi throat diameter : | input data | select | input data | select |  |  |  |  | select | mm | inch
93 |  | Beta ratio (d/D) : | input data |  | input data
94 |  | Differential pressure minimum range : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
95 |  | Differential pressure maximum range : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
96 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in
97 |  | Body flange connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
98 |  | Body flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF
99 |  | Body flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
100 |  | Venturi pressure tap number : | 2 |  | 2 | [5 empty] | select | 2 | 3 | 4
101 |  | Venturi pressure tap size : | 1 |  | 1 | [5 empty] | select | ½ in | 1 in
102 |  | Venturi pressure tap connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF | npt
103 |  | Venturi pressure tap rating : | 150 |  | 150 | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
104 |  | Venturi pressure tap orientation : | input data | deg | input data | deg
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Declaration of the units to be used either select "normal" or "standard".
Note on C19: Temperature to be used for base units.
Note on C20: Pressure to be used to support the base units.
Note on C21: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C22: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C23: Bolting material for pressure retaining applications as detailed in IOGP S-563.
Note on C24: Populate the nut material in line with IOGP S-563.
Note on C26: Selection of the pipe schedule in accordance with the pipe specification.
Note on C27: Process line size to be declared to support sizing and selection by the supplier.
Note on C28: Pressure rating of the system connected.
Note on C29: Instrument process connection to be compatible with that declared by the purchaser.
Note on C30: Orientation of the inlet to the instrument or insertion point.
Note on C31: Material for the instrument to connect to on the upstream face.
Note on C32: Selection of the pipe schedule in accordance with the pipe specification.
Note on C33: Process line size downstream to be declared to support sizing and selection by the supplier.
Note on C34: Pressure rating of the system connected.
Note on C35: Process connection to the system.
Note on C36: Orientation of the inlet or insertion point of the instrument.
Note on C37: Material for the instrument to connect to on the downstream face.
Note on C38: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C39: This figure should be the minimum design pressure of the system installed into.
Note on C40: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C41: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C42: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C44: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C45: Confirm whether it is a liquid or vapour phase.
Note on C46: Free field to input any corrosive elements in the process stream
Note on C47: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C48: Purchaser to declare if the instrument would see a vacuum.
Note on C49: Vapour pressure of the flowing fluid
Note on C50: Operating mass flow rate of the system to which it is installed at the minimum sizing case.
Note on C51: Operating volumetric flow rate of the system at mimimum sizing case
Note on C52: Operating velocity of the system at the minimum sizing case.
Note on C53: Temperature of the process at the minimum sizing case.
Note on C54: Differential pressure of the process at the minimum sizing case.
Note on C55: Specific gravity of the process fluid at the min sizing case
Note on C56: Liquid SG at standard conditions at the minimum sizing case.
Note on C57: Viscosity of the process fluid at minimum sizing conditions
Note on C58: Vapour molecular weight of the process fluid at minimum sizing conditions
Note on C59: Vapour compressibility factor at minimum sizing conditions
Note on C60: Vapour actual density at minimum sizing conditions
Note on C61: Vapour viscosity at minimum sizing conditions.
Note on C62: Normal operating flow rate of the system to which it is installed
Note on C63: Operating volumetric flow rate of the system at normalsizing case
Note on C64: Operating velocity of the system at the normal sizing case.
Note on C65: Temperature of the process at the minimum sizing case.
Note on C66: Pressure of the process for the normal operating case.
Note on C67: Specific gravity of the process fluid at the normal sizing case
Note on C68: Liquid SG at standard conditions at the normal sizing case.
Note on C69: Viscosity of the process fluid at the normal sizing case.
Note on C70: Vapour molecular weight of the process fluid at normal sizing conditions.
Note on C71: Vapour compressibility factor at normal sizing conditions.
Note on C72: Vapour actual density at normal sizing conditions.
Note on C73: Vapour viscosity at normal sizing conditions.
Note on C74: Operating mass flow rate of the system to which it is installed at maximum sizing case.
Note on C75: Operating volumetric flow rate of the system at maximum sizing case.
Note on C76: Operating velocity of the system at the maximum sizing case.
Note on C77: Temperature of the process at the minimum sizing case.
Note on C78: Pressure of the process for the maximum operating case.
Note on C79: Specific gravity of the process fluid at the maximum sizing case.
Note on C80: Liquid SG at standard conditions at the maximum sizing case.
Note on C81: Viscosity of the process fluid at maximum sizing conditions.
Note on C82: Vapour molecular weight of the process fluid at maximum sizing conditions.
Note on C83: Vapour compressibility factor at maximum sizing conditions.
Note on C84: Vapour actual density at minimum sizing conditions.
Note on C85: Vapour viscosity at maximum sizing conditions.
Note on C86: Purchaser to declare the maximum pressure drop that can be catered for across the meter at any point in the flow range.
Note on C87: Input the value as per process data sheet.
Note on C89: Supplier to specify model number of body/element/sensor.
Note on C90: The material of main instrument body is a wetted part and should be suitable for the process fluids.
Note on C91: Input the flange material to be compatible with process conditions, fluid and process connection.
Note on C92: Input the throat diameter after venturi sizing calculations.
Note on C93: Input the ratio of d/D after orifice sizing calculations.
Note on C94: Differential pressure range associated with the minimum flow rates of the fluid being measured.
Note on C95: Differential pressure range associated with the maximum flow rates of the fluid being measured.
Note on C96: Input the selected instrument body size.
Note on C97: Size of the connection to the process line or equipment.
Note on C98: Flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C99: Flange rating to match the rating of the system to which it is connected.
Note on C100: Default value : 2
Note on C101: Connection size for the differential pressure sensing lines. Default value : 1
Note on C102: Select the connection type. Default value : RF
Note on C103: Select the pressure rating of the process connection. Default value : 150
Note on C104: Purchaser to ipnut the orientation from the vertical plane i.e. if installed vertically then will be zero degree.

## Flow Transmitter, Vortex
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Flow Transmitter, Vortex | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
21 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
22 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
23 | 4.3.1.1.2, 4.3.1.2.1 | Bolt pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
24 | 4.3.1.2.1 | Nut pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
25 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
26 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
27 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
28 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
29 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
30 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
31 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
32 |  | Equipment / line conditions
33 |  | Upstream / high-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
34 | 7.2.1 | Upstream / high-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
35 |  | Upstream / high-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
36 |  | Upstream / high-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
37 |  | Upstream / high-side connection orientation : | input data |  | input data
38 |  | Upstream / high-side material type : | input data |  | input data
39 |  | Downstream / low-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
40 |  | Downstream / low-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
41 |  | Downstream / low-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
42 |  | Downstream / low-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
43 |  | Downstream / low-side connection orientation : | input data |  | input data
44 |  | Downstream / low-side material type : | input data |  | input data
45 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
46 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
47 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
48 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
49 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
50 |  | Operating conditions
51 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
52 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
53 |  | Process fluid corrosive compounds : | input data |  | input data
54 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
55 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
56 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kpaa
57 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
58 | 7.3.3 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
59 |  | Minimum operating velocity : | input data | m/s | input data | m/s
60 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
61 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
62 |  | Minimum operating liquid specific gravity : | input data |  | input data
63 |  | Minimum operating liquid specific gravity at standard conditions : | input data |  | input data
64 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
65 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
66 |  | Minimum operating vapour compressibility factor : | input data |  | input data
67 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
68 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
69 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
70 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
71 |  | Normal operating velocity : | input data | m/s | input data | m/s
72 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
73 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
74 |  | Normal operating liquid specific gravity : | input data |  | input data
75 |  | Normal operating liquid specific gravity at standard conditions : | input data |  | input data
76 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
77 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
78 |  | Normal operating vapour compressibility factor : | input data |  | input data
79 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
80 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
81 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
82 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
83 |  | Maximum operating velocity : | input data | m/s | input data | m/s
84 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
85 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
86 |  | Maximum operating liquid specific gravity : | input data |  | input data
87 |  | Maximum operating liquid specific gravity at standard conditions : | input data |  | input data
88 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
89 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
90 |  | Maximum operating vapour compressibility factor : | input data |  | input data
91 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
92 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
93 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH₂O
94 |  | Body/element/sensor
95 |  | Body/element/sensor manufacturer model number : | input data |  | input data
96 | 7.2.2, 7.3.2.3 | Body material : | input data |  | input data
97 |  | Flange material : | input data |  | input data
98 |  | Sensor material : | input data |  | input data
99 |  | Sensor type : | select |  | select | [5 empty] | select | capacitive sensor | piezoelectric sensor | strain gauge sensor | ultrasonic sensor
100 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in
101 |  | Body flange connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
102 |  | Body flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF
103 |  | Body flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
104 |  | Online extraction of vortex sensor : | yes |  | yes | [5 empty] | select | yes | no
105 | 4.3.1.4.1, 4.3.1.4.2 | O-ring material : | input data |  | input data
106 |  | Mean k-factor : | input data |  | input data
107 |  | Redundant sensors : | no |  | no | [5 empty] | select | yes | no
108 |  | Transmitter
109 |  | Transmitter manufacturer model number. : | input data |  | input data
110 |  | Transmitter enclosure material : | input data |  | input data
111 |  | Transmitter location : | integrated |  | integrated | [5 empty] | select | integrated | remote
112 |  | Transmitter connecting cables : | no |  | no | [5 empty] | select | yes | no
113 |  | Transmitter connecting cable length : | input data | select | input data | select |  |  |  |  | select | m | ft
114 |  | Transmitter connecting cable quantity : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4
115 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
116 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | V AC | V DC
117 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | yes | no | not applicable
118 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
119 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
120 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
121 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
122 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
123 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
124 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
125 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
126 |  | Performance
127 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
128 |  | Uncertainty : | input data |  | input data
129 |  | Repeatability : | input data | % | input data | %
130 | 4.2.2 | Vibration : | input data |  | input data
131 |  | Accessories
132 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
133 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Declaration of the units to be used either select "normal" or "standard".
Note on C19: Temperature to be used for base units.
Note on C20: Pressure to be used to support the base units.
Note on C21: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C22: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C23: Bolting material for pressure retaining applications as detailed in IOGP S-563.
Note on C24: Populate the nut material in line with IOGP S-563.
Note on C25: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C26: Ingress protection rating in IP or NEMA.
Note on C27: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C28: Code to be followed for the hazardous area classification.
Note on C29: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C30: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C31: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C33: Selection of the pipe schedule in accordance with the pipe specification.
Note on C34: Process line size to be declared to support sizing and selection by the supplier.
Note on C35: Pressure rating of the system connected.
Note on C36: Instrument process connection to be compatible with that declared by the purchaser.
Note on C37: Orientation of the inlet to the instrument or insertion point.
Note on C38: Material for the instrument to connect to on the upstream face.
Note on C39: Selection of the pipe schedule in accordance with the pipe specification.
Note on C40: Process line size downstream to be declared to support sizing and selection by the supplier.
Note on C41: Pressure rating of the system connected.
Note on C42: Process connection to the system.
Note on C43: Orientation of the inlet or insertion point of the instrument.
Note on C44: Material for the instrument to connect to on the downstream face.
Note on C45: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C46: This figure should be the minimum design pressure of the system installed into.
Note on C47: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C48: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C49: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C51: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C52: Confirm whether it is a liquid or vapour phase.
Note on C53: Free field to input any corrosive elements in the process stream
Note on C54: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C55: Purchaser to declare if the instrument would see a vacuum.
Note on C56: Vapour pressure of the flowing fluid
Note on C57: Operating mass flow rate of the system to which it is installed at the minimum sizing case.
Note on C58: Operating volumetric flow rate of the system at mimimum sizing case
Note on C59: Operating velocity of the system at the minimum sizing case.
Note on C60: Temperature of the process at the minimum sizing case.
Note on C61: Differential pressure of the process at the minimum sizing case.
Note on C62: Specific gravity of the process fluid at the min sizing case
Note on C63: Liquid SG at standard conditions at the minimum sizing case.
Note on C64: Viscosity of the process fluid at minimum sizing conditions
Note on C65: Vapour molecular weight of the process fluid at minimum sizing conditions
Note on C66: Vapour compressibility factor at minimum sizing conditions
Note on C67: Vapour actual density at minimum sizing conditions
Note on C68: Vapour viscosity at minimum sizing conditions.
Note on C69: Normal operating flow rate of the system to which it is installed
Note on C70: Operating volumetric flow rate of the system at normalsizing case
Note on C71: Operating velocity of the system at the normal sizing case.
Note on C72: Temperature of the process at the minimum sizing case.
Note on C73: Pressure of the process for the normal operating case.
Note on C74: Specific gravity of the process fluid at the normal sizing case
Note on C75: Liquid SG at standard conditions at the normal sizing case.
Note on C76: Viscosity of the process fluid at the normal sizing case.
Note on C77: Vapour molecular weight of the process fluid at normal sizing conditions.
Note on C78: Vapour compressibility factor at normal sizing conditions.
Note on C79: Vapour actual density at normal sizing conditions.
Note on C80: Vapour viscosity at normal sizing conditions.
Note on C81: Operating mass flow rate of the system to which it is installed at maximum sizing case.
Note on C82: Operating volumetric flow rate of the system at maximum sizing case.
Note on C83: Operating velocity of the system at the maximum sizing case.
Note on C84: Temperature of the process at the minimum sizing case.
Note on C85: Pressure of the process for the maximum operating case.
Note on C86: Specific gravity of the process fluid at the maximum sizing case.
Note on C87: Liquid SG at standard conditions at the maximum sizing case.
Note on C88: Viscosity of the process fluid at maximum sizing conditions.
Note on C89: Vapour molecular weight of the process fluid at maximum sizing conditions.
Note on C90: Vapour compressibility factor at maximum sizing conditions.
Note on C91: Vapour actual density at minimum sizing conditions.
Note on C92: Vapour viscosity at maximum sizing conditions.
Note on C93: Input the value as per process data sheet.
Note on C95: Supplier to specify model number of body/element/sensor.
Note on C96: The material of main instrument body is a wetted part and should be suitable for the process fluids.
Note on C97: Input the flange material to be compatible with process conditions, fluid and process connection.
Note on C98: Input the material to be selected for the sensor.
Note on C99: Select the sensor technology.
Note on C100: Input the selected instrument body size.
Note on C101: Size of the connection to the process line or equipment.
Note on C102: Flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C103: Flange rating to match the rating of the system to which it is connected.
Note on C104: Select whether the vortex meter is to allow online extraction of the transducer to maintain availability of the process while the instrument is maintained Default value : yes
Note on C105: O-ring material (pressure containing) to meet the specified process requirements and if elastomeric decompression type then relevant type e.g. transducer o-ring on ultrasonic, seal between pressure capsule and diaphragm.
Note on C106: Supplier to input figure as detailed ISO 12764.
Note on C107: Purchaser to advise whether redundant sensors and electronics are required Default value : no
Note on C109: Model number for transmitter only.
Note on C110: Material offered to meet the minimum requirements.
Note on C111: Confirm whether a single integrated assembly or a transmitter to be remotely mounted. Default value : integrated
Note on C112: are external cables required for connection between sensor and transmitter housing or are they integral Default value : no
Note on C113: Provide the length of cable to support routing from the flow meter body to the transmitter housing.
Note on C114: Supplier to advise the number of cables needed between the body and transmitter head.
Note on C115: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C116: External power supply to the flow transmitter to be stated, if loop powered the input "N/A".
Note on C117: Select "yes" if isolated from power supply; "no" if not isolated from power supply, "not applicable" if unit is loop powered hence not applicable. Default value : not applicable
Note on C118: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C119: Communication protocol for the transmitter. Default value : HART
Note on C120: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C121: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C122: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C123: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C124: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C125: Highest value of the measured variable that a device can be adjusted to measure.
Note on C127: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C128: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C129: Repeatabiily of the instrument selected in accordance with the guidelines set out in IEC 62828 series
Note on C130: Vibration to be selected in accordance with the requirements of IEC 62828-1 table 4, typical value is "10 to 1000 Hz with 0,15mm peak amplitude and 20m/s²".
Note on C132: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C133: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Level Transmitter, Magnetic
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Level Transmitter, Magnetic | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
21 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
22 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
23 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
24 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
25 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
26 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
27 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
28 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
29 |  | Equipment / line conditions
30 |  | Upstream / high-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
31 | 7.2.1 | Upstream / high-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
32 |  | Upstream / high-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
33 |  | Upstream / high-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
34 |  | Upstream / high-side connection orientation : | input data |  | input data
35 |  | Upstream / high-side material type : | input data |  | input data
36 |  | Downstream / low-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
37 |  | Downstream / low-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
38 |  | Downstream / low-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
39 |  | Downstream / low-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
40 |  | Downstream / low-side connection orientation : | input data |  | input data
41 |  | Downstream / low-side material type : | input data |  | input data
42 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
43 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
44 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
45 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
46 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
47 |  | Operating conditions
48 |  | Minimum operating upper material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
49 |  | Minimum operating upper material specific gravity : | input data |  | input data
50 |  | Minimum operating upper material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
51 |  | Minimum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
52 |  | Minimum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
53 |  | Minimum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
54 |  | Minimum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
55 |  | Minimum operating lower material phase type. : | select |  | select | [5 empty] | select | gas | liquid | vapour
56 |  | Minimum operating lower fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
57 |  | Minimum operating lower material specific gravity : | input data |  | input data
58 |  | Minimum operating lower material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
59 |  | Normal operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
60 |  | Normal operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
61 |  | Normal operating upper material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
62 |  | Normal operating upper material specific gravity : | input data |  | input data
63 |  | Normal operating upper material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
64 |  | Normal operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
65 |  | Normal operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
66 |  | Normal operating lower material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
67 |  | Normal operating lower material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
68 |  | Normal operating lower fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
69 |  | Normal operating lower material specific gravity : | input data |  | input data
70 |  | Maximum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
71 |  | Maximum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
72 |  | Maximum operating upper material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
73 |  | Maximum operating upper material specific gravity : | input data |  | input data
74 |  | Maximum operating upper material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
75 |  | Maximum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
76 |  | Maximum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
77 |  | Maximum operating lower material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
78 |  | Maximum operating lower fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
79 |  | Maximum operating lower material specific gravity : | input data |  | input data
80 |  | Maximum operating lower material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
81 |  | Interface / dual level
82 | 4.3.1.1.2 | Process fluid upper level / low pressure : | input data |  | input data
83 | 4.3.1.1.2 | Process fluid lower level / high pressure : | input data |  | input data
84 |  | Upper fluid minimum specific gravity : | input data |  | input data
85 |  | Upper fluid maximum specific gravity : | input data |  | input data
86 |  | Lower fluid minimum specific gravity : | input data |  | input data
87 |  | Lower fluid maximum specific gravity : | input data |  | input data
88 |  | Body/element/sensor
89 |  | Body/element/sensor manufacturer model number : | input data |  | input data
90 | 7.2.2, 7.3.2.3 | Body material : | input data |  | input data
91 |  | Flange material : | input data |  | input data
92 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in
93 |  | Body flange connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
94 |  | Body flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF
95 |  | Body flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
96 |  | Level gauge connection orientation : | select |  | select | [5 empty] | select | side-side | side-top | side-bottom | bottom-top
97 |  | Level gauge connection separation : | input data | select | input data | select |  |  |  |  | select | mm | in
98 |  | Level gauge high measurement : | input data | select | input data | select |  |  |  |  | select | % | mm
99 |  | Level gauge low measurement : | input data | select | input data | select |  |  |  |  | select | % | mm
100 |  | Float stop design : | input data |  | input data
101 |  | Float stop material : | input data |  | input data
102 |  | Chamber vent : | input data |  | input data
103 |  | Chamber drain : | input data |  | input data
104 |  | Level gauge float model number/type : | input data |  | input data
105 |  | Level gauge scale divisions : | input data | select | input data | select |  |  |  |  | select | in | mm
106 |  | Level gauge indicator casing material : | input data |  | input data
107 |  | Level gauge indicator visible length : | mm | mm | mm | mm
108 |  | Level gauge indicator wafer bi-colours : | input data |  | input data
109 |  | Transmitter
110 |  | Transmitter manufacturer model number. : | input data |  | input data
111 |  | Transmitter enclosure material : | input data |  | input data
112 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | yes | no | not applicable
113 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
114 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
115 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
116 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
117 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
118 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
119 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
120 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
121 |  | Performance
122 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
123 | 4.2.2 | Uncertainty : | input data |  | input data
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Declaration of the units to be used either select "normal" or "standard".
Note on C19: Temperature to be used for base units.
Note on C20: Pressure to be used to support the base units.
Note on C21: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C22: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C23: Ingress protection rating in IP or NEMA.
Note on C24: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C25: Code to be followed for the hazardous area classification.
Note on C26: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C27: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C28: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C30: Selection of the pipe schedule in accordance with the pipe specification.
Note on C31: Process line size to be declared to support sizing and selection by the supplier.
Note on C32: Pressure rating of the system connected.
Note on C33: Instrument process connection to be compatible with that declared by the purchaser.
Note on C34: Orientation of the inlet to the instrument or insertion point.
Note on C35: Material for the instrument to connect to on the upstream face.
Note on C36: Selection of the pipe schedule in accordance with the pipe specification.
Note on C37: Process line size downstream to be declared to support sizing and selection by the supplier.
Note on C38: Pressure rating of the system connected.
Note on C39: Process connection to the system.
Note on C40: Orientation of the inlet or insertion point of the instrument.
Note on C41: Material for the instrument to connect to on the downstream face.
Note on C42: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C43: This figure should be the minimum design pressure of the system installed into.
Note on C44: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C45: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C46: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C48: Confirmation of the phase at the upper location
Note on C49: Specific gravity of the process fluid in the upper section.
Note on C50: Viscosity of the process fluid in the upper section.
Note on C51: Confirm the pressure at the upper location.
Note on C52: Confirm the upper location temperature.
Note on C53: Confirm the pressure at the lower location.
Note on C54: Confirm the lower location temperature.
Note on C55: Confirm the phase at the upper location.
Note on C56: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C57: Specific gravity of the process fluid in the upper section.
Note on C58: Viscosity of the process fluid in the upper section.
Note on C59: Confirm the pressure at the upper location.
Note on C60: Confirm the upper location temperature.
Note on C61: Confirm the phase at the upper location.
Note on C62: Specific gravity of the process fluid in the upper section.
Note on C63: Viscosity of the process fluid in the upper section.
Note on C64: Confirm the pressure at the upper location.
Note on C65: Confirm the lower location temperature.
Note on C66: Confirm the phase at the lower location.
Note on C67: Viscosity of the process fluid in the upper section.
Note on C68: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C69: Specific gravity of the process fluid in the upper section.
Note on C70: Confirm the pressure at the upper location.
Note on C71: Confirm the upper location temperature.
Note on C72: Confirm the phase at the upper location.
Note on C73: Specific gravity of the process fluid in the upper section.
Note on C74: Viscosity of the process fluid in the upper section.
Note on C75: Confirm the phase at the lower location.
Note on C76: Confirm the lower location temperature.
Note on C77: Confirm the phase at the lower location.
Note on C78: Upper fluid density at temperature & pressure at maximum sizing conditions.
Note on C79: Specific gravity of the process fluid in the upper section.
Note on C80: Viscosity of the process fluid in the upper section.
Note on C82: Process fluid to be declared that resides in the upper process connection
Note on C83: Process fluid to be declared that resides in the lower process connection
Note on C84: Minimum specific gravity for the upper fluid.
Note on C85: Maximum specific gravity for the upper fluid.
Note on C86: Minimum specific gravity for the lower fluid.
Note on C87: Maximum specific gravity for the lower fluid.
Note on C89: Supplier to specify model number of body/element/sensor.
Note on C90: The material of main instrument body is a wetted part and should be suitable for the process fluids.
Note on C91: Input the flange material to be compatible with process conditions, fluid and process connection.
Note on C92: Input the selected instrument body size.
Note on C93: Size of the connection to the process line or equipment.
Note on C94: Flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C95: Flange rating to match the rating of the system to which it is connected.
Note on C96: Purchaser to select location of flanges for the connection of chamber to process
Note on C97: Separattion distance between process connections, either centreline to centreline or centre line to flange face depending on the orientation of the flanges.
Note on C98: Purchaser to input the required high level measurement within the separation range.
Note on C99: Purchaser to input the required low level measurement within the separation range.
Note on C100: Supplier to advise whether float stops are provided and the method e.g. dampening springs
Note on C101: Material for the float stop.
Note on C102: Details of end to be declared whether it is sealed or not and if not then provide details e.g. 3/4 inch 150# RF, 3/4 inch nptf.
Note on C103: Details of end to be declared whether it is sealed or not and if not then provide details e.g. 3/4 inch 150# RF, 3/4 inch nptf.
Note on C104: Provide catalogue part number for float.
Note on C105: Input the units of measure to be used to mark on the gauge.
Note on C106: Input the material of the gauge indicator.
Note on C107: Input the visible length of the indicator. This will confirm what is able to be measured. Default value : mm
Note on C108: Colour requirement for the wafers on the indicator
Note on C110: Model number for transmitter only.
Note on C111: Material offered to meet the minimum requirements.
Note on C112: Select "yes" if isolated from power supply; "no" if not isolated from power supply, "not applicable" if unit is loop powered hence not applicable. Default value : not applicable
Note on C113: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C114: Communication protocol for the transmitter. Default value : HART
Note on C115: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C116: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C117: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C118: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C119: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C120: Highest value of the measured variable that a device can be adjusted to measure.
Note on C122: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C123: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument

## Level Transmitter, Hydrostatic
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Level Transmitter, Hydrostatic | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
21 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
22 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
23 | 4.3.1.1.2, 4.3.1.2.1 | Bolt pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
24 | 4.3.1.2.1 | Nut pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
25 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
26 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
27 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
28 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
29 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
30 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
31 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
32 |  | Equipment / line conditions
33 | 7.2.1 | Upstream / high-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
34 |  | Upstream / high-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
35 |  | Upstream / high-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
36 |  | Upstream / high-side connection orientation : | input data |  | input data
37 |  | Upstream / high-side material type : | input data |  | input data
38 |  | Upstream / high-side pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
39 |  | Downstream / low-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
40 |  | Downstream / low-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
41 |  | Downstream / low-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
42 |  | Downstream / low-side connection orientation : | input data |  | input data
43 |  | Downstream / low-side material type : | input data |  | input data
44 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
45 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
46 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
47 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
48 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
49 |  | Operating conditions
50 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
51 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
52 |  | Process fluid corrosive compounds : | input data |  | input data
53 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
54 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
55 |  | Normal operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
56 |  | Maximum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa
57 |  | Minimum operating upper fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
58 |  | Minimum operating upper material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
59 |  | Minimum operating upper material specific gravity : | input data |  | input data
60 |  | Minimum operating upper material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
61 |  | Minimum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
62 |  | Minimum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
63 |  | Minimum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
64 |  | Minimum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
65 |  | Minimum operating lower material phase type. : | select |  | select | [5 empty] | select | gas | liquid | vapour
66 |  | Minimum operating lower fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
67 |  | Minimum operating lower material specific gravity : | input data |  | input data
68 |  | Minimum operating lower material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
69 |  | Normal operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
70 |  | Normal operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
71 |  | Normal operating upper material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
72 |  | Normal operating upper fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
73 |  | Normal operating upper material specific gravity : | input data |  | input data
74 |  | Normal operating upper material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
75 |  | Normal operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
76 |  | Normal operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
77 |  | Normal operating lower material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
78 |  | Normal operating lower material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
79 |  | Normal operating lower fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
80 |  | Normal operating lower material specific gravity : | input data |  | input data
81 |  | Maximum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
82 |  | Maximum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
83 |  | Maximum operating upper material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
84 |  | Maximum operating upper fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
85 |  | Maximum operating upper material specific gravity : | input data |  | input data
86 |  | Maximum operating upper material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
87 |  | Maximum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
88 |  | Maximum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
89 |  | Maximum operating lower material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
90 |  | Maximum operating lower fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
91 |  | Maximum operating lower material specific gravity : | input data |  | input data
92 |  | Maximum operating lower material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
93 |  | Interface / dual level
94 | 4.3.1.1.2 | Process fluid upper level / low pressure : | input data |  | input data
95 | 4.3.1.1.2 | Process fluid lower level / high pressure : | input data |  | input data
96 |  | Upper fluid minimum specific gravity : | input data |  | input data
97 |  | Upper fluid maximum specific gravity : | input data |  | input data
98 |  | Lower fluid minimum specific gravity : | input data |  | input data
99 |  | Lower fluid maximum specific gravity : | input data |  | input data
100 |  | Body/element/sensor
101 |  | Body/element/sensor manufacturer model number : | input data |  | input data
102 |  | Transmitter
103 |  | PT element fill fluid : | input data |  | input data
104 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.4, 4.3.1.1.6, 5.2.5 | PT element (sensor) material : | input data |  | input data
105 | 4.3.1.1.5 | PT element gold plating : | no |  | no | [5 empty] | select | yes | no
106 | 4.3.1.1.5 | PT element gold plating thickness : | input data | select | input data | select |  |  |  |  | select | micro-inches | nano-metres
107 | 4.3.1.1.1, 4.3.1.1.2, 4.3.1.1.3, 4.3.1.1.4, 4.3.1.1.6 | PT body wetted material : | input data |  | input data
108 |  | O-ring material : | input data |  | input data
109 |  | Transmitter enclosure material : | input data |  | input data
110 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | integral LCD display | remote indicator | not applicable
111 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
112 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
113 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
114 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
115 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
116 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
117 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
118 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
119 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
120 |  | Zero suppression or elevation : | input data | select | input data | select |  |  |  |  | select | mm | in
121 |  | Performance
122 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
123 |  | Uncertainty : | input data |  | input data
124 |  | Response time : | input data | ms | input data | ms
125 |  | Ambient temperature effect : | input data |  | input data
126 |  | Long term drift : | input data |  | input data
127 |  | Supply voltage effect : | input data |  | input data
128 |  | Supply voltage effect : | input data |  | input data
129 |  | Diaphragm seal
130 |  | Diaphragm seal type : | n/a |  | n/a | [5 empty] | select | 2 in extension | 4 in extension | 6 in extension | flush
131 | 5.2.7 | Diaphragm seal configuration : | not applicable |  | not applicable | [5 empty] | select | close coupled (single connection) | remote seal (single connection) | balanced system (both capillaries equal length) | unbalanced system (low side capillary - high side direct connected) | unbalanced system (high side seal - low side open to atmosphere) | not applicable
132 | 5.2.1, 5.2.2, 5.2.3 | Diaphragm seal capillary / armour material : | input data |  | input data
133 |  | Diaphragm seal capillary length : | input data | select | input data | select |  |  |  |  | select | mm | in
134 | 5.2.6, 5.2.7 | Diaphragm seal capillary fill fluid : | input data |  | input data
135 | 4.3.1.1.2 | Diaphragm seal upper housing material : | input data |  | input data
136 | 4.3.1.1.1, 4.3.1.1.2, 4.3.1.1.4, 4.3.1.1.6 | Diaphragm seal lower housing material : | input data |  | input data
137 | 4.3.1.1.4, 4.3.1.1.6, 5.2.5 | Diaphragm seal diaphragm material : | input data |  | input data
138 |  | Diaphragm seal gold plating : | no |  | no | [5 empty] | select | yes | no
139 |  | Diaphragm seal gold plating thickness : | input data | select | input data | select |  |  |  |  | select | micro-inches | nano-metres
140 |  | Diaphragm seal flushing connection : | select |  | select | [5 empty] | select | one 1/4-18NPT | two 1/4-18NPT | one 1/2 -14NPT | two 1/2-14NPT
141 |  | Diaphragm seal process connection size : | 50 |  | 50 | [5 empty] | select | 50 mm | 75 mm | 2 in | 3 in
142 |  | Diaphragm seal process connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF
143 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
144 |  | Manifold
145 |  | Manifold type : | 2 valve |  | 2 valve | [5 empty] | select | 2 valve | 5 valve | not applicable
146 |  | Manifold assembly orientation : | select |  | select | [5 empty] | select | coplanar | biplanar
147 | 4.3.1.1.2 | Manifold material : | input data |  | input data
148 |  | Manifold assembly process connection size : | select |  | select | [5 empty] | select | 12 mm | ½ in | 2 in
149 |  | Manifold assembly process connection type : | nptf |  | nptf | [5 empty] | select | nptf | RF | RTJ | FF
150 |  | Manifold assembly process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
151 |  | Manifold lockable : | no |  | no | [5 empty] | select | yes | no
152 |  | Accessories
153 |  | Weather enclosure : | select |  | select | [5 empty] | select | yes | no
154 |  | Mounting bracket : | select |  | select | [5 empty] | select | yes | no
155 |  | Mounting bracket material : | select |  | select | [5 empty] | select | 316 SS | other
156 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
157 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Declaration of the units to be used either select "normal" or "standard".
Note on C19: Temperature to be used for base units.
Note on C20: Pressure to be used to support the base units.
Note on C21: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C22: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C23: Bolting material for pressure retaining applications as detailed in IOGP S-563.
Note on C24: Populate the nut material in line with IOGP S-563.
Note on C25: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C26: Ingress protection rating in IP or NEMA.
Note on C27: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C28: Code to be followed for the hazardous area classification.
Note on C29: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C30: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C31: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C33: Process line size to be declared to support sizing and selection by the supplier.
Note on C34: Pressure rating of the system connected.
Note on C35: Instrument process connection to be compatible with that declared by the purchaser.
Note on C36: Orientation of the inlet to the instrument or insertion point.
Note on C37: Material for the instrument to connect to on the upstream face.
Note on C38: Selection of the pipe schedule in accordance with the pipe specification.
Note on C39: Process line size downstream to be declared to support sizing and selection by the supplier.
Note on C40: Pressure rating of the system connected.
Note on C41: Process connection to the system.
Note on C42: Orientation of the inlet or insertion point of the instrument.
Note on C43: Material for the instrument to connect to on the downstream face.
Note on C44: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C45: This figure should be the minimum design pressure of the system installed into.
Note on C46: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C47: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C48: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C50: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C51: Confirm whether it is a liquid or vapour phase.
Note on C52: Free field to input any corrosive elements in the process stream
Note on C53: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C54: Differential pressure of the process at the minimum sizing case.
Note on C55: Differential pressure of the process at the normal sizing case.
Note on C56: Differential pressure of the process at the minimum sizing case.
Note on C57: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C58: Confirmation of the phase at the upper location
Note on C59: Specific gravity of the process fluid in the upper section.
Note on C60: Viscosity of the process fluid in the upper section.
Note on C61: Confirm the pressure at the upper location.
Note on C62: Confirm the upper location temperature.
Note on C63: Confirm the pressure at the lower location.
Note on C64: Confirm the lower location temperature.
Note on C65: Confirm the phase at the upper location.
Note on C66: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C67: Specific gravity of the process fluid in the upper section.
Note on C68: Viscosity of the process fluid in the upper section.
Note on C69: Confirm the pressure at the upper location.
Note on C70: Confirm the upper location temperature.
Note on C71: Confirm the phase at the upper location.
Note on C72: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C73: Specific gravity of the process fluid in the upper section.
Note on C74: Viscosity of the process fluid in the upper section.
Note on C75: Confirm the pressure at the upper location.
Note on C76: Confirm the lower location temperature.
Note on C77: Confirm the phase at the lower location.
Note on C78: Viscosity of the process fluid in the upper section.
Note on C79: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C80: Specific gravity of the process fluid in the upper section.
Note on C81: Confirm the pressure at the upper location.
Note on C82: Confirm the upper location temperature.
Note on C83: Confirm the phase at the upper location.
Note on C84: Upper fluid density at temperature & pressure at maximum sizing conditions.
Note on C85: Specific gravity of the process fluid in the upper section.
Note on C86: Viscosity of the process fluid in the upper section.
Note on C87: Confirm the phase at the lower location.
Note on C88: Confirm the lower location temperature.
Note on C89: Confirm the phase at the lower location.
Note on C90: Upper fluid density at temperature & pressure at maximum sizing conditions.
Note on C91: Specific gravity of the process fluid in the upper section.
Note on C92: Viscosity of the process fluid in the upper section.
Note on C94: Process fluid to be declared that resides in the upper process connection
Note on C95: Process fluid to be declared that resides in the lower process connection
Note on C96: Minimum specific gravity for the upper fluid.
Note on C97: Maximum specific gravity for the upper fluid.
Note on C98: Minimum specific gravity for the lower fluid.
Note on C99: Maximum specific gravity for the lower fluid.
Note on C101: Supplier to specify model number of body/element/sensor.
Note on C103: Fill fluid within transmitter pressure capsule within the transmitter body
Note on C104: Material of diaphragm or bellow (wetted part).
Note on C105: Option to be activated if there is hydrogen present and risk of embrittlement. Default value : no
Note on C106: Supplier to declare the calculated thickness supported by calculations.
Note on C107: Material of socket inlet port (wetted part). Input "N/A" if diaphragm seal type is selected.
Note on C108: O-ring material (pressure containing) to meet the specified process requirements and if ED then relevant type e.g. transducer o-ring on ultrasonic, seal between pressure capsule and diaphragm
Note on C109: Material offered to meet the minimum requirements.
Note on C110: Select whether "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C111: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C112: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C113: Communication protocol for the transmitter. Default value : HART
Note on C114: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C115: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C116: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C117: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C118: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C119: Highest value of the measured variable that a device can be adjusted to measure.
Note on C120: If located above the zero point make the units positive, if located below the zero point make units negative e.g. -100mm. Suppler to ensure that this is translated to pressure units in the calculation.
Note on C122: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C123: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C124: Response time to be provided in accordance with IEC 6282 series. Time to reach 90% output and includes 'dead time'.
Note on C125: Ambient temperature effect to be provided in accordance to IEC 62828 series
Note on C126: Long term drift figure to be provided in accordance to IEC 62828 series.
Note on C127: Supply voltage effect figure to be provided in accordance to IEC 62828 series.
Note on C128: Supply voltage effect figure to be provided in accordance to IEC 62828 series.
Note on C130: State the length to which the seal is to protrude inside the nozzle or flush if no extension required. Default value : n/a
Note on C131: Type of diaphragm seal configuration to be selected for chosen application. Default value : not applicable
Note on C132: To be suitable for the ambient conditions and fill fluid; select "N/A" if direct mount.
Note on C133: For a balanced system the length is to be for both capillaries. For an unbalanced system refer to "instrumentation type" datasheet field to determine whether high or low pressure leg.
Note on C134: Silicon or glycerin are standard, subject to operating temperature of the process. Ensure complies with API RP 551, 9.3.1 selection guidance.
Note on C135: Minimum 316 Stainless Steel is common but dependent on fill fluid more exotic material selection can apply.
Note on C136: Minimum 316 Stainless Steel is common but dependent on fill fluid more exotic material selection can apply.
Note on C137: Wetted part material to be suitable for process fluids requirement, normally 316 Stainless Steel or Hastelloy C-276
Note on C138: Option to be activated if there is hydrogen present and risk of embrittlement. Default value : no
Note on C139: Supplier to declare the calculated thickness supported by calculations.
Note on C140: Flushing function is required, declaration size of threaded connection.
Note on C141: Select from 50mm (2 in) or 75mm (3 in) for flanged connection. Default value : 50
Note on C142: Flange finish to be selected. Default value : RF
Note on C143: Input the diaphragm flange rating in line with the installed rating and as per piping specification.
Note on C145: "2 valve" is normally specified for pressure transmitter applications, "5 valve" is specified for differential pressure. "N/A" is used if a diaphragm seal is selected. Default value : 2 valve
Note on C146: Select either coplanar for bottom entry or biplanar for side entry.
Note on C147: Normally 316L SS minimum to meet process requirements.
Note on C148: Detail connection size at the boundary point of suppliers interface to the process.
Note on C149: Select the connection of the manifold to the process. The standard is NPTF allowing for tubing and fitting connections. Default value : nptf
Note on C150: Provide the pressure rating of flanged connection.
Note on C151: Confirmation whether the manifold shall is have the capability to lock the valves in position. Default value : no
Note on C153: Purchaser to advise whether enclosure required and to add to "additional notes" column if enclosure to include other tags.
Note on C154: Select "Yes" if remote mount; select "No" if direct mount.
Note on C155: Minimum material 316 Stainless Steel but others can be selected if more suitable.
Note on C156: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C157: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Level Transmitter, Radar GW
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Level Transmitter, Radar Guided Wave | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
21 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
22 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
23 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
24 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
25 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
26 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
27 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
28 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
29 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
30 |  | Equipment / line conditions
31 |  | Process connection pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
32 | 7.2.1 | Process connection line size : | input data | select | input data | select |  |  |  |  | select | mm | in
33 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
34 |  | Process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
35 |  | Process connection orientation : | input data |  | input data
36 |  | Process connection material type : | input data |  | input data
37 |  | Process connection nozzle/standpipe diameter : | input data | select | input data | select |  |  |  |  | select | mm | in
38 |  | Process connection nozzle/standpipe length : | input data | select | input data | select |  |  |  |  | select | mm | in
39 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
40 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
41 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
42 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
43 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
44 |  | Operating conditions
45 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
46 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
49 |  | Process fluid dielectric constant : | input data |  | input data
50 |  | Process vapour operational density : | input data | select | input data | select |  |  |  |  | select | kg/m3 | lb/in3
51 |  | Process fluid foam presence : | select |  | select | [5 empty] | select | yes | no
52 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
53 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
54 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
55 |  | Minimum operating fluid conductivity : | input data | s/m | input data | s/m
56 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
57 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
58 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
59 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
60 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
61 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
62 |  | Minimum operating fluid conductivity : | input data | s/m | input data | s/m
63 |  | Interface / dual level
64 | 4.3.1.1.2 | Process fluid upper level / low pressure : | input data |  | input data
65 | 4.3.1.1.2 | Process fluid lower level / high pressure : | input data |  | input data
66 |  | Upper fluid minimum dielectric constant : | input data |  | input data
67 |  | Upper fluid maximum dielectric constant : | input data |  | input data
68 |  | Lower fluid minimum dielectric constant : | input data |  | input data
69 |  | Lower fluid maximum dielectric constant : | input data |  | input data
70 |  | Emulsion layer : | select |  | select | [5 empty] | select | yes | no
71 |  | Emulsion layer thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
72 |  | Upper fluid minimum thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
73 |  | Upper fluid maximum thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
74 |  | Body/element/sensor
75 |  | Body/element/sensor manufacturer model number : | input data |  | input data
76 |  | Radar gauge probe material : | input data |  | input data
77 |  | Flange material : | input data |  | input data
78 |  | Body flange connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
79 |  | Body flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF
80 |  | Body flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
81 |  | Probe installation type : | select |  | select | [5 empty] | select | internal | external chamber
82 | 8.3 | Probe length : | input data | select | input data | select |  |  |  |  | select | m | in
83 | 8.3 | Guided wave radar sensor type : | select |  | select | [5 empty] | select | rigid | flexible
84 | 4.3.1.4.1, 4.3.1.4.2 | O-ring material : | input data |  | input data
85 |  | Chamber required : | no |  | no | [5 empty] | select | yes | no
86 |  | Transmitter
87 |  | O-ring material : | input data |  | input data
88 |  | Transmitter enclosure material : | input data |  | input data
89 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
90 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | V AC | V DC
91 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | yes | no | not applicable
92 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
93 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
94 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
95 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
96 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
97 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
98 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
99 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
100 |  | Performance
101 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
102 |  | Uncertainty : | input data |  | input data
103 |  | Repeatability : | input data | % | input data | %
104 |  | Response time : | input data | ms | input data | ms
105 |  | Linearity : | input data | % | input data | %
106 |  | Hysteresis : | input data | % | input data | %
107 | 4.2.2 | Vibration : | input data |  | input data
108 |  | Accessories
109 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
110 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Declaration of the units to be used either select "normal" or "standard".
Note on C19: Temperature to be used for base units.
Note on C20: Pressure to be used to support the base units.
Note on C21: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C22: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C23: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C24: Ingress protection rating in IP or NEMA.
Note on C25: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C26: Code to be followed for the hazardous area classification.
Note on C27: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C28: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C29: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C31: Selection of the pipe schedule in accordance with the pipe specification.
Note on C32: Purchaser to declare the connection size to the process.
Note on C33: Pressure rating of the system connected.
Note on C34: Select the connection type to the process.
Note on C35: Orientation of the inlet or insertion point of the instrument (e.g. vertical upwards).
Note on C36: Purchaser to declare the material of the process flange.
Note on C37: Purchaser to declare the diameter of the standpipe/nozzle
Note on C38: Purchaser to declare the length of the nozzle/standpipe that the instrument is to be installed into.
Note on C39: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C40: This figure should be the minimum design pressure of the system installed into.
Note on C41: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C42: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C43: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C45: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C46: Confirm whether it is a liquid or vapour phase.
Note on C47: Free field to input any corrosive elements in the process stream
Note on C48: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C49: Purchaser to advise the dielectric constant value for the fluid level being measured. Supplier to declare the value that the instrument can measure down to.
Note on C50: Density of the vapour to be declared
Note on C51: Declare whether the foam can be formed.
Note on C52: Temperature of the process at the minimum sizing case.
Note on C53: Differential pressure of the process at the minimum sizing case.
Note on C54: Viscosity of the process fluid at minimum sizing conditions
Note on C55: Provide the process condition of the conductivity at the minimum case.
Note on C56: Temperature of the process at the minimum sizing case.
Note on C57: Pressure of the process for the normal operating case.
Note on C58: Viscosity of the process fluid at the normal sizing case.
Note on C59: Temperature of the process at the minimum sizing case.
Note on C60: Pressure of the process for the maximum operating case.
Note on C61: Viscosity of the process fluid at maximum sizing conditions.
Note on C62: Provide the process condition of the conductivity at the minimum case.
Note on C64: Process fluid to be declared that resides in the upper process connection
Note on C65: Process fluid to be declared that resides in the lower process connection
Note on C66: Purchaser to advise the dielectric constant value for the fluid level being measured. Supplier to declare the value that the instrument can measure down to.
Note on C67: Purchaser to advise the dielectric constant value for the fluid level being measured.
Note on C68: Purchaser to advise the dielectric constant value for the fluid level being measured.
Note on C69: Purchaser to advise the dielectric constant value for the fluid level being measured.
Note on C70: Confirm if an emulsion layer is possible to form.
Note on C71: Input the emulsion layer thickness.
Note on C72: Input minimum thickness of the upper fluid.
Note on C73: Input maximum thickness of the upper fluid.
Note on C75: Supplier to specify model number of body/element/sensor.
Note on C76: Material selection for probe
Note on C77: Input the flange material to be compatible with process conditions, fluid and process connection.
Note on C78: Size of the connection to the process line or equipment.
Note on C79: Flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C80: Flange rating to match the rating of the system to which it is connected.
Note on C81: Select where the probe will be installed to support design selection, e.g. rigid or flexible probe.
Note on C82: Design length of the probe, with measurement taken from flange face to end of probe.
Note on C83: Based upon length required sensor type to be selected.
Note on C84: O-ring material (pressure containing) to meet the specified process requirements and if elastomeric decompression type then relevant type e.g. transducer o-ring on ultrasonic, seal between pressure capsule and diaphragm.
Note on C85: Confirm whether the chamber is required to be supplied with a guided wave radar. If required a separate document is to support the design. Default value : no
Note on C87: O-ring material (pressure containing) to meet the specified process requirements and if ED then relevant type e.g. transducer o-ring on ultrasonic, seal between pressure capsule and diaphragm
Note on C88: Material offered to meet the minimum requirements.
Note on C89: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C90: External power supply to the flow transmitter to be stated, if loop powered the input "N/A".
Note on C91: Select "yes" if isolated from power supply; "no" if not isolated from power supply, "not applicable" if unit is loop powered hence not applicable. Default value : not applicable
Note on C92: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C93: Communication protocol for the transmitter. Default value : HART
Note on C94: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C95: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C96: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C97: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C98: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C99: Highest value of the measured variable that a device can be adjusted to measure.
Note on C101: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C102: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C103: Repeatabiily of the instrument selected in accordance with the guidelines set out in IEC 62828 series
Note on C104: Response time to be provided in accordance with IEC 6282 series. Time to reach 90% output and includes 'dead time'.
Note on C105: Linearity figure to be provided in accordance to IEC 62828 series
Note on C106: Hysteresis figure to be provided in accordance to IEC 62828 series
Note on C107: Vibration to be selected in accordance with the requirements of IEC 62828-1 table 4, typical value is "10 to 1000 Hz with 0,15mm peak amplitude and 20m/s²".
Note on C109: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C110: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Level Transmitter, Radar NC
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Level Transmitter, Radar Non-contact | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | barg | bara | psig | psia
21 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
22 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
23 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
24 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
25 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
26 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
27 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
28 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
29 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
30 |  | Equipment / line conditions
31 |  | Process connection pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
32 | 7.2.1 | Process connection line size : | input data | select | input data | select |  |  |  |  | select | mm | in
33 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
34 |  | Process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
35 |  | Process connection orientation : | input data |  | input data
36 |  | Process connection material type : | input data |  | input data
37 |  | Process connection nozzle/standpipe diameter : | input data | select | input data | select |  |  |  |  | select | mm | in
38 |  | Process connection nozzle/standpipe length : | input data | select | input data | select |  |  |  |  | select | mm | in
39 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
40 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
41 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
42 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
43 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
44 |  | Operating conditions
45 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
46 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
49 |  | Process fluid dielectric constant : | input data |  | input data
50 |  | Process vapour operational density : | input data | select | input data | select |  |  |  |  | select | kg/m3 | lb/in3
51 |  | Process fluid foam presence : | select |  | select | [5 empty] | select | yes | no
52 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
53 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
54 |  | Minimum operating fluid conductivity : | input data | s/m | input data | s/m
55 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
56 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
57 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
58 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
59 |  | Minimum operating fluid conductivity : | input data | s/m | input data | s/m
60 |  | Body/element/sensor
61 |  | Body/element/sensor manufacturer model number : | input data |  | input data
62 |  | Radar gauge probe material : | input data |  | input data
63 |  | Flange material : | input data |  | input data
64 |  | Body flange connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
65 |  | Body flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF
66 |  | Body flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
67 | 4.3.1.4.1, 4.3.1.4.2 | O-ring material : | input data |  | input data
68 |  | Transmitter
69 |  | O-ring material : | input data |  | input data
70 |  | Transmitter enclosure material : | input data |  | input data
71 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
72 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | V AC | V DC
73 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | yes | no | not applicable
74 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
75 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
76 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
77 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
78 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
79 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
80 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
81 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
82 |  | Performance
83 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
84 |  | Uncertainty : | input data |  | input data
85 | 4.2.2 | Vibration : | input data |  | input data
86 |  | Accessories
87 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
88 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Declaration of the units to be used either select "normal" or "standard".
Note on C19: Temperature to be used for base units.
Note on C20: Pressure to be used to support the base units.
Note on C21: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C22: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C23: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C24: Ingress protection rating in IP or NEMA.
Note on C25: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C26: Code to be followed for the hazardous area classification.
Note on C27: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C28: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C29: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C31: Selection of the pipe schedule in accordance with the pipe specification.
Note on C32: Purchaser to declare the connection size to the process.
Note on C33: Pressure rating of the system connected.
Note on C34: Select the connection type to the process.
Note on C35: Orientation of the inlet or insertion point of the instrument (e.g. vertical upwards).
Note on C36: Purchaser to declare the material of the process flange.
Note on C37: Purchaser to declare the diameter of the standpipe/nozzle
Note on C38: Purchaser to declare the length of the nozzle/standpipe that the instrument is to be installed into.
Note on C39: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C40: This figure should be the minimum design pressure of the system installed into.
Note on C41: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C42: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C43: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C45: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C46: Confirm whether it is a liquid or vapour phase.
Note on C47: Free field to input any corrosive elements in the process stream
Note on C48: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C49: Purchaser to advise the dielectric constant value for the fluid level being measured. Supplier to declare the value that the instrument can measure down to.
Note on C50: Density of the vapour to be declared
Note on C51: Declare whether the foam can be formed.
Note on C52: Temperature of the process at the minimum sizing case.
Note on C53: Differential pressure of the process at the minimum sizing case.
Note on C54: Provide the process condition of the conductivity at the minimum case.
Note on C55: Temperature of the process at the minimum sizing case.
Note on C56: Pressure of the process for the normal operating case.
Note on C57: Temperature of the process at the minimum sizing case.
Note on C58: Pressure of the process for the maximum operating case.
Note on C59: Provide the process condition of the conductivity at the minimum case.
Note on C61: Supplier to specify model number of body/element/sensor.
Note on C62: Material selection for probe
Note on C63: Input the flange material to be compatible with process conditions, fluid and process connection.
Note on C64: Size of the connection to the process line or equipment.
Note on C65: Flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C66: Flange rating to match the rating of the system to which it is connected.
Note on C67: O-ring material (pressure containing) to meet the specified process requirements and if elastomeric decompression type then relevant type e.g. transducer o-ring on ultrasonic, seal between pressure capsule and diaphragm.
Note on C69: O-ring material (pressure containing) to meet the specified process requirements and if ED then relevant type e.g. transducer o-ring on ultrasonic, seal between pressure capsule and diaphragm
Note on C70: Material offered to meet the minimum requirements.
Note on C71: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C72: External power supply to the flow transmitter to be stated, if loop powered the input "N/A".
Note on C73: Select "yes" if isolated from power supply; "no" if not isolated from power supply, "not applicable" if unit is loop powered hence not applicable. Default value : not applicable
Note on C74: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C75: Communication protocol for the transmitter. Default value : HART
Note on C76: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C77: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C78: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C79: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C80: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C81: Highest value of the measured variable that a device can be adjusted to measure.
Note on C83: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C84: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C85: Vibration to be selected in accordance with the requirements of IEC 62828-1 table 4, typical value is "10 to 1000 Hz with 0,15mm peak amplitude and 20m/s²".
Note on C87: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C88: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Pressure Transmitter, Diff
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Pressure Transmitter, Differential | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
19 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
20 | 4.3.1.1.2, 4.3.1.2.1 | Bolt pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
21 | 4.3.1.2.1 | Nut pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
22 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
23 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
24 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
25 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
26 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
27 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
28 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
29 |  | Equipment / line conditions
30 | 7.2.1 | Upstream / high-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
31 |  | Upstream / high-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
32 |  | Upstream / high-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
33 |  | Upstream / high-side connection orientation : | input data |  | input data
34 |  | Upstream / high-side material type : | input data |  | input data
35 |  | Downstream / low-side line size : | input data | select | input data | select |  |  |  |  | select | mm | in
36 |  | Downstream / low-side line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
37 |  | Downstream / low-side line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
38 |  | Downstream / low-side connection orientation : | input data |  | input data
39 |  | Downstream / low-side material type : | input data |  | input data
40 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
41 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
42 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
43 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
44 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
45 |  | Operating conditions
46 |  | Process fluid corrosive compounds : | input data |  | input data
47 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
48 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
49 |  | Normal operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
50 |  | Maximum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa
51 |  | Minimum operating upper fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
52 |  | Minimum operating upper material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
53 |  | Minimum operating upper material specific gravity : | input data |  | input data
54 |  | Minimum operating upper material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
55 |  | Minimum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
56 |  | Minimum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
57 |  | Minimum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
58 |  | Minimum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
59 |  | Minimum operating lower material phase type. : | select |  | select | [5 empty] | select | gas | liquid | vapour
60 |  | Minimum operating lower fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
61 |  | Minimum operating lower material specific gravity : | input data |  | input data
62 |  | Minimum operating lower material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
63 |  | Normal operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
64 |  | Normal operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
65 |  | Normal operating upper material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
66 |  | Normal operating upper fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
67 |  | Normal operating upper material specific gravity : | input data |  | input data
68 |  | Normal operating upper material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
69 |  | Normal operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
70 |  | Normal operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
71 |  | Normal operating lower material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
72 |  | Normal operating lower material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
73 |  | Normal operating lower fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
74 |  | Normal operating lower material specific gravity : | input data |  | input data
75 |  | Maximum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
76 |  | Maximum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
77 |  | Maximum operating upper material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
78 |  | Maximum operating upper fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
79 |  | Maximum operating upper material specific gravity : | input data |  | input data
80 |  | Maximum operating upper material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
81 |  | Maximum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
82 |  | Maximum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
83 |  | Maximum operating lower material phase type : | select |  | select | [5 empty] | select | gas | liquid | vapour
84 |  | Maximum operating lower fluid density at minimum operating temperature and minimum operating pressure : | input data | kg/m³ | input data | kg/m³
85 |  | Maximum operating lower material specific gravity : | input data |  | input data
86 |  | Maximum operating lower material viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
87 |  | Transmitter
88 |  | Transmitter manufacturer model number. : | input data |  | input data
89 |  | PT element fill fluid : | input data |  | input data
90 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.4, 4.3.1.1.6, 5.2.5 | PT element (sensor) material : | input data |  | input data
91 | 4.3.1.1.5 | PT element gold plating : | no |  | no | [5 empty] | select | yes | no
92 | 4.3.1.1.5 | PT element gold plating thickness : | input data | select | input data | select |  |  |  |  | select | micro-inches | nano-metres
93 | 4.3.1.1.1, 4.3.1.1.2, 4.3.1.1.3, 4.3.1.1.4, 4.3.1.1.6 | PT body wetted material : | input data |  | input data
94 |  | O-ring material : | input data |  | input data
95 |  | Transmitter enclosure material : | input data |  | input data
96 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | integral LCD display | remote indicator | not applicable
97 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
98 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
99 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
100 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
101 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
102 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
103 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
104 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
105 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
106 |  | Square root extraction : | yes |  | yes | [5 empty] | select | yes | no
107 |  | Performance
108 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
109 |  | Uncertainty : | input data |  | input data
110 |  | Response time : | input data | ms | input data | ms
111 |  | Dead time : | input data | ms | input data | ms
112 |  | Ambient temperature effect : | input data |  | input data
113 |  | Long term drift : | input data |  | input data
114 |  | Supply voltage effect : | input data |  | input data
115 | 4.2.2 | Vibration : | input data |  | input data
116 |  | Diaphragm seal
117 |  | Diaphragm seal type : | n/a |  | n/a | [5 empty] | select | 2 in extension | 4 in extension | 6 in extension | flush
118 | 5.2.7 | Diaphragm seal configuration : | not applicable |  | not applicable | [5 empty] | select | close coupled (single connection) | remote seal (single connection) | balanced system (both capillaries equal length) | unbalanced system (low side capillary - high side direct connected) | unbalanced system (high side seal - low side open to atmosphere) | not applicable
119 | 5.2.1, 5.2.2, 5.2.3 | Diaphragm seal capillary / armour material : | input data |  | input data
120 |  | Diaphragm seal capillary length : | input data | select | input data | select |  |  |  |  | select | mm | in
121 | 5.2.6, 5.2.7 | Diaphragm seal capillary fill fluid : | input data |  | input data
122 | 4.3.1.1.2 | Diaphragm seal upper housing material : | input data |  | input data
123 | 4.3.1.1.1, 4.3.1.1.2, 4.3.1.1.4, 4.3.1.1.6 | Diaphragm seal lower housing material : | input data |  | input data
124 | 4.3.1.1.4, 4.3.1.1.6, 5.2.5 | Diaphragm seal diaphragm material : | input data |  | input data
125 |  | Diaphragm seal gold plating : | no |  | no | [5 empty] | select | yes | no
126 |  | Diaphragm seal gold plating thickness : | input data | select | input data | select |  |  |  |  | select | micro-inches | nano-metres
127 |  | Diaphragm seal flushing connection : | select |  | select | [5 empty] | select | one 1/4-18NPT | two 1/4-18NPT | one 1/2 -14NPT | two 1/2-14NPT
128 |  | Diaphragm seal process connection size : | 50 |  | 50 | [5 empty] | select | 50 mm | 75 mm | 2 in | 3 in
129 |  | Diaphragm seal process connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF
130 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
131 |  | Manifold
132 |  | Manifold type : | 2 valve |  | 2 valve | [5 empty] | select | 2 valve | 5 valve | not applicable
133 |  | Manifold assembly orientation : | select |  | select | [5 empty] | select | coplanar | biplanar
134 | 4.3.1.1.2 | Manifold material : | input data |  | input data
135 |  | Manifold assembly process connection size : | select |  | select | [5 empty] | select | 12 mm | ½ in | 2 in
136 |  | Manifold assembly process connection type : | nptf |  | nptf | [5 empty] | select | nptf | RF | RTJ | FF
137 |  | Manifold assembly process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
138 |  | Manifold lockable : | no |  | no | [5 empty] | select | yes | no
139 |  | Accessories
140 |  | Weather enclosure : | select |  | select | [5 empty] | select | yes | no
141 |  | Mounting bracket : | select |  | select | [5 empty] | select | yes | no
142 |  | Mounting bracket material : | select |  | select | [5 empty] | select | 316 SS | other
143 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
144 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C19: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C20: Bolting material for pressure retaining applications as detailed in IOGP S-563.
Note on C21: Populate the nut material in line with IOGP S-563.
Note on C22: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C23: Ingress protection rating in IP or NEMA.
Note on C24: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C25: Code to be followed for the hazardous area classification.
Note on C26: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C27: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C28: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C30: Process line size to be declared to support sizing and selection by the supplier.
Note on C31: Pressure rating of the system connected.
Note on C32: Instrument process connection to be compatible with that declared by the purchaser.
Note on C33: Orientation of the inlet to the instrument or insertion point.
Note on C34: Material for the instrument to connect to on the upstream face.
Note on C35: Process line size downstream to be declared to support sizing and selection by the supplier.
Note on C36: Pressure rating of the system connected.
Note on C37: Process connection to the system.
Note on C38: Orientation of the inlet or insertion point of the instrument.
Note on C39: Material for the instrument to connect to on the downstream face.
Note on C40: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C41: This figure should be the minimum design pressure of the system installed into.
Note on C42: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C43: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C44: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C46: Free field to input any corrosive elements in the process stream
Note on C47: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C48: Differential pressure of the process at the minimum sizing case.
Note on C49: Differential pressure of the process at the normal sizing case.
Note on C50: Differential pressure of the process at the minimum sizing case.
Note on C51: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C52: Confirmation of the phase at the upper location
Note on C53: Specific gravity of the process fluid in the upper section.
Note on C54: Viscosity of the process fluid in the upper section.
Note on C55: Confirm the pressure at the upper location.
Note on C56: Confirm the upper location temperature.
Note on C57: Confirm the pressure at the lower location.
Note on C58: Confirm the lower location temperature.
Note on C59: Confirm the phase at the upper location.
Note on C60: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C61: Specific gravity of the process fluid in the upper section.
Note on C62: Viscosity of the process fluid in the upper section.
Note on C63: Confirm the pressure at the upper location.
Note on C64: Confirm the upper location temperature.
Note on C65: Confirm the phase at the upper location.
Note on C66: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C67: Specific gravity of the process fluid in the upper section.
Note on C68: Viscosity of the process fluid in the upper section.
Note on C69: Confirm the pressure at the upper location.
Note on C70: Confirm the lower location temperature.
Note on C71: Confirm the phase at the lower location.
Note on C72: Viscosity of the process fluid in the upper section.
Note on C73: Upper fluid density at temperature & pressure at minimum sizing conditions.
Note on C74: Specific gravity of the process fluid in the upper section.
Note on C75: Confirm the pressure at the upper location.
Note on C76: Confirm the upper location temperature.
Note on C77: Confirm the phase at the upper location.
Note on C78: Upper fluid density at temperature & pressure at maximum sizing conditions.
Note on C79: Specific gravity of the process fluid in the upper section.
Note on C80: Viscosity of the process fluid in the upper section.
Note on C81: Confirm the phase at the lower location.
Note on C82: Confirm the lower location temperature.
Note on C83: Confirm the phase at the lower location.
Note on C84: Upper fluid density at temperature & pressure at maximum sizing conditions.
Note on C85: Specific gravity of the process fluid in the upper section.
Note on C86: Viscosity of the process fluid in the upper section.
Note on C88: Model number for transmitter only.
Note on C89: Fill fluid within transmitter pressure capsule within the transmitter body
Note on C90: Material of diaphragm or bellow (wetted part).
Note on C91: Option to be activated if there is hydrogen present and risk of embrittlement. Default value : no
Note on C92: Supplier to declare the calculated thickness supported by calculations.
Note on C93: Material of socket inlet port (wetted part). Input "N/A" if diaphragm seal type is selected.
Note on C94: O-ring material (pressure containing) to meet the specified process requirements and if ED then relevant type e.g. transducer o-ring on ultrasonic, seal between pressure capsule and diaphragm
Note on C95: Material offered to meet the minimum requirements.
Note on C96: Select whether "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C97: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C98: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C99: Communication protocol for the transmitter. Default value : HART
Note on C100: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C101: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C102: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C103: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C104: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C105: Highest value of the measured variable that a device can be adjusted to measure.
Note on C106: Confirmation whether transmitter is to be supplied with the square root extraction active. Default value : yes
Note on C108: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C109: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C110: Response time to be provided in accordance with IEC 6282 series. Time to reach 90% output and includes 'dead time'.
Note on C111: Transmitter's response time from the moment of sensing pressure change until signal output. Generally within 1 second for special applications such as compressor anti-surge control and high integrity pressure protection systems..
Note on C112: Ambient temperature effect to be provided in accordance to IEC 62828 series
Note on C113: Long term drift figure to be provided in accordance to IEC 62828 series.
Note on C114: Supply voltage effect figure to be provided in accordance to IEC 62828 series.
Note on C115: Vibration to be selected in accordance with the requirements of IEC 62828-1 table 4, typical value is "10 to 1000 Hz with 0,15mm peak amplitude and 20m/s²".
Note on C117: State the length to which the seal is to protrude inside the nozzle or flush if no extension required. Default value : n/a
Note on C118: Type of diaphragm seal configuration to be selected for chosen application. Default value : not applicable
Note on C119: To be suitable for the ambient conditions and fill fluid; select "N/A" if direct mount.
Note on C120: For a balanced system the length is to be for both capillaries. For an unbalanced system refer to "instrumentation type" datasheet field to determine whether high or low pressure leg.
Note on C121: Silicon or glycerin are standard, subject to operating temperature of the process. Ensure complies with API RP 551, 9.3.1 selection guidance.
Note on C122: Minimum 316 Stainless Steel is common but dependent on fill fluid more exotic material selection can apply.
Note on C123: Minimum 316 Stainless Steel is common but dependent on fill fluid more exotic material selection can apply.
Note on C124: Wetted part material to be suitable for process fluids requirement, normally 316 Stainless Steel or Hastelloy C-276
Note on C125: Option to be activated if there is hydrogen present and risk of embrittlement. Default value : no
Note on C126: Supplier to declare the calculated thickness supported by calculations.
Note on C127: Flushing function is required, declaration size of threaded connection.
Note on C128: Select from 50mm (2 in) or 75mm (3 in) for flanged connection. Default value : 50
Note on C129: Flange finish to be selected. Default value : RF
Note on C130: Input the diaphragm flange rating in line with the installed rating and as per piping specification.
Note on C132: "2 valve" is normally specified for pressure transmitter applications, "5 valve" is specified for differential pressure. "N/A" is used if a diaphragm seal is selected. Default value : 2 valve
Note on C133: Select either coplanar for bottom entry or biplanar for side entry.
Note on C134: Normally 316L SS minimum to meet process requirements.
Note on C135: Detail connection size at the boundary point of suppliers interface to the process.
Note on C136: Select the connection of the manifold to the process. The standard is NPTF allowing for tubing and fitting connections. Default value : nptf
Note on C137: Provide the pressure rating of flanged connection.
Note on C138: Confirmation whether the manifold shall is have the capability to lock the valves in position. Default value : no
Note on C140: Purchaser to advise whether enclosure required and to add to "additional notes" column if enclosure to include other tags.
Note on C141: Select "Yes" if remote mount; select "No" if direct mount.
Note on C142: Minimum material 316 Stainless Steel but others can be selected if more suitable.
Note on C143: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C144: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Pressure Transmitter
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Pressure Transmitters | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Instrumentation type : | select |  | select | [5 empty] | select | pressure transmitter (gauge) | pressure transmitter (absolute)
5 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
6 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
7 | 4.1.2.2 | Tag number : | input data |  | input data
8 |  | Tag description : | input data |  | input data
9 |  | Manufacturer : | input data |  | input data
10 |  | Assembly model number : | input data |  | input data
11 |  | Equipment manufacturer serial number : | input data |  | input data
12 |  | Project country : | input data |  | input data
13 |  | Project region : | input data |  | input data
14 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
15 |  | P&ID number : | input data |  | input data
16 |  | Line or equipment number : | input data |  | input data
17 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
19 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
20 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
21 | 4.3.1.1.2, 4.3.1.2.1 | Bolt pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
22 | 4.3.1.2.1 | Nut pressure retaining, material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120
23 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
24 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
25 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
26 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
27 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
28 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
29 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
30 |  | Equipment / line conditions
31 | 7.2.1 | Process connection line size : | input data | select | input data | select |  |  |  |  | select | mm | in
32 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
33 |  | Process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
34 |  | Process connection material type : | input data |  | input data
35 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
36 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
37 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
38 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
39 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
40 |  | Operating conditions
41 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
42 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
43 |  | Process fluid corrosive compounds : | input data |  | input data
44 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
45 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
46 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
47 |  | Minimum operating liquid specific gravity : | input data |  | input data
48 |  | Minimum operating liquid specific gravity at standard conditions : | input data |  | input data
49 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
50 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
51 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
52 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
53 |  | Normal operating liquid specific gravity : | input data |  | input data
54 |  | Normal operating liquid specific gravity at standard conditions : | input data |  | input data
55 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
56 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
57 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
58 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
59 |  | Maximum operating liquid specific gravity : | input data |  | input data
60 |  | Maximum operating liquid specific gravity at standard conditions : | input data |  | input data
61 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
62 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
63 |  | Transmitter
64 |  | Transmitter manufacturer model number. : | input data |  | input data
65 |  | PT element fill fluid : | input data |  | input data
66 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.4, 4.3.1.1.6, 5.2.5 | PT element (sensor) material : | input data |  | input data
67 | 4.3.1.1.5 | PT element gold plating : | no |  | no | [5 empty] | select | yes | no
68 | 4.3.1.1.5 | PT element gold plating thickness : | input data | select | input data | select |  |  |  |  | select | micro-inches | nano-metres
69 | 4.3.1.1.1, 4.3.1.1.2, 4.3.1.1.3, 4.3.1.1.4, 4.3.1.1.6 | PT body wetted material : | input data |  | input data
70 |  | O-ring material : | input data |  | input data
71 |  | Transmitter enclosure material : | input data |  | input data
72 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | integral LCD display | remote indicator | not applicable
73 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
74 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
75 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
76 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
77 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
78 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
79 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
80 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
81 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
82 |  | Performance
83 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
84 |  | Uncertainty : | input data |  | input data
85 |  | Response time : | input data | ms | input data | ms
86 |  | Dead time : | input data | ms | input data | ms
87 |  | Ambient temperature effect : | input data |  | input data
88 |  | Long term drift : | input data |  | input data
89 |  | Supply voltage effect : | input data |  | input data
90 | 4.2.2 | Vibration : | input data |  | input data
91 |  | Diaphragm seal
92 |  | Diaphragm seal type : | n/a |  | n/a | [5 empty] | select | 2 in extension | 4 in extension | 6 in extension | flush
93 | 5.2.7 | Diaphragm seal configuration : | not applicable |  | not applicable | [5 empty] | select | close coupled (single connection) | remote seal (single connection) | balanced system (both capillaries equal length) | unbalanced system (low side capillary - high side direct connected) | unbalanced system (high side seal - low side open to atmosphere) | not applicable
94 | 5.2.1, 5.2.2, 5.2.3 | Diaphragm seal capillary / armour material : | input data |  | input data
95 |  | Diaphragm seal capillary length : | input data | select | input data | select |  |  |  |  | select | mm | in
96 | 5.2.6, 5.2.7 | Diaphragm seal capillary fill fluid : | input data |  | input data
97 | 4.3.1.1.2 | Diaphragm seal upper housing material : | input data |  | input data
98 | 4.3.1.1.1, 4.3.1.1.2, 4.3.1.1.4, 4.3.1.1.6 | Diaphragm seal lower housing material : | input data |  | input data
99 | 4.3.1.1.4, 4.3.1.1.6, 5.2.5 | Diaphragm seal diaphragm material : | input data |  | input data
100 |  | Diaphragm seal gold plating : | no |  | no | [5 empty] | select | yes | no
101 |  | Diaphragm seal gold plating thickness : | input data | select | input data | select |  |  |  |  | select | micro-inches | nano-metres
102 |  | Diaphragm seal flushing connection : | select |  | select | [5 empty] | select | one 1/4-18NPT | two 1/4-18NPT | one 1/2 -14NPT | two 1/2-14NPT
103 |  | Diaphragm seal process connection size : | 50 |  | 50 | [5 empty] | select | 50 mm | 75 mm | 2 in | 3 in
104 |  | Diaphragm seal process connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF
105 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
106 |  | Manifold
107 |  | Manifold type : | 2 valve |  | 2 valve | [5 empty] | select | 2 valve | 5 valve | not applicable
108 |  | Manifold assembly orientation : | select |  | select | [5 empty] | select | coplanar | biplanar
109 | 4.3.1.1.2 | Manifold material : | input data |  | input data
110 |  | Manifold assembly process connection size : | select |  | select | [5 empty] | select | 12 mm | ½ in | 2 in
111 |  | Manifold assembly process connection type : | nptf |  | nptf | [5 empty] | select | nptf | RF | RTJ | FF
112 |  | Manifold assembly process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
113 |  | Manifold lockable : | no |  | no | [5 empty] | select | yes | no
114 |  | Accessories
115 |  | Weather enclosure : | select |  | select | [5 empty] | select | yes | no
116 |  | Mounting bracket : | select |  | select | [5 empty] | select | yes | no
117 |  | Mounting bracket material : | select |  | select | [5 empty] | select | 316 SS | other
118 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
119 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Select the instrument type (technology) to be purchased
Note on C5: Code compliance to be for the region where the instrument is to be installed.
Note on C6: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C7: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C8: A functional description of the tag.
Note on C9: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C10: Input the model number of the offered instrument assembly / unit.
Note on C11: Unique identification number for the equipment as prescribed by the supplier.
Note on C12: Name assigned by ISO to the country, in ISO 3166-1.
Note on C13: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C14: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C15: P&ID number where the orifice plate assembly is indicated
Note on C16: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C17: Fill in as per process data
Note on C18: Fill in as per process data
Note on C19: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C20: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C21: Bolting material for pressure retaining applications as detailed in IOGP S-563.
Note on C22: Populate the nut material in line with IOGP S-563.
Note on C23: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C24: Ingress protection rating in IP or NEMA.
Note on C25: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C26: Code to be followed for the hazardous area classification.
Note on C27: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C28: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C29: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C31: Purchaser to declare the connection size to the process.
Note on C32: Pressure rating of the system connected.
Note on C33: Select the connection type to the process.
Note on C34: Purchaser to declare the material of the process flange.
Note on C35: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C36: This figure should be the minimum design pressure of the system installed into.
Note on C37: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C38: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C39: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C41: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C42: Confirm whether it is a liquid or vapour phase.
Note on C43: Free field to input any corrosive elements in the process stream
Note on C44: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C45: Temperature of the process at the minimum sizing case.
Note on C46: Differential pressure of the process at the minimum sizing case.
Note on C47: Specific gravity of the process fluid at the min sizing case
Note on C48: Liquid SG at standard conditions at the minimum sizing case.
Note on C49: Viscosity of the process fluid at minimum sizing conditions
Note on C50: Vapour viscosity at minimum sizing conditions.
Note on C51: Temperature of the process at the minimum sizing case.
Note on C52: Pressure of the process for the normal operating case.
Note on C53: Specific gravity of the process fluid at the normal sizing case
Note on C54: Liquid SG at standard conditions at the normal sizing case.
Note on C55: Viscosity of the process fluid at the normal sizing case.
Note on C56: Vapour viscosity at normal sizing conditions.
Note on C57: Temperature of the process at the minimum sizing case.
Note on C58: Pressure of the process for the maximum operating case.
Note on C59: Specific gravity of the process fluid at the maximum sizing case.
Note on C60: Liquid SG at standard conditions at the maximum sizing case.
Note on C61: Viscosity of the process fluid at maximum sizing conditions.
Note on C62: Vapour viscosity at maximum sizing conditions.
Note on C64: Model number for transmitter only.
Note on C65: Fill fluid within transmitter pressure capsule within the transmitter body
Note on C66: Material of diaphragm or bellow (wetted part).
Note on C67: Option to be activated if there is hydrogen present and risk of embrittlement. Default value : no
Note on C68: Supplier to declare the calculated thickness supported by calculations.
Note on C69: Material of socket inlet port (wetted part). Input "N/A" if diaphragm seal type is selected.
Note on C70: O-ring material (pressure containing) to meet the specified process requirements and if ED then relevant type e.g. transducer o-ring on ultrasonic, seal between pressure capsule and diaphragm
Note on C71: Material offered to meet the minimum requirements.
Note on C72: Select whether "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C73: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C74: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C75: Communication protocol for the transmitter. Default value : HART
Note on C76: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C77: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C78: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C79: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C80: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C81: Highest value of the measured variable that a device can be adjusted to measure.
Note on C83: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C84: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C85: Response time to be provided in accordance with IEC 6282 series. Time to reach 90% output and includes 'dead time'.
Note on C86: Transmitter's response time from the moment of sensing pressure change until signal output. Generally within 1 second for special applications such as compressor anti-surge control and high integrity pressure protection systems..
Note on C87: Ambient temperature effect to be provided in accordance to IEC 62828 series
Note on C88: Long term drift figure to be provided in accordance to IEC 62828 series.
Note on C89: Supply voltage effect figure to be provided in accordance to IEC 62828 series.
Note on C90: Vibration to be selected in accordance with the requirements of IEC 62828-1 table 4, typical value is "10 to 1000 Hz with 0,15mm peak amplitude and 20m/s²".
Note on C92: State the length to which the seal is to protrude inside the nozzle or flush if no extension required. Default value : n/a
Note on C93: Type of diaphragm seal configuration to be selected for chosen application. Default value : not applicable
Note on C94: To be suitable for the ambient conditions and fill fluid; select "N/A" if direct mount.
Note on C95: For a balanced system the length is to be for both capillaries. For an unbalanced system refer to "instrumentation type" datasheet field to determine whether high or low pressure leg.
Note on C96: Silicon or glycerin are standard, subject to operating temperature of the process. Ensure complies with API RP 551, 9.3.1 selection guidance.
Note on C97: Minimum 316 Stainless Steel is common but dependent on fill fluid more exotic material selection can apply.
Note on C98: Minimum 316 Stainless Steel is common but dependent on fill fluid more exotic material selection can apply.
Note on C99: Wetted part material to be suitable for process fluids requirement, normally 316 Stainless Steel or Hastelloy C-276
Note on C100: Option to be activated if there is hydrogen present and risk of embrittlement. Default value : no
Note on C101: Supplier to declare the calculated thickness supported by calculations.
Note on C102: Flushing function is required, declaration size of threaded connection.
Note on C103: Select from 50mm (2 in) or 75mm (3 in) for flanged connection. Default value : 50
Note on C104: Flange finish to be selected. Default value : RF
Note on C105: Input the diaphragm flange rating in line with the installed rating and as per piping specification.
Note on C107: "2 valve" is normally specified for pressure transmitter applications, "5 valve" is specified for differential pressure. "N/A" is used if a diaphragm seal is selected. Default value : 2 valve
Note on C108: Select either coplanar for bottom entry or biplanar for side entry.
Note on C109: Normally 316L SS minimum to meet process requirements.
Note on C110: Detail connection size at the boundary point of suppliers interface to the process.
Note on C111: Select the connection of the manifold to the process. The standard is NPTF allowing for tubing and fitting connections. Default value : nptf
Note on C112: Provide the pressure rating of flanged connection.
Note on C113: Confirmation whether the manifold shall is have the capability to lock the valves in position. Default value : no
Note on C115: Purchaser to advise whether enclosure required and to add to "additional notes" column if enclosure to include other tags.
Note on C116: Select "Yes" if remote mount; select "No" if direct mount.
Note on C117: Minimum material 316 Stainless Steel but others can be selected if more suitable.
Note on C118: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C119: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Temperature Transmitter
Row | S-718D Procurement Data Sheet for Basic Process Measurement Instruments Temperature Transmitter | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.2 | Tag number : | input data |  | input data
7 |  | Tag description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 |  | Assembly model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 |  | Project country : | input data |  | input data
12 |  | Project region : | input data |  | input data
13 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine coastal | subsea | buried | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 |  | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.3.2.1, 4.3.2.2, 4.3.2.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C1 | C2 | C3 | C4 | C5 | CX
19 | 4.3.2.2 | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
20 | 4.1.4 | SIL : | not applicable |  | not applicable | [5 empty] | select | 1 | 2 | 3 | not applicable
21 | 4.5.2, 5.2.3, 6.3.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X | NEMA 7
22 | 4.3.4.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
23 | 4.3.4.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Art. 500 | NFPA 70 Art. 505
24 | 4.3.4.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
25 | 4.3.4.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
26 | 4.3.4.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
27 |  | Equipment / line conditions
28 |  | Process connection pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
29 | 7.2.1 | Process connection line size : | input data | select | input data | select |  |  |  |  | select | mm | in
30 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
31 |  | Process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
32 |  | Process connection material type : | input data |  | input data
33 |  | Design pressure, maximum : | input data | select | input data | select |  |  |  |  | select | barg | psig
34 |  | Design pressure, minimum : | input data | select | input data | select |  |  |  |  | select | barg | psig
35 |  | Design temperature, maximum : | input data | select | input data | select |  |  |  |  | select | °C | °F
36 |  | Design temperature, minimum : | input data | select | input data | select |  |  |  |  | select | °C | °F
37 |  | Sour service specification : | not applicable |  | not applicable | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
38 | 7.2.4 | Insulation thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
39 |  | Operating conditions
40 | 4.3.1.1.2, 4.3.1.4.2 | Process fluid : | input data |  | input data
41 | 5.2.5 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
42 |  | Process fluid corrosive compounds : | input data |  | input data
43 |  | Process fluid erosion possibiliy : | select |  | select | [5 empty] | select | yes | no
44 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
45 | 7.3.3 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
46 |  | Minimum operating velocity : | input data | m/s | input data | m/s
47 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
48 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kpa
49 |  | Minimum operating liquid specific gravity : | input data |  | input data
50 |  | Minimum operating liquid specific gravity at standard conditions : | input data |  | input data
51 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
52 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
53 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
54 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
55 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
56 |  | Normal operating velocity : | input data | m/s | input data | m/s
57 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
58 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
59 |  | Normal operating liquid specific gravity : | input data |  | input data
60 |  | Normal operating liquid specific gravity at standard conditions : | input data |  | input data
61 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
62 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
63 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
64 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
65 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
66 |  | Maximum operating velocity : | input data | m/s | input data | m/s
67 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
68 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kpag
69 |  | Maximum operating liquid specific gravity : | input data |  | input data
70 |  | Maximum operating liquid specific gravity at standard conditions : | input data |  | input data
71 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
72 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
73 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
74 |  | Worst case velocity for thermowell calculation : | input data | m/s | input data | m/s
75 |  | Body/element/sensor
76 |  | Body/element/sensor manufacturer model number : | input data |  | input data
77 |  | Temperature element type : | select |  | select | [5 empty] | select | RTD PT 100 3-wire | RTD PT 100 4-wire | TC type J | TC type B | TC type E | TC type K | TC type N | TC type R | TC type S | TC type T | TC type C
78 |  | Temperature element tolerance class : | select |  | select | [5 empty] | select | Class AA (IEC 60751) | Class BB (IEC 60751) | Class A | Class B (IEC 60751) | Grade A (ASTM E1137) | Grade B (ASTM E1137) | Class 1 (IEC 60584) | Class 2 (IEC 60584) | special tolerance (ASTM E230) | standard tolerance (ASTM E230)
79 |  | Temperature element sheath material : | input data |  | input data
80 | 6.1.9 | Temperature element, simplex/duplex : | select |  | select | [5 empty] | select | simplex | duplex
81 |  | Temperature element sheath outside diameter : | 6 mm |  | 6 mm | [5 empty] | select | 6 mm | ¼ inch | other
82 |  | Temperature element nipple-union-nipple material : | input data |  | input data
83 |  | RTD number of terminals : | 6 |  | 6 | [5 empty] | select | 6 | 8
84 | 6.2 | Thermocouple tip : | ungrounded |  | ungrounded | [5 empty] | select | grounded | ungrounded
85 |  | Thermowell type (seamless) : | select |  | select | [5 empty] | select | single piece bar | single piece forged | Van Stone
86 |  | Thermowell design : | tapered |  | tapered | [5 empty] | select | tapered | straight | stepped
87 | 4.3.1.1.1, 4.3.1.1.2, 4.3.1.1.4, 4.3.1.1.6 | Thermowell material : | input data |  | input data
88 |  | Thermowell process connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF
89 |  | Thermowell process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
90 |  | Thermowell process connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
91 |  | Thermowell insertion length (U) : | input data | select | input data | select |  |  |  |  | select | mm | inch
92 |  | Thermowell extension length (T) : | input data | select | input data | select |  |  |  |  | select | mm | inch
93 |  | Thermowell root diameter (A) : | input data | select | input data | select |  |  |  |  | select | mm | in
94 |  | Thermowell tip diameter (B) : | input data | select | input data | select |  |  |  |  | select | mm | in
95 |  | Thermowell bore diameter (d) : | 6.6 mm |  | 6.6 mm | [5 empty] | select | 6.6 mm | 0.26 inch | other
96 |  | Thermowell tip thickness (t) : | input data | select | input data | select |  |  |  |  | select | mm | in
97 |  | Thermowell fillet radius (b) : | input data | select | input data | select |  |  |  |  | select | mm | in
98 |  | Thermowell shielded length (Lo) : | input data | select | input data | select |  |  |  |  | select | mm | in
99 |  | Transmitter
100 |  | Transmitter manufacturer model number. : | input data |  | input data
101 |  | Transmitter enclosure material : | input data |  | input data
102 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | integral LCD display | remote indicator | not applicable
103 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
104 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
105 | 4.1.2.3 | Communication protocol : | HART |  | HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Profibus
106 |  | HART Version : | 7 |  | 7 | [5 empty] | select | 5 | 6 | 7 | 8 | other | not applicable
107 | 4.1.2.2 | Fail safe direction : | fail low |  | fail low | [5 empty] | select | fail high | fail low
108 | 4.1.2.2, 4.1.3.2, 7.3.3 | Calibrated range, low : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
109 | 4.1.2.2, 4.1.3.2 | Calibrated range, high : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
110 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
111 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | m | in | °C | °F | barg | psig | kPag | kg/h | lb/h
112 | 6.1.4 | Linearization : | select |  | select | [5 empty] | select | ASTM | NIST | other | inactive - raw signal
113 |  | Performance
114 | 7.1.5, 8.1.4, Table 4, Table 8 | Accuracy : | input data | % of span | input data | % of span
115 |  | Uncertainty : | input data |  | input data
116 |  | Dead time : | input data | ms | input data | ms
117 |  | Ambient temperature effect : | input data |  | input data
118 |  | Long term drift : | input data |  | input data
119 |  | Supply voltage effect : | input data |  | input data
120 | 4.2.2 | Vibration : | input data |  | input data
121 |  | Accessories
122 |  | Electrical surge protector : | no |  | no | [5 empty] | select | yes | no
123 |  | Sunshade : | no |  | no | [5 empty] | select | yes | no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Code compliance to be for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Indicate the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C7: A functional description of the tag.
Note on C8: Provide the manufacturer's name after the package evaluation, but prior to the purchase order
Note on C9: Input the model number of the offered instrument assembly / unit.
Note on C10: Unique identification number for the equipment as prescribed by the supplier.
Note on C11: Name assigned by ISO to the country, in ISO 3166-1.
Note on C12: Geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Describe the location of the facility (e.g. offshore, coastal, subsea) where the equipment will be permanently installed.
Note on C14: P&ID number where the orifice plate assembly is indicated
Note on C15: Line, vessel or equipment where the instrument assembly is installed for measurement purpose
Note on C16: Fill in as per process data
Note on C17: Fill in as per process data
Note on C18: Specify the atmospheric corrosivity category in accordance with ISO 12944-2. Default value : C3
Note on C19: Specify the required project painting durability level or "N/A" if painting is not required.
Note on C20: Select the relevant SIL level required, if instrumentation not used in a safety loop, select "not applicable". Default value : not applicable
Note on C21: Ingress protection rating in IP or NEMA.
Note on C22: Electrical protection for the specified hazardous area (e.g. Ex ia, Ex d). Default value : Exia
Note on C23: Code to be followed for the hazardous area classification.
Note on C24: Specify the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C25: Specify the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C26: Specify the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, 505) or division classification (NFPA 70, 500).
Note on C28: Selection of the pipe schedule in accordance with the pipe specification.
Note on C29: Purchaser to declare the connection size to the process.
Note on C30: Pressure rating of the system connected.
Note on C31: Select the connection type to the process.
Note on C32: Purchaser to declare the material of the process flange.
Note on C33: This figure should be below the maximum allowable working pressure (MAWP) of the system installed into and depending on company standards, it can be 10 to 25% above the maximum operating pressure.
Note on C34: This figure should be the minimum design pressure of the system installed into.
Note on C35: This figure should be below the maximum temperature of the system installed into and depending on company standards can be 10 to 25% above the maximum operating temperature.
Note on C36: This figure should be the minimum design temperature of the system the instrument is installed into.
Note on C37: Code selection not only dependent on the H2S concentration, other factors include pressure, temperature, pH, concentration of other contaminants such as chlorides, cyanide, etc. Default value : not applicable
Note on C38: Insulation material thickness of the process pipe, vessel or equipment where the thermowell or orifice plate is connected.
Note on C40: Process fluid according to the process data sheet wetted parts to be compatible.
Note on C41: Confirm whether it is a liquid or vapour phase.
Note on C42: Free field to input any corrosive elements in the process stream
Note on C43: Purchaser to advise whether the process has erosive particles contained within. If 'yes' is selected, further details are to be provided on the supplementary notes sheet.
Note on C44: Operating mass flow rate of the system to which it is installed at the minimum sizing case.
Note on C45: Operating volumetric flow rate of the system at mimimum sizing case
Note on C46: Operating velocity of the system at the minimum sizing case.
Note on C47: Temperature of the process at the minimum sizing case.
Note on C48: Differential pressure of the process at the minimum sizing case.
Note on C49: Specific gravity of the process fluid at the min sizing case
Note on C50: Liquid SG at standard conditions at the minimum sizing case.
Note on C51: Viscosity of the process fluid at minimum sizing conditions
Note on C52: Vapour molecular weight of the process fluid at minimum sizing conditions
Note on C53: Vapour actual density at minimum sizing conditions
Note on C54: Normal operating flow rate of the system to which it is installed
Note on C55: Operating volumetric flow rate of the system at normalsizing case
Note on C56: Operating velocity of the system at the normal sizing case.
Note on C57: Temperature of the process at the minimum sizing case.
Note on C58: Pressure of the process for the normal operating case.
Note on C59: Specific gravity of the process fluid at the normal sizing case
Note on C60: Liquid SG at standard conditions at the normal sizing case.
Note on C61: Viscosity of the process fluid at the normal sizing case.
Note on C62: Vapour molecular weight of the process fluid at normal sizing conditions.
Note on C63: Vapour actual density at normal sizing conditions.
Note on C64: Operating mass flow rate of the system to which it is installed at maximum sizing case.
Note on C65: Operating volumetric flow rate of the system at maximum sizing case.
Note on C66: Operating velocity of the system at the maximum sizing case.
Note on C67: Temperature of the process at the minimum sizing case.
Note on C68: Pressure of the process for the maximum operating case.
Note on C69: Specific gravity of the process fluid at the maximum sizing case.
Note on C70: Liquid SG at standard conditions at the maximum sizing case.
Note on C71: Viscosity of the process fluid at maximum sizing conditions.
Note on C72: Vapour molecular weight of the process fluid at maximum sizing conditions.
Note on C73: Vapour actual density at minimum sizing conditions.
Note on C74: Purchaser to input the worst case maximum velocity of fluid, taking into consideration cases of slugging, blowdown or flaring.
Note on C76: Supplier to specify model number of body/element/sensor.
Note on C77: Select the temperature element type required.
Note on C78: Class or Grade tolerances should be defined as per the applicable standard.
Note on C79: Sheath material (metal or others) are to be suitable for the specified operating environment.
Note on C80: Select whether a single or duplex element is required.
Note on C81: OD of the element to fit inside the thermowell Default value : 6 mm
Note on C82: Nipple material shall be suitable for the environment conditions
Note on C83: Terminal block to cater for duplex installations and selection from six or eight terminals Default value : 6
Note on C84: Select "Grounded" or "Ungrounded". Default value : ungrounded
Note on C85: Select "single piece bar", "single piece forged" or "Van Stone" type thermowell of seamless construction.
Note on C86: Select "tapered", "straight" or "stepped" fabricated from single piece bar stock. Geometry of thermowell to be in accordance with ASME PTC 19.3 TW. Default value : tapered
Note on C87: Material of thermowell is a wetted part and shall be suitable for the process fluids.
Note on C88: Standard flange connections. Default value : RF
Note on C89: Input the flange rating as per the piping specification.
Note on C90: Input the flange size which is compatible with process connection flange.
Note on C91: Length measured from the bottom of the flange to the tip of the thermowell. ASME PTC 19.3 TW uses the term "unsupported length"' with variable "L".
Note on C92: Length measured from the bottom of the flange to the top of the thermowell assembly, including any nipple extension. Terminal heads attached to thermowells with extension pieces providing space for at least 80 mm, 3 inch insulation.
Note on C93: Supplier to advise the root diameter of the model supplied and figure to be used in calculations.
Note on C94: Supplier to advise the tip diameter of the model supplied and figure to be used in calculations.
Note on C95: Supplier to advise the bore diameter and figure to be used in calculations, the standard size in industry being 6.6mm (0.26 inch). Test thermowells can be 9.8mm (0.385 inch) to allow easy insertion and removal. Default value : 6.6 mm
Note on C96: Supplier to advise the tip thickness of the model supplied and figure to be used in calculations.
Note on C97: Supplier to advise the fillet radius (b) of the model supplied and figure to be used in calculations.
Note on C98: Supplier to advise the shielded length of the model supplied and figure to be used in calculations.
Note on C100: Model number for transmitter only.
Note on C101: Material offered to meet the minimum requirements.
Note on C102: Select whether "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C103: The power supply to the instrument generally 24Vdc. Default value : 24 V DC loop power
Note on C104: Size of cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5 Default value : M20 x 1.5
Note on C105: Communication protocol for the transmitter. Default value : HART
Note on C106: To specify the required version of HART protocol, default version 7. Intelligent transmitters with 4-20 mA hardwired outputs to be supplied with the latest version of the HART protocol. Default value : 7
Note on C107: Specific requirement to specify the fail direction for transmitters when the status is faulty Default value : fail low
Note on C108: The low setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C109: The high setting for calibration purposes. Most common used units are m³/h, ft³/h, kg/h, lb/h, m, in, °C, °F, bara, psia, kPaa, barg, psig, kPag, bar, psi, kPa, %, mmH2O, inH2O, mmHg, inHg, mbar
Note on C110: Lowest value of the measured variable that a device can be adjusted to measure.
Note on C111: Highest value of the measured variable that a device can be adjusted to measure.
Note on C112: Purchaser to advise whether the output from the temperature transmitter is to be linearized as per industry standard tables such ASTM and NIST.
Note on C114: Purchaser to initially populate the required accuracy for the given service. Units typically are percentage of span.
Note on C115: Provide the uncertainty figure for the range within which the measured value lies and is an indicator of the performance available from the instrument
Note on C116: Transmitter's response time from the moment of sensing pressure change until signal output. Generally within 1 second for special applications such as compressor anti-surge control and high integrity pressure protection systems..
Note on C117: Ambient temperature effect to be provided in accordance to IEC 62828 series
Note on C118: Long term drift figure to be provided in accordance to IEC 62828 series.
Note on C119: Supply voltage effect figure to be provided in accordance to IEC 62828 series.
Note on C120: Vibration to be selected in accordance with the requirements of IEC 62828-1 table 4, typical value is "10 to 1000 Hz with 0,15mm peak amplitude and 20m/s²".
Note on C122: Transmitter's protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C123: Protection of the transmitter against direct exposure to sun causing problems to its operation. Default value : no

## Supplement
Row |  | S-718D Procurement Data Sheets for Basic Process Measurement Instruments | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
9
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
Public Review Draft

## Guidance
S-718D Procurement Data Sheets for
Basic Process Measurement Instruments
Guidance on the use of this procurement data sheet
To be used in conjunction with :
IOGP S-718 Specification for Basic Process Measurement Instruments.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
Public Review Draft
Public Review Draft

## Back Cover
Month XXXX
Public Review Draft