## Front & Preliminaries
|  |  |  | SPECIFICATION | March
|  |  |  | S-733D | 2022
Procurement Data Sheet for
Low Voltage Motors
(IEEE Std 841-2021)
Revision history
| VERSION | DATE | PURPOSE
| 1.1 | March 2022 | Issued for Public Review
| 1 | November 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-733D Procurement Data Sheet for
Low Voltage Motors (IEEE Std 841-2021)
Revision description
- The following rows have been added: 13, 16, 110, 41, 76, 108 - The following rows have been edited: 3, 15, 35, 111, 23, 44, 53, 61, 70, 71, 72, 78, 80, 81, 84, 86, 87, 89, 90, 92, 93, 94, 30, 71, 120
S-733D Procurement Data Sheet for
Low Voltage Motors (IEEE Std 841-2021)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
S-733D Procurement Data Sheet for
Low Voltage Motors (IEEE Std 841-2021)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of low voltage motors and shall be used in conjunction with IEEE Std 841-2021, IEEE Standard for Petroleum and Chemical Industry—Premium-Efficiency, Severe-Duty, Totally Enclosed Fan-Cooled (TEFC) Squirrel Cage Induction Motors—From 0.75 kW to 370 kW (1 hp to 500 hp).
This procurement data sheet defines application specific requirements, attributes and options specified by the purchaser for the supply of the equipment. This procurement data sheet may also include fields for supplier-provided information attributes subject to purchaser’s technical evaluation. Additional purchaser supplied documents may also be incorporated or referenced in the procurement data sheet to define the scope and the technical requirements for enquiry and purchase of the equipment.
Purchaser required quality and information requirements are also included in this procurement data sheet.
This procurement data sheet is in accordance with IEEE Std 841-2021. However, it excludes medium voltage motors.
The terminology used within this data sheet follows that of IEEE Std 841-2021 and is in accordance with ISO/IEC Directives, Part 2 as appropriate.
This procurement data sheet is published as an editable document for the purchaser to specify application specific requirements.
Information requirements
Information requirements are defined under the Documentation section of this procurement data sheet.
Inspection and testing requirements
Inspection and testing requirements are defined under the Inspection and testing section of this procurement data sheet.
Quality management system
The supplier quality management system shall conform to one of the following: ISO 9001, ISO 29001, API Specification Q1 or an equivalent quality management system standard.
Normative references
The following documents are referred to in the data sheet in such a way that some or all of their content constitutes requirements of this document. For dated references, only the edition cited applies. For undated references, the latest edition of the references document (including any amendments) applies:
— UL Standard 674, Electric Motors and Generators for Use in Hazardous (Classified) Locations;
— ISO 12944-1, Paints and varnishes — Corrosion protection of steel structures by protective paint systems — Part 1: General introduction;
— ISO 12944-2, Paints and varnishes — Corrosion protection of steel structures by protective paint systems — Part 2: Classification of environments.
Order of precedence
The order of precedence (highest authority listed first) of the documents shall be:
a) regulatory requirements; b) contract documentation (e.g. purchase order); c) purchaser defined requirements (procurement data sheet); d) IEEE Std 841-2021.
JIP33 Specification for Procurement Documents Procurement Data Sheet
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Procurement Data Sheet
Row | S-733D Data Sheet for Low Voltage Motors (IEEE Std 841-2021) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Order status : | select |  | select | [5 empty] | select | for enquiry (purchaser to supplier) | for proposal (supplier to purchaser)
4 |  | Purchaser information
5 |  | Client name : | input data |  | input data
6 |  | Site or location : | input data |  | input data
7 |  | Project title or number : | input data |  | input data
8 |  | Purchase order number : | input data |  | input data
9 |  | Date : | input data |  | input data
10 |  | General
11 |  | Manufacturer : | input data |  | input data
12 |  | Model number : | input data |  | input data
13 | 14.1, 14.2, 14.3, 14.4, 14.5 | IEEE Std 841 motor type : | IEEE Std 841-2021 motor |  | IEEE Std 841-2021 motor | [5 empty] | select | IEEE Std 841-2021 motor | IEEE Std 841-2021 features motor | IEEE Std 841-2021 non-compliant
14 |  | Additional certification : | none |  | none | [5 empty] | select | none | other
15 | 6.3.1 | Starting method : | direct on line (DOL) |  | direct on line (DOL) | [5 empty] | select | direct on line (DOL) | soft start | ASD | other
16 | 5.4 | Number of poles/motor synchronous speed : | 4 poles/1800 rpm/1500 rpm |  | 4 poles/1800 rpm/1500 rpm | [5 empty] | select | 2 poles/3600 rpm/3000 rpm | 4 poles/1800 rpm/1500 rpm | 6 poles/1200 rpm/1000 rpm | 8 poles/900 rpm/750 rpm
17 | 6.1 | Direction of rotation : | bi-directional |  | bi-directional | [5 empty] | select | bi-directional | clockwise | counter-clockwise
18 |  | Method of motor coupling to driven equipment : | select |  | select | [5 empty] | select | direct | belt | gearbox
19 | 7.1 | External radial loading on motor shaft end : | input data | select | input data | select |  |  |  |  | select | lb | N
20 | 7.1 | External axial loading on motor shaft end : | input data | select | input data | select |  |  |  |  | select | lb | N
21 |  | Electrical operating conditions
22 | 4.2, 5.3 | Motor rated frequency : | 60 | Hz | 60 | Hz |  |  |  |  | select | 60 | 50
23 | 4.2, 5.3 | Motor rated voltage : | select | V AC | select | V AC |  |  |  |  | select | 200 | 220 | 230 | 380 | 460 | 575 | 660
24 |  | Rating
25 | 5.2 | Frame size : | input data |  | input data
26 | 5.1 | Rated power output : | input data | select | input data | select |  |  |  |  | select | kW | hp
27 | 5.1 | Service factor : | 1 |  | 1 | [5 empty] | select | 1 | 1.15
28 | 6.1 | Full load current (FLC) : | input data | A | input data | A
29 |  | ASD fed motor data
30 | 4.2, 6.2, 6.3.2.1 | Load type : | variable torque |  | variable torque | [5 empty] | select | variable torque | constant torque | constant horsepower
31 | 6.3.2.1 | Minimum operating speed : | input data | rpm | input data | rpm
32 | 6.3.2.1 | Maximum operating speed : | input data | rpm | input data | rpm
33 |  | Site conditions
34 |  | Location environment
35 |  | Floating/marine/shipboard : | not applicable |  | not applicable | [5 empty] | select | not applicable | applicable
36 | 4.1, 4.2 | Chemical or corrosives : | input data |  | input data
37 | 4.1, 4.2 | Altitude : | 1000 (3300) | m (ft) | 1000 (3300) | m (ft) |  |  |  |  | select | 1000 (3300) | other
38 | 4.1 | Minimum ambient air temperature : | -25 (-13) | °C (°F) | -25 (-13) | °C (°F) |  |  |  |  | select | -25 (-13) | -40 (-40) | other
39 | 4.1 | Maximum ambient air temperature : | 40 (104) | °C (°F) | 40 (104) | °C (°F) |  |  |  |  | select | 40 (104) | 45 (113) | 50 (122) | other
40 |  | Starting performance
41 | 4.1, 4.2 | Motor designs and starting characteristics : | NEMA Design B |  | NEMA Design B | [5 empty] | select | NEMA Design A | NEMA Design B | NEMA Design C
42 |  | Operating performance
43 | 10.4.1 | Rated full load speed : | input data | rpm | input data | rpm
44 | 10.4.1 | Rated full load torque (FLT) : | input data | select | input data | select |  |  |  |  | select | ft·lb | kg·m
45 | 10.4.1 | Rated breakdown torque : | input data | % of FLT | input data | % of FLT
46 | 10.4.1 | Efficiency at 100% rated output : | input data | % | input data | %
47 | 10.4.1 | Efficiency at 75% rated output : | input data | % | input data | %
48 | 10.4.1 | Efficiency at 50% rated output : | input data | % | input data | %
49 | 10.4.1 | Power factor at 100% rated output : | input data | % | input data | %
50 | 10.4.1 | Power factor at 75% rated output : | input data | % | input data | %
51 | 10.4.1 | Power factor at 50% rated output : | input data | % | input data | %
52 |  | Noise
53 | 7.8 | Maximum permissible sound pressure at 1 m (3 ft) (sinewave, no load) : | select | db(A) | select | db(A) |  |  |  |  | select | ≤85 | other
54 | 10.4.1, 7.8 | Motor sound pressure at 1 m (3 ft) (sinewave, no load) : | input data | db(A) | input data | db(A)
55 |  | Machine construction
56 |  | Motor weight : | input data | select | input data | select |  |  |  |  | select | kg | lb
57 | 14.3 | Stainless steel hardware : | not required |  | not required | [5 empty] | select | not required | required
58 | 5.5 | Enclosure type : | TEFC |  | TEFC | [5 empty] | select | TEFC | TENV | explosion proof
59 | 5.5 | Enclosure ingress protection : | IP55 |  | IP55 | [5 empty] | select | IP55 | other
60 |  | Fan
61 | 7.4 | Fan material : | manufacturer's standard (supplier to provide details) |  | manufacturer's standard (supplier to provide details) | [5 empty] | select | manufacturer's standard (supplier to provide details) | conductive plastic | bronze alloy | coated aluminum | other
62 |  | Main terminal box
63 |  | Position : | select |  | select | [5 empty] | select | left (F1) | right (F2) | top (F3) | bottom (C3) | other
64 | 5.5 | Ingress protection of terminal boxes : | IP55 |  | IP55 | [5 empty] | select | IP55 | other
65 | 7.5.1 | Main terminal box cable entry hole size and number : | as per NEMA MG1 Part 4 |  | as per NEMA MG1 Part 4 | [5 empty] | select | as per NEMA MG1 Part 4 | other
66 | 7.5.1, 7.5.2, Table 1 | Oversized terminal box : | not required |  | not required | [5 empty] | select | not required | required
67 | 7.5.1, 7.5.2 | Main terminal box material : | cast iron |  | cast iron | [5 empty] | select | cast iron | cast steel | steel plate
68 |  | Bearings
69 | 7.1 | L10 life : | 50000 | hours | 50000 | hours |  |  |  |  | select | 26280 | 50000 | 100000 | other
70 | 7.1 | Drive end (DE) bearing number : | input data |  | input data
71 | 7.1 | Non-drive end (NDE) bearing number : | input data |  | input data
72 | 7.1 | Recommended lubricant : | select |  | select | [5 empty] | select | grease | oil bath | oil mist
73 | 7.1 | Grease : | input data |  | input data
74 | 7.1 | Oil mist lubricant : | input data |  | input data
75 | 7.1 | Sealed for life anti-friction bearing : | not required |  | not required | [5 empty] | select | not required | required
76 |  | ASD fed motor: non-drive end (NDE) insulation bearing requirement : | required |  | required | [5 empty] | select | not required | required
77 |  | Space heaters
78 | 12 | Space heater : | not required |  | not required | [5 empty] | select | not required | required
79 |  | Space heater terminal box : | not required |  | not required | [5 empty] | select | not required | required
80 | 12 | Space heater voltage : | 120 | V AC | 120 | V AC |  |  |  |  | select | 120 | other
81 | 12 NOTE | Warning label : | select |  | select | [5 empty] | select | not required | required
82 |  | Warning label language : | English |  | English | [5 empty] | select | English | other
83 |  | Mounting
84 |  | Mounting position : | horizontal |  | horizontal | [5 empty] | select | horizontal | vertical
85 |  | Type of mounting : | select |  | select | [5 empty] | select | foot only | flange only | foot and flange
86 |  | Flange type : | select |  | select | [5 empty] | select | C-face | D-flange | P-base | not applicable | other
87 |  | Vertical motor shaft orientation : | select |  | select | [5 empty] | select | shaft up | shaft down
88 |  | Non reverse ratchet : | not required |  | not required | [5 empty] | select | not required | required
89 |  | Drip cover : | select |  | select | [5 empty] | select | not required | required
90 | 7.1 | Vertical motors compliance to API 610, 7.1.9 : | not required |  | not required | [5 empty] | select | not required | required
91 |  | Instrumentation
92 | 14.3 | Provisions for vibration monitoring : | not required |  | not required | [5 empty] | select | not required | required
93 | 14.3 | Winding temperature detectors : | not required |  | not required | [5 empty] | select | not required | required
94 | 14.3 | Bearing temperature detectors : | not required |  | not required | [5 empty] | select | not required | required
95 | 14.3 | Instrumentation terminal box : | not required |  | not required | [5 empty] | select | not required | required
96 |  | Provision for IoT hardware installation : | not required |  | not required | [5 empty] | select | not required | required
97 |  | Motor monitoring device (IoT) : | not required |  | not required | [5 empty] | select | not required | required
98 |  | Surface protection
99 | 10.4.2, 10.4.3 | Atmospheric corrosivity category : | C3 |  | C3 | [5 empty] | select | C3 | C4 | C5 | CX
100 | 10.4.2, 10.4.3, 8.1 | Surface protection durability category : | medium (M) 7 to 15 years |  | medium (M) 7 to 15 years | [5 empty] | select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
101 |  | Motors for hazardous locations
102 | 4.1 | Hazardous area classification : | select |  | select | [5 empty] | select | non-hazardous (unclassified) | Class I Div 1 | Class I Div 2 | Class II Div 1 | Class II Div 2 | Zone 1 | Zone 2 | Zone 21 | Zone 22
103 |  | UL 674 (or equivalent) listing : | not required |  | not required | [5 empty] | select | not required | required
104 |  | Temperature group : | T3 |  | T3 | [5 empty] | select | T3 | other
105 |  | Gas/dust group : | input data |  | input data
106 |  | Testing and inspection
107 | 10.3 | Shop inspection : | not required |  | not required | [5 empty] | select | not required | required
108 | 7.9 | Vibration test : | resilient mount |  | resilient mount | [5 empty] | select | resilient mount | rigid mount
109 | 10.3, 6.4.1, 6.4.2 | Additional test : | not required |  | not required | [5 empty] | select | not required | required
110 |  | Preservation and storage
111 |  | Storage conditions : | input data |  | input data
112 |  | Storage duration : | input data | month (s) | input data | month (s)
113 | 7.1 | Motor nameplate "Oil Mist Lubricated" : | not required |  | not required | [5 empty] | select | not required | required
114 | 7.1 | Motor temporary tag "Oil mist ready, do not run without oil" : | not required |  | not required | [5 empty] | select | not required | required
115 |  | Documentation
116 |  | Motor data sheet : | required |  | required | [5 empty] | select | not required | required
117 | 10.4.1 | Motor performance data : | required |  | required | [5 empty] | select | required | required - electronic
118 | 10.4.1 | Torque and current vs speed curve : | not required |  | not required | [5 empty] | select | not required | required
119 | 10.4.1 | Motor thermal curves : | not required |  | not required | [5 empty] | select | not required | required
120 | 6.1 | Maximum permissible stall time data (at 90% and 100% rated voltage) : | not required |  | not required | [5 empty] | select | not required | required
121 |  | ASD operation curve : | not required |  | not required | [5 empty] | select | not required | required
122 |  | Dimensional outline drawing showing weight, location of terminal boxes, and accessories : | not required |  | not required | [5 empty] | select | not required | required
123 |  | Installation, operation and maintenance manuals : | not required |  | not required | [5 empty] | select | not required | required
124 |  | Motor connection diagram including auxiliaries : | not required |  | not required | [5 empty] | select | not required | required
125 |  | Additional test record : | not required |  | not required | [5 empty] | select | not required | required
126 |  | Certifications : | not required |  | not required | [5 empty] | select | not required | required
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C3: Select 'for enquiry' (purchaser to supplier) or 'for proposal' (supplier to purchaser).
Note on C11: The purchaser may want to specify the motor manufacturer to allow for duplicate or replacement motor orders.
Note on C12: The purchaser may want to specify the model number of the original motor to allow for duplicate or replacement motor orders.
Note on C13: Supplier to indicate motor type. Default value : IEEE Std 841-2021 motor
Note on C14: Select additional certification requirements (beyond NRTL) . If 'other' is selected, specify the required certification in the 'Additional notes' column. Default value : none
Note on C15: Select the starting method of the motor. If 'other' is selected, specify the method of motor starting in the 'Additional notes' column. Default value : direct on line (DOL)
Note on C16: Select the number of poles/motor synchronous speed. Default value : 4 poles/1800 rpm/1500 rpm
Note on C17: Select the direction of motor shaft rotation observed when facing the motor drive end. Default value : bi-directional
Note on C18: Select the method of power transfer to driven equipment. Assists with selection of bearings which may be potentially subjected to higher axial or radial loading.
Note on C19: Purchaser to specify the maximum anticipated radial loading on the shaft end for belt driven loads. Supplier to specify the maximum permissible radial loading if not defined by the purchaser.
Note on C20: Specify the maximum anticipated axial loading (upward or downward thrust) on the shaft end. Supplier to specify the maximum permissible axial loading if not defined by the Purchaser.
Note on C22: Select the motor supply frequency. Default value : 60
Note on C23: Select the motor supply voltage.
Note on C25: Specify the motor frame size. NEMA MG-1, Part 4, Table 4-2 defines the preferred frame sizes for A.C. induction motors. Purchaser to indicate the frame size if this is a replacement motor.
Note on C26: Specify the motor shaft rated mechanical power output at the defined maximum ambient air temperature.
Note on C27: Select the required service factor. IEEE 841 default is a service factor of 1.00. Default value : 1.00
Note on C28: Specify the motor full load current while operating at rated voltage and rated frequency.
Note on C30: Default value : variable torque
Note on C31: Specify the minimum operating speed of the motor.
Note on C32: Specify the maximum operating speed of the motor.
Note on C35: Default value : not applicable
Note on C36: Specify the chemicals or corrosives that are present in the location environment.
Note on C37: Select the altitude above sea-level. IEEE 841 default is 1000 m (3300 ft) or less. Modify 1000 m (3300 ft) value only if the site conditions are higher than the IEEE default (select 'other' and enter value in the 'additional notes' column). Default value : 1000 (3300)
Note on C38: Modify -25 °C value only if the site conditions are lower than the IEEE 841 default. Default value : -25 (-13)
Note on C39: Modify 40 °C value only if the site conditions are higher than the IEEE 841 default. Default value : 40 (104)
Note on C41: Selection of a 'NEMA Design A' or a 'NEMA Design C' nameplated motor are allowable options for an 'IEEE Std 841-2021 Features' motor. Default value : NEMA Design B
Note on C43: Specify the steady-state asynchronous rotor speed while delivering 100% rated power at the rated voltage and frequency. Note: Includes the slip of the motor at full load and at working temperature.
Note on C44: Specify the steady-state asynchronous rotor torque while delivering 100% rated power at the rated voltage and frequency.
Note on C45: Specify the maximum steady-state asynchronous torque which the motor develops without an abrupt drop in speed, when the motor is supplied at the rated voltage and frequency.
Note on C46: Specify the efficiency of the motor while operating at 100% rated power.
Note on C47: Specify the efficiency of the motor while operating at 75% rated power.
Note on C48: Specify the efficiency of the motor while operating at 50% rated power.
Note on C49: Specify the power factor when the motor is operated at 100% rated power.
Note on C50: Specify the power factor when the motor is operated at 75% rated power.​
Note on C51: Specify the power factor when the motor is operated at 50% rated power.​
Note on C53: Specify the motor maximum permissible sound pressure level at 1 m (3 ft) no load, sinewave in dbA. IEEE 841: not to exceed 85 dbA and motors greater than 445 frame not to exceed 92 dbA.
Note on C54: Specify the motor sound pressure level at 1 m (3 ft) no load, sinewave in dbA.
Note on C56: Specify the fully assembled weight of the motor.
Note on C57: If required, specify the grade of stainless steel required in the 'Additional notes' column. Default value : not required
Note on C58: Select the type of motor enclosure that is required. IEEE 841 default is TEFC. Default value : TEFC
Note on C59: Select the enclosure ingress protection. IEEE 841 default is IP55. If 'other' is selected, specify data in the 'Additional notes' column. Default value : IP55
Note on C61: Select the material for the fan. The manufacturer's standard is preferred to optimize cost and delivery. If 'other' is selected, specify in the 'Additional notes' column. Supplier to indicate the type of fan material. Default value : manufacturer's standard (supplier to provide details)
Note on C63: Select the location of the motor line conductor terminal box as viewed from the motor drive end. Refe to NEMA Part 4, MG1, Figure 4-6.
Note on C64: Select the ingress protection method according to ANSI / IEC 60529 for the terminal box(es). If 'other' is selected, specify in the 'additional notes' column. Default value : IP55
Note on C65: NEMA MG1 Part 4, Table 4.4.1 provides conduit entry size per motor frame size. If 'other' is selected, specify the number and size of cable entry holes in main terminal box in the 'Additional notes' column. Default value : as per NEMA MG1 Part 4
Note on C66: Select the requirement for an oversized main terminal box. Specify the size of oversized main terminal box in the 'Additional notes' column. Default value : not required
Note on C67: Default value is cast iron per IEEE 841 requirements, section 7.5. Default value : cast iron
Note on C69: Select bearing operating life requirement. In IEEE 841, 50000 hours is the default bearing operational life (26280 hours for vertical and belted motors). If 'other' is selected, specify value in the 'Additional notes' column. Default value : 50000
Note on C70: Specify the motor drive end bearing number as per ABMA 9 or 11.
Note on C71: Specify the motor non-drive end bearing number as per ABMA 9 or 11.
Note on C72: Select the recommended lubricant for bearings.
Note on C73: Purchaser to provide the grease specification. If not provided by the purchaser, manufacturer to provide proposed grease.
Note on C74: Specify the type and grade of oil used. This is subject to supplier's approval.
Note on C75: Sealed for life anti-friction bearings are generally specified for smaller frame motors defined as motors up to 20 hp. As per IEEE 841 regreaseable open bearings are standard requirement. Sealed for life bearings are allowed as a 'features' motor. Default value : not required
Note on C76: Select the NDE bearing type to be used for ASD fed motor applications to prevent circulating common mode current. Default value : required
Note on C78: Select if a motor space heater is required. Default option is that no space heaters will be provided. Default value : not required
Note on C79: If space heater required, select if a separate terminal box for the space heater power supply is required. Note: This option may not be available on smaller frame sizes. Default value : not required
Note on C80: IEEE 841 standard winding space heater voltage is 120V AC. If 'other' is selected, specify the required voltage in the 'Additional notes' column. Default value : 120
Note on C81: Only applicable if space heater is specified - Select the requirement for a warning label to be provided. Warning label to state that the heater terminals may be energized when the motor is isolated.
Note on C82: If a space heater is required, select the language of the label. If 'other' is selected, specify the language required in the 'Additional notes' column. Default value : English
Note on C84: Select the motor mounting arrangement for the driven equipment. Default value : horizontal
Note on C85: Select the type of mounting for the motor.
Note on C86: Select the flange type. Only applicable if flange is specified for the type of mounting.
Note on C87: Only applicable for vertical motors.
Note on C88: Default value : not required
Note on C90: Only applicable to vertical motors. Select the requirement for compliance of the vertical motor as defined in API 610, 7.1.9 Default value : not required
Note on C92: Select the requirement for a vibration monitoring connection point. If 'other' is selected, provide details in the 'Additional notes' column. Default value : not required
Note on C93: Select the requirement for embedded temperature detection in the stator windings. Provide details (i.e. type and quantity per phase) in the 'Additional notes' column. Default value : not required
Note on C94: Select the requirement for bearing temperature detectors and their type. Provide details (i.e. type/number of wires) in the 'Additional notes' column. Default value : not required
Note on C95: Indicate if a separate terminal box is required for instrumentation. Provide Additional details (i.e. location, size, etc.) in the 'Supplement' tab. Default value : not required
Note on C96: Select the requirement for Internet of Things (IoT) hardware mounting points. Default value : not required
Note on C97: Select the requirement for a motor monitoring device mounted to the motor. Default value : not required
Note on C99: Select the atmospheric corrosivity category in accordance with ISO 12944-2, section 5.1.1. Default value : C3
Note on C100: Select the surface durability category in accordance with ISO 12944-1, section 5.5. The durability range is not a 'guarantee time'. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance program. Default value : medium (M) 7 to 15 years
Note on C102: Select the division or zone for the hazardous area classification. Class I Div 1/Zone 1 will be an explosion proof motor with IEEE 841 'features'. Identify the dust type in dust environment in the 'Additional notes'.
Note on C103: Select UL 674 (or equivalent) listing requirements for motors to be used in hazardous areas. Not for all motors to be used in hazardous areas. Default value : not required
Note on C104: Select the temperature group (T-code). If 'other', specify the temperature group in the 'additional notes' column. T- code groups can be found in standards such as NFPA 70 (NEC) article 500, Table 500.8 or Article 505 for Zone. Default value : T3
Note on C105: Specify the gas/dust group. For gas group, refer to NFPA 497.
Note on C107: Select the requirement for a shop inspection. May be required for a new supplier. Default value : not required
Note on C108: Select the mount for the vibration test. 'Resilient mount' means the motor is mounted on an elastic support. Default value : resilient mount
Note on C109: List any additional required testing. Specify the required tests in the 'Additional notes' column or 'Supplement' tab. Default value : not required
Note on C111: Provide storage conditions (e.g. minimum/maximum ambient, relative humidity, dust, vibration)
Note on C112: Specify the expected storage duration of the motor at site.
Note on C113: Select if 'Oil Mist Lubricated' is required or not required. If required, manufacturer to provide preservation requirements (e.g. grease packing). Default value : not required
Note on C114: Select the requirement for the motor temporary tag identifying 'Oil mist ready, do not run without oil'. If required, manufacturer to provide preservation requirements (e.g. grease packing). Default value : not required
Note on C116: This can be the manufacturer's standard data sheet as long as it includes the information listed on purchaser data sheet. Default value : required
Note on C117: One data pack per type or size of motor, however 'electronic copy' can be specified. Default value : required
Note on C118: One data pack per type or size of motor. Default value : not required
Note on C119: One data pack per type or size of motor. Default value : not required
Note on C120: Data to provide the maximum stall time at 90% and 100% rated voltage, for cold and hot starts. Default value : not required
Note on C121: Only required if ASD is specified. Default value : not required
Note on C122: One data pack per type or size of motor. Default value : not required
Note on C123: One set for standard motors covered by the purchase order. Dedicated IOM may be required for specialty motors. Default value : not required
Note on C124: Default value : not required
Note on C125: If additional testing and inspection are specified, supplier to submit results in the additional test record. Default value : not required
Note on C126: If certification is required, list the required certifications in the 'Additional notes' column. This is to define the required certifications such as USGC, EX, etc. Default value : not required

## Supplement
Row |  | S-733D Procurement Data Sheet for Low Voltage Motors (IEEE Std 841-2021) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
9
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
Public Review Draft

## Guidance
S-733D Procurement Data Sheet for
Low Voltage Motors (IEEE Std 841-2021)
Guidance on the use of this procurement data sheet
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
Public Review Draft
Public Review Draft

## Back Cover
Month XXXX
Public Review Draft