## Front & Preliminaries
|  |  |  | SPECIFICATION | May 2023
|  |  |  | IOGP S-734L | Version 1.1
Information Requirements for
AC Uninterruptible Power Supply (UPS)
System (PIP)
Revision history
| VERSION | DATE | PURPOSE
| 1.1 | May 2023 | Issued for Public Review
| 1 | November 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-734L (1.1) Information Requirements for
AC Uninterruptible Power Supply (UPS) System (PIP)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-734L (1.1) Information Requirements for
AC Uninterruptible Power Supply (UPS) System (PIP)
Introduction
The purpose of this information requirements specification (IRS) is to define information requirements for the procurement of AC uninterruptible power supply (UPS) System in accordance with IOGP S-734 for application in the petroleum and natural gas industries. The IRS defines the information requirements, including format, timing and purpose, for information to be provided by the supplier. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the specification (IOGP S-734), procurement data sheet (IOGP S-734D) and quality requirements specification (IOGP S-734Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Instructions
IOGP S-734L (1.1) Information Requirements for
AC Uninterruptible Power Supply (UPS) System (PIP)
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS Structure Contents
| 1 | 'Front & Preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes / No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information Submission Abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS .
Column K — 'Translation Required' (Yes / No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable Formats
Column F — 'CFIHOS Document Type Code' relates to the CFIHOS document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3 below. Metadata listed below are as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The document master to which this revision is related |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification |  |  | The Export Control Rule that is applicable for the document revision (e.g., ECCN, EAR). |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
| Security classification |  |  | Indicates internal Owner-Operator access restriction applicable for the document |  |  | TBA
Table 3 — Supplier Deliverable Metadata
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Requirements
IOGP S-734L (1.1) Information Requirements for AC Uninterruptible Power Supply (UPS) System (PIP)
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Document Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S734-IR-1 | Supplier master information schedule |  | Information deliverables list | No | For Acceptance |  | - | - |  | -
S734-IR-2 | Delivery schedule |  | Delivery/Production schedule | Yes | For Information |  | - | - |  | -
S734-IR-3 | Progress report |  | Progress report | No | For Information |  | - | - |  | -
S734-IR-4 | Quality plan | Required for CAS A, CAS B | Quality plan | - | - |  | - | - |  |  | CAS A, CAS B - Submit at Proposal (Yes), CAS C, CAS D - Submit at proposal (No). CAS A - For acceptance, CAS B - For information
S734-IR-6 | Inspection and test plan |  | Inspection and test plan (ITP) | No | For Acceptance |  | - | - |  | -
S734-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | - | - |  | -
S734-IR-8 | Non-conformance records |  | Non-conformance records | No | For Acceptance |  | - | - |  | -
S734-IR-61 | Nominated sub-supplier list and scope | Required for CAS A, CAS B | Sub-Supplier list | - | - |  | - | - |  | -
S734-IR-64 | Inspection release notes (authorization to release equipment) |  | Inspection release notes | No | For Acceptance |  | - | - |  | -
S734-IR-74 | Handling, lifting, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | - | - |  | -
Technical Information Deliverables
S734-IR-20 | General arrangement diagram |  | General arrangement diagram | Yes | For Information |  | - | - |  | -
S734-IR-29 | Design data sheet |  | Design data sheet | Yes | For Acceptance |  | - | - |  | -
S734-IR-23 | Manufacturer data sheet |  | Manufacturer data sheet | No | For Acceptance |  | - | - |  | -
S734-IR-24 | Single line diagram |  | Single line diagram | Yes | For Acceptance |  | - | - |  | -
S734-IR-25 | Wiring diagram |  | Wiring diagram | No | For Acceptance |  | - | - |  | -
S734-IR-65 | Schematic diagram |  | Schematic diagram | No | For Acceptance |  | - | - |  | -
S734-IR-60 | Short circuit protection device coordination data |  | Short circuit calculation | No | For Information |  | - | - |  | -
S734-IR-32 | Bill of materials |  | Bill of materials | No | For Information |  | - | - |  | -
S734-IR-66 | Recommended spare part list |  | Spare part list | No | For Information |  | - | - |  | -
S734-IR-34 | Packing list |  | Packing list | No | For Information |  | - | - |  | -
S734-IR-35 | Installation manual |  | Installation manual | No | For Information |  | - | - |  | - | Installation manual index, if required, should be provided in first revision of the document. When index agreed, Installation manual content shall be provided in subsequent revision of the document.
S734-IR-37 | Operating manual |  | Operating manual | No | For Information |  | - | - |  | - | Operating manual index, if required, should be provided in first revision of the document. When index agreed, Operating manual content shall be provided in subsequent revision of the document.
S734-IR-36 | Maintenance manual |  | Maintenance manual | No | For Information |  | - | - |  | - | Maintenance manual index, if required, should be provided in first revision of the document. When index agreed, Maintenance manual content shall be provided in subsequent revision of the document.
S734-IR-67 | Obsolescence management plan |  | Obsolescence management plan | Yes | For Acceptance |  | - | - |  | -
S734-IR-39 | Factory acceptance test (FAT) procedure |  | Factory acceptance test (FAT) procedure | No | For Acceptance |  | - | - |  | -
S734-IR-41 | Factory acceptance test (FAT) records |  | Factory acceptance test (FAT) records | No | For Acceptance |  | - | - |  | -
S734-IR-76 | Type test certificate | Required for CAS A, CAS B, CAS C | General certificate | - |  |  |  | - |  | -
S734-IR-68 | Seismic certification | When seismic certification is required due to site location | Certificate of Conformance | No | For Acceptance |  | - | - |  | -
S734-IR-45 | Nameplates |  | Name plate drawing | No | For Acceptance |  | - | - |  | - | CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Acceptance (before start of manufacturing), CAS D: For Information
S734-IR-46 | Full load heat rejection rate |  | Heat dissipation calculation and loads | Yes | For Information |  | - | - |  | -
S734-IR-55 | Efficiency, reliability and availability | Required for CAS A, CAS B | Reliability, availability, safety integrity level calculation | - | - |  | - | - |  | - | CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance, CAS C: - (N/A), CAS D: - (N/A)
S734-IR-57 | Battery sizing calculation |  | Design calculation | Yes | For Acceptance |  | - | - |  | -
S734-IR-62 | Site acceptance test (SAT) procedure |  | Site acceptance test (SAT) procedure | No | For Acceptance |  | - | - |  | -
S734-IR-63 | Site acceptance test (SAT) records |  | Site acceptance test (SAT) records | No | For Acceptance |  | - | - |  | - | Applicable only if site test (battery capacity test) is included in the order.
S734-IR-69 | Special tools list | Required for CAS A, CAS B, CAS C | Special tools list | - |  |  | - | - |  | -
S734-IR-72 | Battery gas evolution calculations | Battery type dependent and when batteries are supplied by the UPS Supplier. | General calculation | Yes | For Information |  | - | - |  | - | CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
S734-IR-71 | Regulatory compliance certificate |  | Regulatory compliance certificate | No | For Information |  | - | - |  | - | ABS or USCG Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information Submit at proposal: CAS A: Yes, CAS B: Yes, CAS C: Yes, CAS D: No
S734-IR-77 | Certificate of conformance | Required for CAS A, CAS B, CAS C | Certificate of conformance | - | - |  | - | - |  | - | UL1778. Guidance: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: - (N/A)
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Definitions
IOGP S-734L (1.1) Information Requirements for AC Uninterruptible Power Supply (UPS) System (PIP)
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Document Type Code — CFIHOS document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Deliverables
S734-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Supplier] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Supplier] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S734-IR-2 | Delivery schedule | Schedule depicting design, supply, manufacture, inspection, testing and delivery activities to be executed by [supplier]. Schedule details typically** include; a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [supplier's] standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S734-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, internal and outsourced inspection and audit activities. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S734-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [supplier], and when applicable [sub-supplier] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q1/Q2 may be used to inform the development of Service Quality Plans] |  | PDF
S734-IR-6 | Inspection and test plan | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [supplier], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. | 4.22.1 | PDF | CFIHOS-70000180
S734-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000389
S734-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [supplier/sub-supplier] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [supplier] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S734-IR-61 | Nominated sub-supplier list and scope | Definition of products, services or processes, that will be externally provided and the controls to be applied by the supplier to ensure conformance with agreed requirements. |  | Native
S734-IR-64 | Inspection release notes (authorization to release equipment) | Supplier release notes are to be issued by the buyer, which the supplier is to endorse together with the buyer's representative. In some circumstances the buyer may decide to waive final inspection, in which case the buyer is to complete a Release Note, which is to be endorsed 'Inspection waived' at the buyer's office. | 4.20.1 | PDF
S734-IR-74 | Handling, lifting, shipping, storage and preservation procedure | Definition of practices to be followed during the storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container(s), b. special packing/unpacking/handling and lifting requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning, e. drawings shall be provided indicating size of shipping splits, center of gravity, weight, identification, and packing list of contents. NOTE: Copies of applicable lifting procedures are included in the delivery documentation which accompanies shipments of equipment. | 4.21.1, 4.21.10, 4.21.2, 4.21.4, 4.21.5 | PDF | CFIHOS-70000154
Technical Information Deliverables
S734-IR-20 | General arrangement diagram | The drawing(s) will contain the following information: • Overall dimensions, critical interface dimensions • Equipment / components with cross sectional views • Location of ventilation openings • Terminal blocks for field connections • Weights of assemblies, equipment and components • Location of cabinet grounds • Center of gravity • Withdrawal/installation and maintenance space • Installation, anchoring and mounting details (including removal cable gland plates) • Lifting arrangement | 4.10.1, 4.21.7, 4.22.1, 4.22.2 | PDF | CFIHOS-70000153
S734-IR-29 | Design data sheet | IOGP S-734D provides technical information about the UPS equipment, including supplier information. | 4.1.20, 4.1.6, 4.1.7, 4.10.5, 4.13.3, 4.15.1, 4.18.7.2, 4.22.1, 4.3, 4.6.1, Table 1 Section D | Native | CFIHOS-70000117
S734-IR-23 | Manufacturer data sheet | Documentation providing technical data and characteristics about material, products or systems and their environment for proper implementation. These documents provide a structured data form containing part number/model, design information, I/O data address mapping, operational data and limitations of the equipment relating to meeting the performance criteria of IOGP S-734, PIP ELSAP04 and IOGP S-734D. | 4.22.1, 4.3, Table 1 Section D | PDF | CFIHOS-70000416
S734-IR-24 | Single line diagram | A diagram depicting the main equipment items and current ratings (e.g. rectifiers, charger, batteries, transformers, protection and isolation devices). | 4.10.1, 4.15.1, 4.22.1, 4.22.2 | PDF | CFIHOS-70000371
S734-IR-25 | Wiring diagram | Diagram providing information on the circuitry, including the following: — Graphical symbols representing the objects — Graphical symbols representing the connections among objects — Reference designations — Terminal designations — Signal level conventions (applicable to logic signals) — Information necessary to trace paths and circuits (signal designations, location references) — Supplementary information necessary for the understanding of functions — Customer connections to be clearly identified (e.g. communications and power interconnections) — Cable and cable core identification. — maximum cross section area and number of runs of power cables; | 4.1.25, 4.10.1, 4.17.4, 4.22.1, 4.22.2 | PDF | CFIHOS-70000268
S734-IR-65 | Schematic diagram | A pictorial representation of the main elements and functions of a control circuit for electrical equipment with input/output sources (switches, relays etc.) and their relationships. Details logic functions of the circuit. | 4.1.10, 4.1.13, 4.1.14, 4.22.1, 4.22.2 | PDF | CFIHOS-70000328
S734-IR-60 | Short circuit protection device coordination data | Short circuit protection device coordination data for purchaser power system studies. Necessary to determine the capacity of electrical equipment under fault conditions. Typically input and output circuit breakers and fuses. | 4.1.24, 4.22.1, Table 1 Section D | PDF | CFIHOS-70000369
S734-IR-32 | Bill of materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and references to material specifications. | 4.1.25, 4.13.3, 4.16.3, 4.17.1, 4.22.1, 4.22.2 | PDF | CFIHOS-70000028
S734-IR-66 | Recommended spare part list | Table containing list items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for later use. Mandatory content of information: – Item reference number; – Quantity; – Part number or global identifier (together with manufacturer / supplier); – Part name. Optional content of information: – Type designation; – Specifying technical data; – Descriptive technical data; – Mass, dimensions; – Reference to document; – Remark. | 4.22.1 | PDF | CFIHOS-70000374
S734-IR-34 | Packing list | A detailed list of the equipment being packaged and shipped. | 4.21.11, 4.21.12, 4.21.6, 4.22.1 | PDF | CFIHOS-70000269
S734-IR-35 | Installation manual | Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a standalone document. | 4.1.25, 4.10.1, 4.13.3, 4.21.7, 4.22.1 | PDF | CFIHOS-70000181
S734-IR-37 | Operating manual | Description of equipment operation including instructions, procedures, drawings, tables, etc. for the operation, startup, switching and isolation. | 4.10.1, 4.19.8, 4.22.1, 4.6.1 | PDF | CFIHOS-70000228
Supplier to include in the operating manual (or hand over to purchaser) any system configured/protected password needed for the maintenance and operation (e.g. battery float and equalize voltages, temperature alarms and battery charge duration) of the equipment. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a standalone document.
S734-IR-36 | Maintenance manual | Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package supplier. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a standalone document. | 4.10.1, 4.16.3, 4.17.1, 4.22.1 | PDF | CFIHOS-70000206
S734-IR-67 | Obsolescence management plan | The supplier to submit an obsolescence management plan in accordance with IEC 62402. The plan will provide milestone dates such as end of production (EOP) and also predicted end of supply. 1. Plan to present relevant obsolescence activities, and strategies to minimise obsolescence during design. 2. Contents. - Authorities and resources responsible for developing, reviewing and maintaining the plan. - Scope: >items being considered. >length of each items lifecycle >the organisations obsolescence management policy >the customer or end user requirements. 3. Objectives e.g. data acquisition, strategies to minimise, monitoring | 4.1.4.1, 4.1.4.3, 4.22.1, Table 3 | PDF
S734-IR-39 | Factory acceptance test (FAT) procedure | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document shall include all testing activities and their acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Test set-up and test equipment shall be defined. Suppliers standard (routine) test procedures should be used as far as possible | 4.1.24, 4.1.8, 4.10.1, 4.16.3, 4.17.1, 4.20.1, 4.20.2, 4.22.1 | PDF | CFIHOS-70000427
S734-IR-41 | Factory acceptance test (FAT) records | The FAT report will be used for acceptance of the equipment being supplied. This document includes all testing activities, test results, corresponding analysis and outcome. This includes S-734Q: routine testing (4.20.1.1), and additional testing (4.20.1.2). | 4.20.10, 4.10.5, 4.20.1, 4.20.11, 4.20.12, 4.20.2, 4.20.9, 4.22.1 | PDF | CFIHOS-70000429
S734-IR-76 | Type test certificate | A document providing objective evidence that the equipment is compliant to the Type testing requirements identified in IEC 62040-3, Table 5. | 4.20.1, 4.20.2, 4.20.3 | - | CFIHOS-70000239
S734-IR-68 | Seismic certification | Document providing equipment certification by third party for seismic design. | 4.2.6, 4.22.1 | PDF | CFIHOS-70000013
S734-IR-45 | Nameplates | Graphic and equipment information posted on the UPS that depicts layout and procedures required as referenced to PIP ELSAP04 (4.19 Tagging and Nameplates). | 4.19.1, 4.19.2, 4.19.3.1, 4.19.3.2, 4.19.3.3, 4.19.3.5, 4.19.3.6, 4.19.3.7, 4.19.3.8, 4.19.4, 4.19.6, 4.19.7, 4.22.1, 4.22.2 | PDF
S734-IR-46 | Full load heat rejection rate | This document contains the calculation by the manufacturer to arrive at the heat load produced by the equipment, which is typically used for HVAC sizing. | 4.22.1 | PDF
S734-IR-55 | Efficiency, reliability and availability | Demonstrates operating reliability and availability of purchased equipment (e.g. mean time between failure data) and UPS system overall efficiency. | 4.1.4.1, 4.1.4.2, 4.22.1 | PDF | CFIHOS-70000312
S734-IR-57 | Battery sizing calculation | Document providing information about data, and basic conditions and assumptions used for selection and sizing of appropriate batteries. | 4.22.1 | PDF | CFIHOS-70000086
S734-IR-62 | Site acceptance test (SAT) procedure | Procedure documenting the manufacturers recommended site tests including battery capacity test, discrete functional unit and overall system, interlocks (electrical, mechanical), interfaces, protection and communications. | 4.20.1, 4.20.2 | PDF | CFIHOS-70000428
S734-IR-63 | Site acceptance test (SAT) records | Records demonstrating results of site tests including battery capacity test, discrete functional unit and overall system, interlocks (electrical, mechanical), interfaces, protection and communications. | 4.20.1, 4.20.2 | PDF | CFIHOS-70000430
S734-IR-69 | Special tools list | The special tools list shall identify all special tools necessary for handling, dismantling, maintenance etc. of equipment. Shall be part of the Spare part list Special Tools List shall include: • Identification - the tag number the special tool shall support • Description of the special tool • Storage, i.e. the location where the special tool can be found • Document references, if applicable Note that the actual special tool shall be marked with the identification, i.e. tag number that it supports. | 4.22.1 | PDF
S734-IR-72 | Battery gas evolution calculations | A document Supplier to provide a copy of the calculations used determine the gas evolution from the battery bank. | 4.22.1 | PDF | CFIHOS-70000238
S734-IR-71 | Regulatory compliance certificate | A document certifying conformity to local regulations which accompanies shipment of equipment and/or goods. e.g., Official certificate issued by manufacturer. This would include USCG, ABS, or DNV type certifications or similar designations. | 4.1.26, 4.22.1 | PDF | CFIHOS-70000079
S734-IR-77 | Certificate of conformance | A statement of conformity where attestation is performed by the person or body that is independent of the person or organization that provides the object, and of user interests in that object (third party). (Source: ISO 17000, clause 5.6). This includes UL certification. | 4.1.3 | PDF | CFIHOS-70000013
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Back Cover
Public Review Draft

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: