## Addendum 2
Date of issue:
February 2024
Affected publication:
IOGP S-718D, Specification for Basic Process Measurement Instruments, First Edition, September 2022, including Addendum 1, December 2023
ADDENDUM 2 FOR PUBLIC REVIEW
This addendum will replace Edition 1.0 published in September 2022 and Addendum 1 published in December 2023.
While this addendum primarily adds requirements and data sheet elements for additional level instruments, due to the extent of updates, it should be treated as a new document.
Public Review Draft

## Front & Preliminaries
|  |  |  | SPECIFICATION | February 2024
|  |  |  | IOGP S-718D | Version 1.011
ADDENDUM 2 TO FIRST EDITION (SEPTEMBER 2022)
Procurement Data Sheets for
Basic Process Measurement Instruments
Revision history
| VERSION | DATE | PURPOSE
| 1.011 | February 2024 | Addendum 2 for Public Review
| 1.01 | December 2023 | Addendum 1
| 1.0 | September 2022 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-718D (1.011) Procurement Data Sheets for
Basic Process Measurement Instruments
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-718D (1.011) Procurement Data Sheets for
Basic Process Measurement Instruments
Introduction
The purpose of these procurement data sheets is to define purchaser specific requirements for the procurement of basic process measurement instruments in accordance with IOGP S-718 for application in the petroleum and natural gas industries. The procurement data sheets provide project specific requirements where the specification requires the purchaser to define an application specific requirement. They also include information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheets to define scope and technical requirements for enquiry and purchase of the equipment.
These procurement data sheets shall be used in conjunction with the specification (IOGP S-718), information requirements specification (IOGP S-718L) and quality requirements specification (IOGP S-718Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS PressGauge
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Pressure Gauge | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
19 |  | Installation conditions
20 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
21 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
22 |  | Process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
23 |  | Process connection material type : | input data |  | input data
24 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
25 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
26 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
27 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
28 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
29 | 7.2.1.3 | Insulation thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
30 |  | Operating conditions
31 |  | Process fluid(s) : | input data |  | input data
32 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
33 |  | Service description : | input data |  | input data
34 |  | Process fluid corrosive compounds : | input data |  | input data
35 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
36 |  | Process fluid plugging : | no |  | no | [5 empty] | select | yes | no
37 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
38 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
39 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
40 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
41 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
42 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
43 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
44 |  | Body/element/sensor
45 |  | Element type : | bourdon |  | bourdon | [5 empty] | select | bourdon | diaphragm | bellows | capsule | piezoresistive | other
46 |  | Gauge dial size : | select |  | select | [5 empty] | select | 63 mm (2,5 in) | 80 mm (3 in) | 100 mm (4 in) | 113 mm (4,5 in) | 130 mm (5 in) | 150 mm (6 in)
47 |  | Gauge range - minimum : | input data | select | input data | select |  |  |  |  | select | bar | kPa | Mpa | psi | inH2O
48 |  | Gauge range - minimum : | input data | select | input data | select |  |  |  |  | select | ºC | ºF
49 |  | Gauge range - maximum : | input data | select | input data | select |  |  |  |  | select | bar | kPa | Mpa | psi | inH2O
50 |  | Gauge range - maximum : | input data | select | input data | select |  |  |  |  | select | ºC | ºF
51 | 5.4.8 | Case type : | select |  | select | [5 empty] | select | S3 | blowout back and baffle wall and safety glass | other
52 |  | Case mounting style : | standalone |  | standalone | [5 empty] | select | standalone | panel mount | surface mount
53 |  | Case material : | 316 stainless steel |  | 316 stainless steel | [5 empty] | select | 316 stainless steel | polymer | other
54 |  | Connection orientation : | bottom |  | bottom | [5 empty] | select | bottom | rear | 2 o'clock (side) | 9 o'clock (side) | 3 o'clock (side)
55 |  | Ring style : | bayonet ring |  | bayonet ring | [5 empty] | select | bayonet ring | crimp ring | profile ring | standoff ring | friction ring
56 |  | Ring material : | 316 stainless steel |  | 316 stainless steel | [5 empty] | select | 316 stainless steel | other
57 |  | Window material : | safety glass |  | safety glass | [5 empty] | select | ​​​​​​​safety glass | plastic
58 |  | Wetted parts material : | 316 stainless steel |  | 316 stainless steel | [5 empty] | select | 316 stainless steel | monel | hastelloy 276 | other
59 | 5.4.4 | Case liquid fill material : | glycerin |  | glycerin | [5 empty] | select | glycerin | silicone oil | none
60 |  | Pointer colour : | black |  | black | [5 empty] | select | black | other
61 |  | Dial colour : | select |  | select | [5 empty] | select | white
62 |  | Markings colour : | black |  | black | [5 empty] | select | black | other
63 |  | Pointer zero adjustment : | external |  | external | [5 empty] | select | external | other
64 |  | Pointer stop pin : | yes |  | yes | [5 empty] | select | yes | no
65 |  | Vacuum protection : | select |  | select | [5 empty] | select | yes | no
66 |  | Over pressure protection : | no |  | no | [5 empty] | select | yes | no
67 |  | Siphon requirement : | select |  | select | [5 empty] | select | no | trumpet | u-form | compact
68 |  | Transmitter
69 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
70 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
71 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
72 |  | Protocol version : | input data |  | input data
73 |  | Performance
74 |  | Nominal accuracy grade : | select |  | select | [5 empty] | select | Grade 2A (ASME B40.100) | Class 1 (EN 837-1)
75 |  | Diaphragm seal (option)
76 |  | Diaphragm seal type : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other | not applicable
77 | 5.2.5 | Diaphragm seal configuration : | select |  | select | [5 empty] | select | close coupled (single connection) | remote seal (single connection) | balanced system (both capillaries equal length) | unbalanced system (low side capillary - high side direct connected) | unbalanced system (high side seal - low side open to atmosphere) | not applicable
78 |  | Diaphragm seal - sealing material : | select |  | select | [5 empty] | select | graphite | FPM | PTFE | other
79 | 5.2.1, 5.2.2 | Diaphragm seal capillary / armour material : | input data |  | input data
80 |  | Diaphragm seal capillary length : | input data | select | input data | select |  |  |  |  | select | mm | in | m | ft
81 | 5.2.2, 5.2.4, 5.2.5 | Diaphragm seal capillary fill fluid : | input data |  | input data
82 |  | Diaphragm seal upper housing material : | input data |  | input data
83 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.5 | Diaphragm seal lower housing material : | input data |  | input data
84 | 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
85 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | none | gold
86 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | micro-inches | nano-metres
87 |  | Diaphragm seal flushing connection : | select |  | select | [5 empty] | select | one 1/4-18 NPT(F) | two 1/4-18 NPT(F) | one 1/2 -14 NPT(F) | two 1/2-14 NPT(F)
88 |  | Diaphragm seal process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in | not applicable
89 |  | Diaphragm seal process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
90 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
91 |  | Manifold (option)
92 |  | Manifold manufacturer : | input data |  | input data
93 |  | Manifold model number : | input data |  | input data
94 |  | Manifold type : | select |  | select | [5 empty] | select | 2-valve | 5-valve | not applicable
95 |  | Manifold assembly orientation : | select |  | select | [5 empty] | select | bottom | side
96 |  | Manifold material : | input data |  | input data
97 |  | Manifold packing material : | input data |  | input data
98 |  | Manifold assembly process connection size : | select |  | select | [5 empty] | select | 12 mm | ½ in | 2 in
99 |  | Manifold assembly process connection type : | select |  | select | [5 empty] | select | NPT(F) | RF | RTJ | FF
100 |  | Manifold assembly process connection rating : | select |  | select | [5 empty] | select | 3 000 psi | 6 000 psi | 10 000 psi
101 |  | Manifold assembly vent/drain connection size : | select |  | select | [5 empty] | select | 6 mm | 12 mm | ½ in | ¼ in
102 |  | Manifold assembly vent/drain connection type : | select |  | select | [5 empty] | select | NPT(F) | other
103 |  | Manifold assembly vent/drain connection rating : | select |  | select | [5 empty] | select | 3 000 psi | 6 000 psi | 10 000 psi
104 |  | Manifold valves lockable : | select |  | select | [5 empty] | select | yes | no
105 |  | Accessories
106 |  | Pressure limit valve : | no |  | no | [5 empty] | select | yes | no
107 |  | Restrictor : | no |  | no | [5 empty] | select | yes | no
108 |  | Snubber : | no |  | no | [5 empty] | select | yes | no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the ingress protection rating in IP or NEMA.
Note on C20: Specify the size of the connection to the process.
Note on C21: Select the pressure rating of the system connected.
Note on C22: Select the type of the connection to the process.
Note on C23: Specify the material of the process flange.
Note on C24: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C25: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C26: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C27: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C28: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C29: Specify the insulation material thickness of the process pipe, vessel or equipment where the thermowell or orifice plate is connected.
Note on C31: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C32: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C33: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C34: Specify any corrosive elements in the process stream.
Note on C35: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C36: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C37: Specify the temperature of the process at the minimum sizing case.
Note on C38: Specify the differential pressure of the process at the minimum sizing case.
Note on C39: Specify the temperature of the process at the minimum sizing case.
Note on C40: Specify the pressure of the process for the normal operating case.
Note on C41: Specify the temperature of the process at the maximum sizing case.
Note on C42: Specify the pressure of the process for the maximum operating case.
Note on C43: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C45: Select the type of pressure sensing element in contact with the process fluid. Default value : bourdon
Note on C46: Select the required diameter of gauge required for the application.
Note on C47: Specify the minimum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating pressure to be within 50 % to 70 % of the scale.
Note on C48: Specify the minimum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating temperature to be within 50 % to 70 % of the scale.
Note on C49: Specify the maximum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating pressure to be within 50 % to 70 % of the scale.
Note on C50: Specify the maximum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating temperature to be within 50 % to 70 % of the scale.
Note on C51: Select the safety protection elements.
Note on C52: Select the design of case to be supplied. Default value : standalone
Note on C53: Specify the case material from which the case is to be manufactured. Default value : 316 stainless steel
Note on C54: Select the process connection position in relation to the pressure gauge. Default value : bottom
Note on C55: Select the type of ring style. Default value : bayonet ring
Note on C56: Specify the ring material from which the ring is to be manufactured. Default value : 316 stainless steel
Note on C57: Select the material to be supplied for the gauge window. Default value : safety glass
Note on C58: Select the material for items in contact with the process medium (e.g. stem). Default value : 316 stainless steel
Note on C59: Select the liquid fill material to reduce vibration, if required. Default value : glycerin
Note on C60: Select the required colour of the pointer. Default value : black
Note on C61: Select the required colour of the dial.
Note on C62: Select what colour the markings are to be on the dial. Default value : black
Note on C63: Select whether the pointer requires the function to adjust the zero setting externally. Default value : external
Note on C64: Select whether the pointer stop pin is required. Default value : yes
Note on C65: Select whether the pressure gauge is to be exposed to a vacuum.
Note on C66: Select whether the offered instrument needs to be designed for over pressure past the design conditions. Default value : no
Note on C67: Select the siphon to be added if process conditions dictate.
Note on C69: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C70: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C71: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C72: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C74: Select the required performance levels for the instrument.
Note on C76: Select the length that the seal is to protrude to inside the nozzle or flush if no extension is required.
Note on C77: Select the type of diaphragm seal configuration to be selected for chosen application.
Note on C78: Select the material of seal between the diaphragm and the process connection.
Note on C79: Specify the material suitable for the ambient conditions and fill fluid. Select "not applicable" when it is direct mount.
Note on C80: Specify the length. For a balanced system, the length is to be for both capillaries. For an unbalanced system, refer to the "instrumentation type" data sheet field to determine whether it is high or low pressure leg.
Note on C81: Specify the fill fluid. Silicon or glycerin are standard, subject to the operating temperature of the process. Ensure that it complies with API RP 551, 9.3.1.
Note on C82: Specify the upper housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C83: Specify the lower housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C84: Select the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C85: Select the option for gold plating if required for hydrogen service.
Note on C86: Specify the calculated thickness (to be supported by calculations).
Note on C87: Select the size of threaded connection when the flushing function is required.
Note on C88: Select the size for the flanged connection.
Note on C89: Select the flange finish.
Note on C90: Select the diaphragm flange rating in line with the installed rating and as per the piping specification.
Note on C92: Specify the manifold make.
Note on C93: Specify the full model number of the manifold being supplied.
Note on C94: Select the manifold type. "2-valve" is normally specified for pressure transmitter applications and "5-valve" for differential pressure. Select "not applicable" if a diaphragm seal is selected.
Note on C95: Select either bottom entry or side entry for connection to transmitter.
Note on C96: Specify the manifold material, normally 316L stainless steel minimum to meet process requirements.
Note on C97: Specify the material used in packing material.
Note on C98: Select the connection size at the boundary point of supplier interface to the process.
Note on C99: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C100: Select the pressure rating of flanged connection.
Note on C101: Select the connection size at the boundary point of suppliers interface to the process.
Note on C102: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C103: Select the pressure rating of vent/drain connection.
Note on C104: Select whether for the manifold the capability to lock the valves in the position is required.
Note on C106: Select whether the pressure limit valve is required. If "yes" is selected, provide further details including materials in the "Supplement" tab. Default value : no
Note on C107: Select whether the restrictor is required. If "yes" selected, provide further details including restriction size in the "Supplement" tab. Default value : no
Note on C108: Select based on process conditions whether the snubber is required. If "yes" selected, specify model number, materials and design in the "Supplement" tab. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS PressDiffGauge
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Pressure Differential Gauge | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
19 |  | Installation conditions
20 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
21 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
22 |  | Process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
23 |  | Process connection material type : | input data |  | input data
24 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
25 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
26 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
27 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
28 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
29 | 7.2.1.3 | Insulation thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
30 |  | Operating conditions
31 |  | Process fluid(s) : | input data |  | input data
32 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
33 |  | Service description : | input data |  | input data
34 |  | Process fluid corrosive compounds : | input data |  | input data
35 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
36 |  | Process fluid plugging : | no |  | no | [5 empty] | select | yes | no
37 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
38 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa
39 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
40 |  | Normal operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa
41 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
42 |  | Maximum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa
43 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
44 |  | Body/element/sensor
45 |  | Element type : | bourdon |  | bourdon | [5 empty] | select | bourdon | diaphragm | bellows | capsule | piezoresistive | other
46 |  | Gauge dial size : | select |  | select | [5 empty] | select | 63 mm (2,5 in) | 80 mm (3 in) | 100 mm (4 in) | 113 mm (4,5 in) | 130 mm (5 in) | 150 mm (6 in)
47 |  | Gauge range - minimum : | input data | select | input data | select |  |  |  |  | select | bar | kPa | Mpa | psi | inH2O
48 |  | Gauge range - minimum : | input data | select | input data | select |  |  |  |  | select | ºC | ºF
49 |  | Gauge range - maximum : | input data | select | input data | select |  |  |  |  | select | bar | kPa | Mpa | psi | inH2O
50 |  | Gauge range - maximum : | input data | select | input data | select |  |  |  |  | select | ºC | ºF
51 | 5.4.8 | Case type : | select |  | select | [5 empty] | select | S3 | blowout back and baffle wall and safety glass | other
52 |  | Case mounting style : | standalone |  | standalone | [5 empty] | select | standalone | panel mount | surface mount
53 |  | Case material : | 316 stainless steel |  | 316 stainless steel | [5 empty] | select | 316 stainless steel | polymer | other
54 |  | Connection orientation : | bottom |  | bottom | [5 empty] | select | bottom | rear | 2 o'clock (side) | 9 o'clock (side) | 3 o'clock (side)
55 |  | Ring style : | bayonet ring |  | bayonet ring | [5 empty] | select | bayonet ring | crimp ring | profile ring | standoff ring | friction ring
56 |  | Ring material : | 316 stainless steel |  | 316 stainless steel | [5 empty] | select | 316 stainless steel | other
57 |  | Window material : | safety glass |  | safety glass | [5 empty] | select | ​​​​​​​safety glass | plastic
58 |  | Wetted parts material : | 316 stainless steel |  | 316 stainless steel | [5 empty] | select | 316 stainless steel | monel | hastelloy 276 | other
59 | 5.4.4 | Case liquid fill material : | glycerin |  | glycerin | [5 empty] | select | glycerin | silicone oil | none
60 |  | Pointer colour : | black |  | black | [5 empty] | select | black | other
61 |  | Dial colour : | select |  | select | [5 empty] | select | white
62 |  | Markings colour : | black |  | black | [5 empty] | select | black | other
63 |  | Pointer zero adjustment : | external |  | external | [5 empty] | select | external | other
64 |  | Pointer stop pin : | yes |  | yes | [5 empty] | select | yes | no
65 |  | Vacuum protection : | select |  | select | [5 empty] | select | yes | no
66 |  | Over pressure protection : | no |  | no | [5 empty] | select | yes | no
67 |  | Siphon requirement : | select |  | select | [5 empty] | select | no | trumpet | u-form | compact
68 |  | Transmitter
69 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
70 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
71 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
72 |  | Protocol version : | input data |  | input data
73 |  | Performance
74 |  | Influence of static pressure : | input data | % | input data | %
75 |  | Nominal accuracy grade : | select |  | select | [5 empty] | select | Grade 2A (ASME B40.100) | Class 1 (EN 837-1)
76 |  | Diaphragm seal (option)
77 |  | Diaphragm seal type : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other | not applicable
78 | 5.2.5 | Diaphragm seal configuration : | select |  | select | [5 empty] | select | close coupled (single connection) | remote seal (single connection) | balanced system (both capillaries equal length) | unbalanced system (low side capillary - high side direct connected) | unbalanced system (high side seal - low side open to atmosphere) | not applicable
79 |  | Diaphragm seal - sealing material : | select |  | select | [5 empty] | select | graphite | FPM | PTFE | other
80 | 5.2.1, 5.2.2 | Diaphragm seal capillary / armour material : | input data |  | input data
81 |  | Diaphragm seal capillary length : | input data | select | input data | select |  |  |  |  | select | mm | in | m | ft
82 | 5.2.2, 5.2.4, 5.2.5 | Diaphragm seal capillary fill fluid : | input data |  | input data
83 |  | Diaphragm seal upper housing material : | input data |  | input data
84 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.5 | Diaphragm seal lower housing material : | input data |  | input data
85 | 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
86 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | none | gold
87 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | micro-inches | nano-metres
88 |  | Diaphragm seal flushing connection : | select |  | select | [5 empty] | select | one 1/4-18 NPT(F) | two 1/4-18 NPT(F) | one 1/2 -14 NPT(F) | two 1/2-14 NPT(F)
89 |  | Diaphragm seal process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in | not applicable
90 |  | Diaphragm seal process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
91 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
92 |  | Manifold (option)
93 |  | Manifold manufacturer : | input data |  | input data
94 |  | Manifold model number : | input data |  | input data
95 |  | Manifold type : | select |  | select | [5 empty] | select | 2-valve | 5-valve | not applicable
96 |  | Manifold assembly orientation : | select |  | select | [5 empty] | select | bottom | side
97 |  | Manifold material : | input data |  | input data
98 |  | Manifold packing material : | input data |  | input data
99 |  | Manifold assembly process connection size : | select |  | select | [5 empty] | select | 12 mm | ½ in | 2 in
100 |  | Manifold assembly process connection type : | select |  | select | [5 empty] | select | NPT(F) | RF | RTJ | FF
101 |  | Manifold assembly process connection rating : | select |  | select | [5 empty] | select | 3 000 psi | 6 000 psi | 10 000 psi
102 |  | Manifold assembly vent/drain connection size : | select |  | select | [5 empty] | select | 6 mm | 12 mm | ½ in | ¼ in
103 |  | Manifold assembly vent/drain connection type : | select |  | select | [5 empty] | select | NPT(F) | other
104 |  | Manifold assembly vent/drain connection rating : | select |  | select | [5 empty] | select | 3 000 psi | 6 000 psi | 10 000 psi
105 |  | Manifold valves lockable : | select |  | select | [5 empty] | select | yes | no
106 |  | Accessories
107 |  | Pressure limit valve : | no |  | no | [5 empty] | select | yes | no
108 |  | Restrictor : | no |  | no | [5 empty] | select | yes | no
109 |  | Snubber : | no |  | no | [5 empty] | select | yes | no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the ingress protection rating in IP or NEMA.
Note on C20: Specify the size of the connection to the process.
Note on C21: Select the pressure rating of the system connected.
Note on C22: Select the type of the connection to the process.
Note on C23: Specify the material of the process flange.
Note on C24: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C25: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C26: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C27: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C28: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C29: Specify the insulation material thickness of the process pipe, vessel or equipment where the thermowell or orifice plate is connected.
Note on C31: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C32: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C33: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C34: Specify any corrosive elements in the process stream.
Note on C35: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C36: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C37: Specify the temperature of the process at the minimum sizing case.
Note on C38: Specify the differential pressure of the process at the minimum sizing case.
Note on C39: Specify the temperature of the process at the minimum sizing case.
Note on C40: Specify the differential pressure of the process at the normal sizing case.
Note on C41: Specify the temperature of the process at the maximum sizing case.
Note on C42: Specify the differential pressure of the process at the maximum sizing case.
Note on C43: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C45: Select the type of pressure sensing element in contact with the process fluid. Default value : bourdon
Note on C46: Select the required diameter of gauge required for the application.
Note on C47: Specify the minimum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating pressure to be within 50 % to 70 % of the scale.
Note on C48: Specify the minimum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating temperature to be within 50 % to 70 % of the scale.
Note on C49: Specify the maximum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating pressure to be within 50 % to 70 % of the scale.
Note on C50: Specify the maximum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating temperature to be within 50 % to 70 % of the scale.
Note on C51: Select the safety protection elements.
Note on C52: Select the design of case to be supplied. Default value : standalone
Note on C53: Specify the case material from which the case is to be manufactured. Default value : 316 stainless steel
Note on C54: Select the process connection position in relation to the pressure gauge. Default value : bottom
Note on C55: Select the type of ring style. Default value : bayonet ring
Note on C56: Specify the ring material from which the ring is to be manufactured. Default value : 316 stainless steel
Note on C57: Select the material to be supplied for the gauge window. Default value : safety glass
Note on C58: Select the material for items in contact with the process medium (e.g. stem). Default value : 316 stainless steel
Note on C59: Select the liquid fill material to reduce vibration, if required. Default value : glycerin
Note on C60: Select the required colour of the pointer. Default value : black
Note on C61: Select the required colour of the dial.
Note on C62: Select what colour the markings are to be on the dial. Default value : black
Note on C63: Select whether the pointer requires the function to adjust the zero setting externally. Default value : external
Note on C64: Select whether the pointer stop pin is required. Default value : yes
Note on C65: Select whether the pressure gauge is to be exposed to a vacuum.
Note on C66: Select whether the offered instrument needs to be designed for over pressure past the design conditions. Default value : no
Note on C67: Select the siphon to be added if process conditions dictate.
Note on C69: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C70: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C71: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C72: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C74: Specify the test results in accordance with IEC 62828-2, 6.2.4.
Note on C75: Select the required performance levels for the instrument.
Note on C77: Select the length that the seal is to protrude to inside the nozzle or flush if no extension is required.
Note on C78: Select the type of diaphragm seal configuration to be selected for chosen application.
Note on C79: Select the material of seal between the diaphragm and the process connection.
Note on C80: Specify the material suitable for the ambient conditions and fill fluid. Select "not applicable" when it is direct mount.
Note on C81: Specify the length. For a balanced system, the length is to be for both capillaries. For an unbalanced system, refer to the "instrumentation type" data sheet field to determine whether it is high or low pressure leg.
Note on C82: Specify the fill fluid. Silicon or glycerin are standard, subject to the operating temperature of the process. Ensure that it complies with API RP 551, 9.3.1.
Note on C83: Specify the upper housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C84: Specify the lower housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C85: Select the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C86: Select the option for gold plating if required for hydrogen service.
Note on C87: Specify the calculated thickness (to be supported by calculations).
Note on C88: Select the size of threaded connection when the flushing function is required.
Note on C89: Select the size for the flanged connection.
Note on C90: Select the flange finish.
Note on C91: Select the diaphragm flange rating in line with the installed rating and as per the piping specification.
Note on C93: Specify the manifold make.
Note on C94: Specify the full model number of the manifold being supplied.
Note on C95: Select the manifold type. "2-valve" is normally specified for pressure transmitter applications and "5-valve" for differential pressure. Select "not applicable" if a diaphragm seal is selected.
Note on C96: Select either bottom entry or side entry for connection to transmitter.
Note on C97: Specify the manifold material, normally 316L stainless steel minimum to meet process requirements.
Note on C98: Specify the material used in packing material.
Note on C99: Select the connection size at the boundary point of supplier interface to the process.
Note on C100: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C101: Select the pressure rating of flanged connection.
Note on C102: Select the connection size at the boundary point of suppliers interface to the process.
Note on C103: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C104: Select the pressure rating of vent/drain connection.
Note on C105: Select whether for the manifold the capability to lock the valves in the position is required.
Note on C107: Select whether the pressure limit valve is required. If "yes" is selected, provide further details including materials in the "Supplement" tab. Default value : no
Note on C108: Select whether the restrictor is required. If "yes" selected, provide further details including restriction size in the "Supplement" tab. Default value : no
Note on C109: Select based on process conditions whether the snubber is required. If "yes" selected, specify model number, materials and design in the "Supplement" tab. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS PressTrans
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Pressure Transmitter | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Instrumentation type : | select |  | select | [5 empty] | select | pressure transmitter (gauge) | pressure transmitter (absolute)
5 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
6 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
7 | 4.1.2.1 | Tag number : | input data |  | input data
8 |  | Service description : | input data |  | input data
9 |  | Manufacturer : | input data |  | input data
10 | 8.3.4.1 | Model number : | input data |  | input data
11 |  | Equipment manufacturer serial number : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
13 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
14 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
15 |  | P&ID number : | input data |  | input data
16 |  | Line or equipment number : | input data |  | input data
17 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
19 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
20 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
21 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
22 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
23 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
24 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
25 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
26 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
27 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
28 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
29 |  | Installation conditions
30 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
31 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
32 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
33 |  | Process connection material type : | input data |  | input data
34 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
35 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
36 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
37 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
38 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
39 |  | Operating conditions
40 |  | Process fluid(s) : | input data |  | input data
41 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
42 |  | Service description : | input data |  | input data
43 |  | Process fluid corrosive compounds : | input data |  | input data
44 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
45 |  | Process fluid plugging : | no |  | no | [5 empty] | select | T1: yes; T2: no
46 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
47 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
48 |  | Minimum operating liquid specific gravity : | input data |  | input data
49 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
50 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
51 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
52 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
53 |  | Normal operating liquid specific gravity : | input data |  | input data
54 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
55 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
56 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
57 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
58 |  | Maximum operating liquid specific gravity : | input data |  | input data
59 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
60 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
61 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
62 |  | Minimum pressure span : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag | bar | psi | kPa
63 |  | Maximum pressure span : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag | bar | psi | kPa
64 |  | Transmitter
65 |  | Transmitter model number : | input data |  | input data
66 | 4.3.1.1.1 - 4.3.1.1.3, 4.3.1.1.5 | Transmitter body wetted material : | input data |  | input data
67 | 4.3.1.4 | O-ring material : | input data |  | input data
68 |  | Transmitter enclosure material : | input data |  | input data
69 | 4.3.1.1.1 - 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Isolating diaphragm (sensor) material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
70 |  | Isolating diaphragm fill fluid : | input data |  | input data
71 | 4.3.1.1.4 | Isolating diaphragm plating : | none |  | none | [5 empty] | select | T1: none; T2: gold
72 | 4.3.1.1.4 | Isolating diaphragm plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: µm; T2: µin
73 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
74 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
75 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
76 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
77 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
78 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
79 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
80 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
81 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
82 |  | Protocol version : | input data |  | input data
83 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
84 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
85 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
86 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
87 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
88 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
89 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
90 |  | Performance
91 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
92 |  | Long term drift : | input data |  | input data
93 |  | Long term stability : | input data |  | input data
94 |  | Diaphragm seal (option)
95 |  | Diaphragm seal type : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other | not applicable
96 | 5.2.5 | Diaphragm seal configuration : | select |  | select | [5 empty] | select | close coupled (single connection) | remote seal (single connection) | balanced system (both capillaries equal length) | unbalanced system (low side capillary - high side direct connected) | unbalanced system (high side seal - low side open to atmosphere) | not applicable
97 |  | Diaphragm seal - sealing material : | select |  | select | [5 empty] | select | graphite | FPM | PTFE | other
98 | 5.2.1, 5.2.2 | Diaphragm seal capillary / armour material : | input data |  | input data
99 |  | Diaphragm seal capillary length : | input data | select | input data | select |  |  |  |  | select | mm | in | m | ft
100 | 5.2.2, 5.2.4, 5.2.5 | Diaphragm seal capillary fill fluid : | input data |  | input data
101 |  | Diaphragm seal upper housing material : | input data |  | input data
102 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.5 | Diaphragm seal lower housing material : | input data |  | input data
103 | 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
104 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | T1: none; T2: gold
105 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: micro-inches; T2: nano-metres
106 |  | Diaphragm seal flushing connection : | select |  | select | [5 empty] | select | one 1/4-18 NPT(F) | two 1/4-18 NPT(F) | one 1/2 -14 NPT(F) | two 1/2-14 NPT(F)
107 |  | Diaphragm seal process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in | not applicable
108 |  | Diaphragm seal process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
109 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
110 |  | Manifold (option)
111 |  | Manifold manufacturer : | input data |  | input data
112 |  | Manifold model number : | input data |  | input data
113 |  | Manifold type : | select |  | select | [5 empty] | select | T1: 2-valve; T2: 5-valve; T3: not applicable
114 |  | Manifold assembly orientation : | select |  | select | [5 empty] | select | T1: bottom; T2: side
115 |  | Manifold material : | input data |  | input data
116 |  | Manifold packing material : | input data |  | input data
117 |  | Manifold assembly process connection size : | select |  | select | [5 empty] | select | T1: 12 mm; T2: ½ in; T3: 2 in
118 |  | Manifold assembly process connection type : | select |  | select | [5 empty] | select | NPT(F) | RF | RTJ | FF
119 |  | Manifold assembly process connection rating : | select |  | select | [5 empty] | select | T1: 3 000 psi; T2: 6 000 psi; T3: 10 000 psi
120 |  | Manifold assembly vent/drain connection size : | select |  | select | [5 empty] | select | 6 mm | 12 mm | ½ in | ¼ in
121 |  | Manifold assembly vent/drain connection type : | select |  | select | [5 empty] | select | T1: NPT(F); T2: other
122 |  | Manifold assembly vent/drain connection rating : | select |  | select | [5 empty] | select | T1: 3 000 psi; T2: 6 000 psi; T3: 10 000 psi
123 |  | Manifold valves lockable : | select |  | select | [5 empty] | select | T1: yes; T2: no
124 |  | Accessories
125 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
126 |  | Mounting bracket : | select |  | select | [5 empty] | select | T1: yes; T2: no
127 |  | Mounting bracket material : | select |  | select | [5 empty] | select | T1: 316 SS; T2: other
128 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
129 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the instrument type (technology) to be purchased.
Note on C5: Select the code compliance for the region where the instrument is to be installed.
Note on C6: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C7: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C8: Specify a functional description of the tag.
Note on C9: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C10: Specify the model number of the offered instrument assembly/unit.
Note on C11: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C12: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C13: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C14: Select the location of the facility where the equipment is to be permanently installed.
Note on C15: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C16: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C17: Specify as per process data.
Note on C18: Specify as per process data.
Note on C19: Select the required project painting durability level.
Note on C20: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C21: Select the nut material as detailed in IOGP S-563.
Note on C22: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C23: Select the ingress protection rating in IP or NEMA.
Note on C24: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C25: Select the code to be followed for the hazardous area classification.
Note on C26: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C27: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C28: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C30: Specify the size of the connection to the process.
Note on C31: Select the pressure rating of the system connected.
Note on C32: Select the type of the connection to the process.
Note on C33: Specify the material of the process flange.
Note on C34: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C35: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C36: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C37: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C38: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C40: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C41: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C42: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C43: Specify any corrosive elements in the process stream.
Note on C44: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C45: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C46: Specify the temperature of the process at the minimum sizing case.
Note on C47: Specify the differential pressure of the process at the minimum sizing case.
Note on C48: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C49: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C50: Specify the vapour viscosity at minimum sizing conditions.
Note on C51: Specify the temperature of the process at the minimum sizing case.
Note on C52: Specify the pressure of the process for the normal operating case.
Note on C53: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C54: Specify the viscosity of the process fluid at the normal sizing case.
Note on C55: Specify the vapour viscosity at normal sizing conditions.
Note on C56: Specify the temperature of the process at the maximum sizing case.
Note on C57: Specify the pressure of the process for the maximum operating case.
Note on C58: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C59: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C60: Specify the vapour viscosity at the maximum sizing conditions.
Note on C61: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C62: Specify the minimum span that the pressure element is capable of.
Note on C63: Specify the maximum span that the pressure element is capable of.
Note on C65: Specify the model number for the transmitter only.
Note on C66: Specify the material of the socket inlet port (wetted part). Input "not applicable" when diaphragm seal type is selected.
Note on C67: Specify the O-ring material (pressure-containing) to meet the specified process requirements. Consider whether explosive decompression standards are to be complied with.
Note on C68: Specify the material offered to meet the minimum requirements.
Note on C69: Specify the material of the diaphragm or bellow (wetted part).
Note on C70: Specify the fill fluid within transmitter pressure capsule within the transmitter body.
Note on C71: Select whether there is hydrogen present, hence risk of embrittlement and therefore the need for gold plating. Default value : none
Note on C72: Specify the calculated thickness supported by calculations.
Note on C73: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C74: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C75: Select the required signal type.
Note on C76: Select the type of power supply to the instrument. Default value : hardwired
Note on C77: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C78: Select the type of connection for the cable to the transmitter head.
Note on C79: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C80: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C81: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C82: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C83: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C84: Specify the bespoke range when supplier non-standard calibration is required.
Note on C85: Specify the lowest measured point for the instrument.
Note on C86: Specify the highest measured point for the instrument.
Note on C87: Select where the functionality is to be located.
Note on C88: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C89: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C91: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C92: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C93: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C95: Select the length that the seal is to protrude to inside the nozzle or flush if no extension is required.
Note on C96: Select the type of diaphragm seal configuration to be selected for chosen application.
Note on C97: Select the material of seal between the diaphragm and the process connection.
Note on C98: Specify the material suitable for the ambient conditions and fill fluid. Select "not applicable" when it is direct mount.
Note on C99: Specify the length. For a balanced system, the length is to be for both capillaries. For an unbalanced system, refer to the "instrumentation type" data sheet field to determine whether it is high or low pressure leg.
Note on C100: Specify the fill fluid. Silicon or glycerin are standard, subject to the operating temperature of the process. Ensure that it complies with API RP 551, 9.3.1.
Note on C101: Specify the upper housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C102: Specify the lower housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C103: Select the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C104: Select the option for gold plating if required for hydrogen service.
Note on C105: Specify the calculated thickness (to be supported by calculations).
Note on C106: Select the size of threaded connection when the flushing function is required.
Note on C107: Select the size for the flanged connection.
Note on C108: Select the flange finish.
Note on C109: Select the diaphragm flange rating in line with the installed rating and as per the piping specification.
Note on C111: Specify the manifold make.
Note on C112: Specify the full model number of the manifold being supplied.
Note on C113: Select the manifold type. "2-valve" is normally specified for pressure transmitter applications and "5-valve" for differential pressure. Select "not applicable" if a diaphragm seal is selected.
Note on C114: Select either bottom entry or side entry for connection to transmitter.
Note on C115: Specify the manifold material, normally 316L stainless steel minimum to meet process requirements.
Note on C116: Specify the material used in packing material.
Note on C117: Select the connection size at the boundary point of supplier interface to the process.
Note on C118: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C119: Select the pressure rating of flanged connection.
Note on C120: Select the connection size at the boundary point of suppliers interface to the process.
Note on C121: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C122: Select the pressure rating of vent/drain connection.
Note on C123: Select whether for the manifold the capability to lock the valves in the position is required.
Note on C125: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C126: Select "yes" When remote mount or "no" if direct mount.
Note on C127: Select the mounting bracket material. Minimum material 316 stainless steel but "other" can be selected when more suitable.
Note on C128: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C129: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS PressDiffTrans
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Pressure Differential Transmitter | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
19 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
20 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
21 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
22 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
23 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
24 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
25 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
26 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
27 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
28 |  | Flow meter : | input data |  | input data
29 |  | Installation conditions
30 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
31 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
32 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
33 |  | Process connection material type : | input data |  | input data
34 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
35 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
36 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
37 |  | Upstream (high-side) connection orientation : | input data |  | input data
38 |  | Upstream (high-side) material type : | input data |  | input data
39 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
40 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
41 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
42 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
43 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
44 |  | Downstream (bottom-side) material type : | input data |  | input data
45 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
46 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
47 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
48 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
49 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
50 |  | Operating conditions
51 |  | Process fluid(s) : | input data |  | input data
52 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
53 |  | Service description : | input data |  | input data
54 |  | Process fluid corrosive compounds : | input data |  | input data
55 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
56 |  | Process fluid plugging : | no |  | no | [5 empty] | select | T1: yes; T2: no
57 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
58 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | T1: bar; T2: psi; T3: kPa
59 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
60 |  | Normal operating pressure differential : | input data | select | input data | select |  |  |  |  | select | T1: bar; T2: psi; T3: kPa
61 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
62 |  | Maximum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | T1: bar; T2: psi; T3: kPa
63 |  | Minimum operating upper fluid density : | input data | kg/m³ | input data | kg/m³
64 |  | Minimum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
65 |  | Minimum operating upper fluid specific gravity : | input data |  | input data
66 |  | Minimum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
67 |  | Minimum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kpag
68 |  | Minimum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
69 |  | Minimum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
70 |  | Minimum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
71 |  | Minimum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
72 |  | Minimum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
73 |  | Minimum operating lower fluid specific gravity : | input data |  | input data
74 |  | Minimum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
75 |  | Normal operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
76 |  | Normal operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
77 |  | Normal operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
78 |  | Normal operating upper fluid density : | input data | kg/m³ | input data | kg/m³
79 |  | Normal operating upper fluid specific gravity : | input data |  | input data
80 |  | Normal operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
81 |  | Normal operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
82 |  | Normal operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
83 |  | Normal operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
84 |  | Normal operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
85 |  | Normal operating lower fluid density : | input data | kg/m³ | input data | kg/m³
86 |  | Normal operating lower fluid specific gravity : | input data |  | input data
87 |  | Maximum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
88 |  | Maximum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
89 |  | Maximum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
90 |  | Maximum operating upper fluid density : | input data | kg/m³ | input data | kg/m³
91 |  | Maximum operating upper fluid specific gravity : | input data |  | input data
92 |  | Maximum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
93 |  | Maximum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
94 |  | Maximum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
95 |  | Maximum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
96 |  | Maximum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
97 |  | Maximum operating lower fluid specific gravity : | input data |  | input data
98 |  | Maximum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
99 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
100 |  | Body/element/sensor
101 |  | Minimum differential pressure span : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | InH2O
102 |  | Maximum differential pressure span : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | InH2O
103 |  | Minimum pressure span : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag | bar | psi | kPa
104 |  | Maximum pressure span : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag | bar | psi | kPa
105 |  | Transmitter
106 |  | Transmitter model number : | input data |  | input data
107 | 4.3.1.1.1 - 4.3.1.1.3, 4.3.1.1.5 | Transmitter body wetted material : | input data |  | input data
108 | 4.3.1.4 | O-ring material : | input data |  | input data
109 |  | Transmitter enclosure material : | input data |  | input data
110 | 4.3.1.1.1 - 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Isolating diaphragm (sensor) material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
111 |  | Isolating diaphragm fill fluid : | input data |  | input data
112 | 4.3.1.1.4 | Isolating diaphragm plating : | none |  | none | [5 empty] | select | T1: none; T2: gold
113 | 4.3.1.1.4 | Isolating diaphragm plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: µm; T2: µin
114 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
115 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
116 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
117 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
118 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
119 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
120 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
121 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
122 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
123 |  | Protocol version : | input data |  | input data
124 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
125 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
126 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
127 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
128 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
129 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
130 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
131 |  | Static pressure output : | select |  | select | [5 empty] | select | T1: yes; T2: no
132 |  | Square root extraction : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
133 |  | Temperature transmitter
134 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
135 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
136 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
137 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
138 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
139 |  | Body/element/sensor manufacturer model number : | input data |  | input data
140 | 4.1.2.1 | Temperature instrument tag number : | input data |  | input data
141 |  | Temperature element type : | select |  | select | [5 empty] | select | RTD Pt-100 3-wire | RTD Pt-100 4-wire | TC type J | TC type B | TC type E | TC type K | TC type N | TC type R | TC type S | TC type T | TC type C
142 |  | Temperature element tolerance class : | select |  | select | [5 empty] | select | Class AA (IEC 60751) | Class BB (IEC 60751) | Class A | Class B (IEC 60751) | Grade A (ASTM E1137/E1137M) | Grade B (ASTM E1137/E1137M) | Class 1 (IEC 60584) | Class 2 (IEC 60584) | special tolerance (ASTM E230/E230M) | standard tolerance (ASTM E230/E230M)
143 |  | Temperature element sheath material : | input data |  | input data
144 | 6.1.9 | Temperature element, simplex/duplex : | duplex |  | duplex | [5 empty] | select | T1: duplex; T2: simplex
145 |  | Temperature element sheath outside diameter : | 6 mm |  | 6 mm | [5 empty] | select | T1: 6 mm; T2: ¼ in; T3: other
146 |  | Temperature element extension material : | input data |  | input data
147 |  | Temperature element extension type : | input data |  | input data
148 |  | Temperature element number of terminals : | 6 |  | 6 | [5 empty] | select | T1: 4; T2: 6; T3: 8
149 |  | Thermowell insertion length (U) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
150 |  | Thermowell lagging extension length (T) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
151 |  | Thermowell root diameter (A) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
152 |  | Thermowell tip diameter (B) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
153 |  | Thermowell bore diameter (d) : | 6,6 mm |  | 6,6 mm | [5 empty] | select | T1: 6,6 mm; T2: 0,26 in; T3: other
154 |  | Thermowell tip thickness (t) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
155 |  | Thermowell fillet radius (b) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
156 |  | Performance
157 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
158 |  | Long term drift : | input data |  | input data
159 |  | Long term stability : | input data |  | input data
160 |  | Influence of static pressure : | input data | % | input data | %
161 |  | Electronic remote seal (option)
162 |  | Diaphragm seal type - primary : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other
163 |  | Diaphragm seal type - secondary : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other | not applicable
164 |  | Diaphragm seal upper housing material : | input data |  | input data
165 |  | Diaphragm seal lower housing material : | input data |  | input data
166 |  | Connecting cable length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
167 |  | Tag number - secondary transmitter : | input data |  | input data
168 |  | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
169 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | T1: none; T2: gold
170 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: µm, µin
171 |  | Diaphragm seal process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in
172 |  | Diaphragm seal process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
173 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
174 |  | Diaphragm seal (option)
175 |  | Diaphragm seal type : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other | not applicable
176 | 5.2.5 | Diaphragm seal configuration : | select |  | select | [5 empty] | select | close coupled (single connection) | remote seal (single connection) | balanced system (both capillaries equal length) | unbalanced system (low side capillary - high side direct connected) | unbalanced system (high side seal - low side open to atmosphere) | not applicable
177 |  | Diaphragm seal - sealing material : | select |  | select | [5 empty] | select | graphite | FPM | PTFE | other
178 | 5.2.1, 5.2.2 | Diaphragm seal capillary / armour material : | input data |  | input data
179 |  | Diaphragm seal capillary length : | input data | select | input data | select |  |  |  |  | select | mm | in | m | ft
180 | 5.2.2, 5.2.4, 5.2.5 | Diaphragm seal capillary fill fluid : | input data |  | input data
181 |  | Diaphragm seal upper housing material : | input data |  | input data
182 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.5 | Diaphragm seal lower housing material : | input data |  | input data
183 | 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
184 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | T1: none; T2: gold
185 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: micro-inches; T2: nano-metres
186 |  | Diaphragm seal flushing connection : | select |  | select | [5 empty] | select | one 1/4-18 NPT(F) | two 1/4-18 NPT(F) | one 1/2 -14 NPT(F) | two 1/2-14 NPT(F)
187 |  | Diaphragm seal process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in | not applicable
188 |  | Diaphragm seal process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
189 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
190 |  | Manifold (option)
191 |  | Manifold manufacturer : | input data |  | input data
192 |  | Manifold model number : | input data |  | input data
193 |  | Manifold type : | select |  | select | [5 empty] | select | T1: 2-valve; T2: 5-valve; T3: not applicable
194 |  | Manifold assembly orientation : | select |  | select | [5 empty] | select | T1: bottom; T2: side
195 |  | Manifold material : | input data |  | input data
196 |  | Manifold packing material : | input data |  | input data
197 |  | Manifold assembly process connection size : | select |  | select | [5 empty] | select | T1: 12 mm; T2: ½ in; T3: 2 in
198 |  | Manifold assembly process connection type : | select |  | select | [5 empty] | select | NPT(F) | RF | RTJ | FF
199 |  | Manifold assembly process connection rating : | select |  | select | [5 empty] | select | T1: 3 000 psi; T2: 6 000 psi; T3: 10 000 psi
200 |  | Manifold assembly vent/drain connection size : | select |  | select | [5 empty] | select | 6 mm | 12 mm | ½ in | ¼ in
201 |  | Manifold assembly vent/drain connection type : | select |  | select | [5 empty] | select | T1: NPT(F); T2: other
202 |  | Manifold assembly vent/drain connection rating : | select |  | select | [5 empty] | select | T1: 3 000 psi; T2: 6 000 psi; T3: 10 000 psi
203 |  | Manifold valves lockable : | select |  | select | [5 empty] | select | T1: yes; T2: no
204 |  | Accessories
205 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
206 |  | Mounting bracket : | select |  | select | [5 empty] | select | T1: yes; T2: no
207 |  | Mounting bracket material : | select |  | select | [5 empty] | select | T1: 316 SS; T2: other
208 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
209 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the required project painting durability level.
Note on C19: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C20: Select the nut material as detailed in IOGP S-563.
Note on C21: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C22: Select the ingress protection rating in IP or NEMA.
Note on C23: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C24: Select the code to be followed for the hazardous area classification.
Note on C25: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C26: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C27: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C28: Specify the tag of the flow meter to which the multivariable transmitter is linked.
Note on C30: Specify the size of the connection to the process.
Note on C31: Select the pressure rating of the system connected.
Note on C32: Select the type of the connection to the process.
Note on C33: Specify the material of the process flange.
Note on C34: Specify the process line size to support sizing and selection by the supplier.
Note on C35: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C36: Select the instrument process connection compatible with that declared by the purchaser.
Note on C37: Specify the orientation of the inlet to the instrument or insertion point.
Note on C38: Specify the material which the instrument connects to on the upstream face.
Note on C39: Select the pipe schedule in accordance with the pipe specification.
Note on C40: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C41: Select the pressure rating of the system connected.
Note on C42: Select the process connection to the system.
Note on C43: Specify the orientation of the inlet or insertion point of the instrument.
Note on C44: Specify the material which the instrument connects to on the downstream face.
Note on C45: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C46: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C47: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C48: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C49: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C51: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C52: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C53: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C54: Specify any corrosive elements in the process stream.
Note on C55: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C56: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C57: Specify the temperature of the process at the minimum sizing case.
Note on C58: Specify the differential pressure of the process at the minimum sizing case.
Note on C59: Specify the temperature of the process at the minimum sizing case.
Note on C60: Specify the differential pressure of the process at the normal sizing case.
Note on C61: Specify the temperature of the process at the maximum sizing case.
Note on C62: Specify the differential pressure of the process at the maximum sizing case.
Note on C63: Specify the upper fluid density.
Note on C64: Select the phase at the upper location.
Note on C65: Specify the specific gravity of the process fluid in the upper section.
Note on C66: Specify the viscosity of the process fluid in the upper section.
Note on C67: Specify the pressure at the upper location.
Note on C68: Specify the upper location temperature.
Note on C69: Specify the pressure at the lower location.
Note on C70: Specify the lower location temperature.
Note on C71: Select the phase at the upper location.
Note on C72: Specify the lower fluid density.
Note on C73: Specify the specific gravity of the process fluid in the upper section.
Note on C74: Specify the viscosity of the process fluid in the upper section.
Note on C75: Specify the pressure at the upper location.
Note on C76: Specify the upper location temperature.
Note on C77: Select the phase at the upper location.
Note on C78: Specify the upper fluid density
Note on C79: Specify the specific gravity of the process fluid in the upper section.
Note on C80: Specify the viscosity of the process fluid in the upper section.
Note on C81: Specify the pressure at the upper location.
Note on C82: Specify the lower location temperature.
Note on C83: Select the phase at the lower location.
Note on C84: Specify the viscosity of the process fluid in the upper section.
Note on C85: Specify the lower fluid density.
Note on C86: Specify the specific gravity of the process fluid in the upper section.
Note on C87: Specify the pressure at the upper location.
Note on C88: Specify the upper location temperature.
Note on C89: Select the phase at the upper location.
Note on C90: Specify the upper fluid density.
Note on C91: Specify the specific gravity of the process fluid in the upper section.
Note on C92: Specify the viscosity of the process fluid in the upper section.
Note on C93: Specify the phase at the lower location.
Note on C94: Specify the lower location temperature.
Note on C95: Select the phase at the lower location.
Note on C96: Specify the lower fluid density
Note on C97: Specify the specific gravity of the process fluid in the upper section.
Note on C98: Specify the viscosity of the process fluid in the upper section.
Note on C99: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C101: Specify the minimum differential span that the pressure element is capable of.
Note on C102: Specify the maximum differential span that the pressure element is capable of.
Note on C103: Specify the minimum span that the pressure element is capable of.
Note on C104: Specify the maximum span that the pressure element is capable of.
Note on C106: Specify the model number for the transmitter only.
Note on C107: Specify the material of the socket inlet port (wetted part). Input "not applicable" when diaphragm seal type is selected.
Note on C108: Specify the O-ring material (pressure-containing) to meet the specified process requirements. Consider whether explosive decompression standards are to be complied with.
Note on C109: Specify the material offered to meet the minimum requirements.
Note on C110: Specify the material of the diaphragm or bellow (wetted part).
Note on C111: Specify the fill fluid within transmitter pressure capsule within the transmitter body.
Note on C112: Select whether there is hydrogen present, hence risk of embrittlement and therefore the need for gold plating. Default value : none
Note on C113: Specify the calculated thickness supported by calculations.
Note on C114: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C115: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C116: Select the required signal type.
Note on C117: Select the type of power supply to the instrument. Default value : hardwired
Note on C118: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C119: Select the type of connection for the cable to the transmitter head.
Note on C120: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C121: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C122: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C123: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C124: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C125: Specify the bespoke range when supplier non-standard calibration is required.
Note on C126: Specify the lowest measured point for the instrument.
Note on C127: Specify the highest measured point for the instrument.
Note on C128: Select where the functionality is to be located.
Note on C129: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C130: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C131: Confirm whether the static pressure is required as an output variable from the transmitter.
Note on C132: Select whether the transmitter is to be supplied with the square root extraction active. Default value : yes
Note on C134: Specify the lowest measured point for the instrument.
Note on C135: Specify the highest measured point for the instrument.
Note on C136: Select where the functionality is to be located.
Note on C137: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C138: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C139: Specify the model number of body/element/sensor.
Note on C140: Specify the unique tag number for the equipment, following the operator's philosophy for tagging globally.
Note on C141: Select the temperature element type required.
Note on C142: Select the class or grade tolerances as per the applicable standard.
Note on C143: Specify the sheath material (metal or others) suitable for the specified operating environment.
Note on C144: Select whether a single or duplex element is required. The specification mandates duplex hence only single option and any deviation would need to be stated in notes field. Default value : duplex
Note on C145: Select the outside diameter (OD) of the element to fit inside the thermowell. Default value : 6 mm
Note on C146: Specify the nipple material suitable for the environment conditions.
Note on C147: Specify the type of extension selected for the purchaser declared service conditions.
Note on C148: Select the terminal block to cater for duplex installations and selection from six or eight terminals. Default value : 6
Note on C149: Specify the length measured from the bottom of the flange to the tip of the thermowell. ASME PTC 19.3 TW uses the term "unsupported length"' with variable "L".
Note on C150: Specify the length measured from the bottom of the flange to the top of the thermowell assembly, including any nipple extension. Terminal heads attached to thermowells with extension pieces providing space for at least 80 mm (3 in) insulation.
Note on C151: Specify the root diameter of the model supplied and figure to be used in calculations.
Note on C152: Specify the tip diameter of the model supplied and figure to be used in calculations.
Note on C153: Select the bore diameter and figure to be used in calculations, the standard size in industry being 6,6 mm (0,26 in). Test thermowells can be 9,8 mm (0,385 in) to allow easy insertion and removal. Default value : 6,6 mm
Note on C154: Specify the tip thickness of the model supplied and figure to be used in calculations.
Note on C155: Specify the fillet radius (b) of the model supplied and figure to be used in calculations.
Note on C157: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C158: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C159: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C160: Specify the test results in accordance with IEC 62828-2, 6.2.4.
Note on C162: Select the length to which the seal is to protrude (on the primary / high pressure side) to inside the nozzle or flush if no extension is required. If extension is selected, specify the length in the "Additional notes" column.
Note on C163: Select the length to which the seal is to protrude (on the secondary / low pressure) to inside the nozzle or flush if no extension is required.
Note on C164: Specify the upper housing (non wetted) material. Minimum 316 stainless steel is common but depending on the fill fluid, more exotic material selection can apply.
Note on C165: Specify the lower housing (wetted) material. Minimum 316 stainless steel is common but depending on the fill fluid, more exotic material selection can apply.
Note on C166: Specify the length of cable to connect between the primary and secondary transmitters.
Note on C167: Specify the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C168: Specify the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C169: Select the option for plating.
Note on C170: Specify the calculated thickness (to be supported by calculations).
Note on C171: Select the size for flanged connection. The default value is normally 50 mm (2 in).
Note on C172: Select the flange finish.
Note on C173: Select the diaphragm flange rating in line with the installed rating and as per piping specification.
Note on C175: Select the length that the seal is to protrude to inside the nozzle or flush if no extension is required.
Note on C176: Select the type of diaphragm seal configuration to be selected for chosen application.
Note on C177: Select the material of seal between the diaphragm and the process connection.
Note on C178: Specify the material suitable for the ambient conditions and fill fluid. Select "not applicable" when it is direct mount.
Note on C179: Specify the length. For a balanced system, the length is to be for both capillaries. For an unbalanced system, refer to the "instrumentation type" data sheet field to determine whether it is high or low pressure leg.
Note on C180: Specify the fill fluid. Silicon or glycerin are standard, subject to the operating temperature of the process. Ensure that it complies with API RP 551, 9.3.1.
Note on C181: Specify the upper housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C182: Specify the lower housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C183: Select the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C184: Select the option for gold plating if required for hydrogen service.
Note on C185: Specify the calculated thickness (to be supported by calculations).
Note on C186: Select the size of threaded connection when the flushing function is required.
Note on C187: Select the size for the flanged connection.
Note on C188: Select the flange finish.
Note on C189: Select the diaphragm flange rating in line with the installed rating and as per the piping specification.
Note on C191: Specify the manifold make.
Note on C192: Specify the full model number of the manifold being supplied.
Note on C193: Select the manifold type. "2-valve" is normally specified for pressure transmitter applications and "5-valve" for differential pressure. Select "not applicable" if a diaphragm seal is selected.
Note on C194: Select either bottom entry or side entry for connection to transmitter.
Note on C195: Specify the manifold material, normally 316L stainless steel minimum to meet process requirements.
Note on C196: Specify the material used in packing material.
Note on C197: Select the connection size at the boundary point of supplier interface to the process.
Note on C198: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C199: Select the pressure rating of flanged connection.
Note on C200: Select the connection size at the boundary point of suppliers interface to the process.
Note on C201: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C202: Select the pressure rating of vent/drain connection.
Note on C203: Select whether for the manifold the capability to lock the valves in the position is required.
Note on C205: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C206: Select "yes" When remote mount or "no" if direct mount.
Note on C207: Select the mounting bracket material. Minimum material 316 stainless steel but "other" can be selected when more suitable.
Note on C208: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C209: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS PressDiffTransMV
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Pressure Differential Transmitter - Multivariable | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
19 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
20 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
21 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
22 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
23 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
24 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
25 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
26 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
27 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
28 |  | Flow meter : | input data |  | input data
29 |  | Installation conditions
30 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
31 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
32 |  | Process connection material type : | input data |  | input data
33 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
34 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
35 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
36 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
37 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
38 |  | Operating conditions
39 |  | Process fluid(s) : | input data |  | input data
40 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
41 |  | Service description : | input data |  | input data
42 |  | Process fluid corrosive compounds : | input data |  | input data
43 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
44 |  | Process fluid plugging : | no |  | no | [5 empty] | select | T1: yes; T2: no
45 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
46 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | T1: bar; T2: psi; T3: kPa
47 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
48 |  | Normal operating pressure differential : | input data | select | input data | select |  |  |  |  | select | T1: bar; T2: psi; T3: kPa
49 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
50 |  | Maximum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | T1: bar; T2: psi; T3: kPa
51 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
52 |  | Body/element/sensor
53 |  | Minimum differential pressure span : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | InH2O
54 |  | Maximum differential pressure span : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | InH2O
55 |  | Minimum pressure span : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag | bar | psi | kPa
56 |  | Maximum pressure span : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag | bar | psi | kPa
57 |  | Transmitter
58 |  | Transmitter model number : | input data |  | input data
59 | 4.3.1.1.1 - 4.3.1.1.3, 4.3.1.1.5 | Transmitter body wetted material : | input data |  | input data
60 | 4.3.1.4 | O-ring material : | input data |  | input data
61 |  | Transmitter enclosure material : | input data |  | input data
62 | 4.3.1.1.1 - 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Isolating diaphragm (sensor) material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
63 |  | Isolating diaphragm fill fluid : | input data |  | input data
64 | 4.3.1.1.4 | Isolating diaphragm plating : | none |  | none | [5 empty] | select | T1: none; T2: gold
65 | 4.3.1.1.4 | Isolating diaphragm plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: µm; T2: µin
66 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
67 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
68 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
69 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
70 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
71 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
72 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
73 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
74 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
75 |  | Protocol version : | input data |  | input data
76 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
77 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
78 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
79 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
80 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
81 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
82 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
83 |  | Static pressure output : | select |  | select | [5 empty] | select | T1: yes; T2: no
84 |  | Square root extraction : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
85 |  | Temperature transmitter
86 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
87 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
88 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
89 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
90 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
91 |  | Body/element/sensor manufacturer model number : | input data |  | input data
92 | 4.1.2.1 | Temperature instrument tag number : | input data |  | input data
93 |  | Temperature element type : | select |  | select | [5 empty] | select | RTD Pt-100 3-wire | RTD Pt-100 4-wire | TC type J | TC type B | TC type E | TC type K | TC type N | TC type R | TC type S | TC type T | TC type C
94 |  | Temperature element tolerance class : | select |  | select | [5 empty] | select | Class AA (IEC 60751) | Class BB (IEC 60751) | Class A | Class B (IEC 60751) | Grade A (ASTM E1137/E1137M) | Grade B (ASTM E1137/E1137M) | Class 1 (IEC 60584) | Class 2 (IEC 60584) | special tolerance (ASTM E230/E230M) | standard tolerance (ASTM E230/E230M)
95 |  | Temperature element sheath material : | input data |  | input data
96 | 6.1.9 | Temperature element, simplex/duplex : | duplex |  | duplex | [5 empty] | select | T1: duplex; T2: simplex
97 |  | Temperature element sheath outside diameter : | 6 mm |  | 6 mm | [5 empty] | select | T1: 6 mm; T2: ¼ in; T3: other
98 |  | Temperature element extension material : | input data |  | input data
99 |  | Temperature element extension type : | input data |  | input data
100 |  | Temperature element number of terminals : | 6 |  | 6 | [5 empty] | select | T1: 4; T2: 6; T3: 8
101 |  | Thermowell insertion length (U) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
102 |  | Thermowell lagging extension length (T) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
103 |  | Thermowell root diameter (A) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
104 |  | Thermowell tip diameter (B) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
105 |  | Thermowell bore diameter (d) : | 6,6 mm |  | 6,6 mm | [5 empty] | select | T1: 6,6 mm; T2: 0,26 in; T3: other
106 |  | Thermowell tip thickness (t) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
107 |  | Thermowell fillet radius (b) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
108 |  | Performance
109 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
110 |  | Long term drift : | input data |  | input data
111 |  | Long term stability : | input data |  | input data
112 |  | Influence of static pressure : | input data | % | input data | %
113 |  | Electronic remote seal (option)
114 |  | Diaphragm seal type - primary : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other
115 |  | Diaphragm seal type - secondary : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other | not applicable
116 |  | Diaphragm seal upper housing material : | input data |  | input data
117 |  | Diaphragm seal lower housing material : | input data |  | input data
118 |  | Connecting cable length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
119 |  | Tag number - secondary transmitter : | input data |  | input data
120 |  | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
121 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | T1: none; T2: gold
122 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: µm, µin
123 |  | Diaphragm seal process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in
124 |  | Diaphragm seal process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
125 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
126 |  | Diaphragm seal (option)
127 |  | Diaphragm seal type : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other | not applicable
128 | 5.2.5 | Diaphragm seal configuration : | select |  | select | [5 empty] | select | close coupled (single connection) | remote seal (single connection) | balanced system (both capillaries equal length) | unbalanced system (low side capillary - high side direct connected) | unbalanced system (high side seal - low side open to atmosphere) | not applicable
129 |  | Diaphragm seal - sealing material : | select |  | select | [5 empty] | select | graphite | FPM | PTFE | other
130 | 5.2.1, 5.2.2 | Diaphragm seal capillary / armour material : | input data |  | input data
131 |  | Diaphragm seal capillary length : | input data | select | input data | select |  |  |  |  | select | mm | in | m | ft
132 | 5.2.2, 5.2.4, 5.2.5 | Diaphragm seal capillary fill fluid : | input data |  | input data
133 |  | Diaphragm seal upper housing material : | input data |  | input data
134 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.5 | Diaphragm seal lower housing material : | input data |  | input data
135 | 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
136 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | T1: none; T2: gold
137 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: micro-inches; T2: nano-metres
138 |  | Diaphragm seal flushing connection : | select |  | select | [5 empty] | select | one 1/4-18 NPT(F) | two 1/4-18 NPT(F) | one 1/2 -14 NPT(F) | two 1/2-14 NPT(F)
139 |  | Diaphragm seal process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in | not applicable
140 |  | Diaphragm seal process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
141 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
142 |  | Manifold (option)
143 |  | Manifold manufacturer : | input data |  | input data
144 |  | Manifold model number : | input data |  | input data
145 |  | Manifold type : | select |  | select | [5 empty] | select | T1: 2-valve; T2: 5-valve; T3: not applicable
146 |  | Manifold assembly orientation : | select |  | select | [5 empty] | select | T1: bottom; T2: side
147 |  | Manifold material : | input data |  | input data
148 |  | Manifold packing material : | input data |  | input data
149 |  | Manifold assembly process connection size : | select |  | select | [5 empty] | select | T1: 12 mm; T2: ½ in; T3: 2 in
150 |  | Manifold assembly process connection type : | select |  | select | [5 empty] | select | NPT(F) | RF | RTJ | FF
151 |  | Manifold assembly process connection rating : | select |  | select | [5 empty] | select | T1: 3 000 psi; T2: 6 000 psi; T3: 10 000 psi
152 |  | Manifold assembly vent/drain connection size : | select |  | select | [5 empty] | select | 6 mm | 12 mm | ½ in | ¼ in
153 |  | Manifold assembly vent/drain connection type : | select |  | select | [5 empty] | select | T1: NPT(F); T2: other
154 |  | Manifold assembly vent/drain connection rating : | select |  | select | [5 empty] | select | T1: 3 000 psi; T2: 6 000 psi; T3: 10 000 psi
155 |  | Manifold valves lockable : | select |  | select | [5 empty] | select | T1: yes; T2: no
156 |  | Accessories
157 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
158 |  | Mounting bracket : | select |  | select | [5 empty] | select | T1: yes; T2: no
159 |  | Mounting bracket material : | select |  | select | [5 empty] | select | T1: 316 SS; T2: other
160 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
161 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the required project painting durability level.
Note on C19: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C20: Select the nut material as detailed in IOGP S-563.
Note on C21: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C22: Select the ingress protection rating in IP or NEMA.
Note on C23: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C24: Select the code to be followed for the hazardous area classification.
Note on C25: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C26: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C27: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C28: Specify the tag of the flow meter to which the multivariable transmitter is linked.
Note on C30: Specify the size of the connection to the process.
Note on C31: Select the pressure rating of the system connected.
Note on C32: Specify the material of the process flange.
Note on C33: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C34: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C35: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C36: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C37: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C39: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C40: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C41: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C42: Specify any corrosive elements in the process stream.
Note on C43: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C44: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C45: Specify the temperature of the process at the minimum sizing case.
Note on C46: Specify the differential pressure of the process at the minimum sizing case.
Note on C47: Specify the temperature of the process at the minimum sizing case.
Note on C48: Specify the differential pressure of the process at the normal sizing case.
Note on C49: Specify the temperature of the process at the maximum sizing case.
Note on C50: Specify the differential pressure of the process at the maximum sizing case.
Note on C51: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C53: Specify the minimum differential span that the pressure element is capable of.
Note on C54: Specify the maximum differential span that the pressure element is capable of.
Note on C55: Specify the minimum span that the pressure element is capable of.
Note on C56: Specify the maximum span that the pressure element is capable of.
Note on C58: Specify the model number for the transmitter only.
Note on C59: Specify the material of the socket inlet port (wetted part). Input "not applicable" when diaphragm seal type is selected.
Note on C60: Specify the O-ring material (pressure-containing) to meet the specified process requirements. Consider whether explosive decompression standards are to be complied with.
Note on C61: Specify the material offered to meet the minimum requirements.
Note on C62: Specify the material of the diaphragm or bellow (wetted part).
Note on C63: Specify the fill fluid within transmitter pressure capsule within the transmitter body.
Note on C64: Select whether there is hydrogen present, hence risk of embrittlement and therefore the need for gold plating. Default value : none
Note on C65: Specify the calculated thickness supported by calculations.
Note on C66: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C67: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C68: Select the required signal type.
Note on C69: Select the type of power supply to the instrument. Default value : hardwired
Note on C70: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C71: Select the type of connection for the cable to the transmitter head.
Note on C72: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C73: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C74: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C75: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C76: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C77: Specify the bespoke range when supplier non-standard calibration is required.
Note on C78: Specify the lowest measured point for the instrument.
Note on C79: Specify the highest measured point for the instrument.
Note on C80: Select where the functionality is to be located.
Note on C81: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C82: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C83: Confirm whether the static pressure is required as an output variable from the transmitter.
Note on C84: Select whether the transmitter is to be supplied with the square root extraction active. Default value : yes
Note on C86: Specify the lowest measured point for the instrument.
Note on C87: Specify the highest measured point for the instrument.
Note on C88: Select where the functionality is to be located.
Note on C89: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C90: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C91: Specify the model number of body/element/sensor.
Note on C92: Specify the unique tag number for the equipment, following the operator's philosophy for tagging globally.
Note on C93: Select the temperature element type required.
Note on C94: Select the class or grade tolerances as per the applicable standard.
Note on C95: Specify the sheath material (metal or others) suitable for the specified operating environment.
Note on C96: Select whether a single or duplex element is required. The specification mandates duplex hence only single option and any deviation would need to be stated in notes field. Default value : duplex
Note on C97: Select the outside diameter (OD) of the element to fit inside the thermowell. Default value : 6 mm
Note on C98: Specify the nipple material suitable for the environment conditions.
Note on C99: Specify the type of extension selected for the purchaser declared service conditions.
Note on C100: Select the terminal block to cater for duplex installations and selection from six or eight terminals. Default value : 6
Note on C101: Specify the length measured from the bottom of the flange to the tip of the thermowell. ASME PTC 19.3 TW uses the term "unsupported length"' with variable "L".
Note on C102: Specify the length measured from the bottom of the flange to the top of the thermowell assembly, including any nipple extension. Terminal heads attached to thermowells with extension pieces providing space for at least 80 mm (3 in) insulation.
Note on C103: Specify the root diameter of the model supplied and figure to be used in calculations.
Note on C104: Specify the tip diameter of the model supplied and figure to be used in calculations.
Note on C105: Select the bore diameter and figure to be used in calculations, the standard size in industry being 6,6 mm (0,26 in). Test thermowells can be 9,8 mm (0,385 in) to allow easy insertion and removal. Default value : 6,6 mm
Note on C106: Specify the tip thickness of the model supplied and figure to be used in calculations.
Note on C107: Specify the fillet radius (b) of the model supplied and figure to be used in calculations.
Note on C109: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C110: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C111: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C112: Specify the test results in accordance with IEC 62828-2, 6.2.4.
Note on C114: Select the length to which the seal is to protrude (on the primary / high pressure side) to inside the nozzle or flush if no extension is required. If extension is selected, specify the length in the "Additional notes" column.
Note on C115: Select the length to which the seal is to protrude (on the secondary / low pressure) to inside the nozzle or flush if no extension is required.
Note on C116: Specify the upper housing (non wetted) material. Minimum 316 stainless steel is common but depending on the fill fluid, more exotic material selection can apply.
Note on C117: Specify the lower housing (wetted) material. Minimum 316 stainless steel is common but depending on the fill fluid, more exotic material selection can apply.
Note on C118: Specify the length of cable to connect between the primary and secondary transmitters.
Note on C119: Specify the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C120: Specify the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C121: Select the option for plating.
Note on C122: Specify the calculated thickness (to be supported by calculations).
Note on C123: Select the size for flanged connection. The default value is normally 50 mm (2 in).
Note on C124: Select the flange finish.
Note on C125: Select the diaphragm flange rating in line with the installed rating and as per piping specification.
Note on C127: Select the length that the seal is to protrude to inside the nozzle or flush if no extension is required.
Note on C128: Select the type of diaphragm seal configuration to be selected for chosen application.
Note on C129: Select the material of seal between the diaphragm and the process connection.
Note on C130: Specify the material suitable for the ambient conditions and fill fluid. Select "not applicable" when it is direct mount.
Note on C131: Specify the length. For a balanced system, the length is to be for both capillaries. For an unbalanced system, refer to the "instrumentation type" data sheet field to determine whether it is high or low pressure leg.
Note on C132: Specify the fill fluid. Silicon or glycerin are standard, subject to the operating temperature of the process. Ensure that it complies with API RP 551, 9.3.1.
Note on C133: Specify the upper housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C134: Specify the lower housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C135: Select the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C136: Select the option for gold plating if required for hydrogen service.
Note on C137: Specify the calculated thickness (to be supported by calculations).
Note on C138: Select the size of threaded connection when the flushing function is required.
Note on C139: Select the size for the flanged connection.
Note on C140: Select the flange finish.
Note on C141: Select the diaphragm flange rating in line with the installed rating and as per the piping specification.
Note on C143: Specify the manifold make.
Note on C144: Specify the full model number of the manifold being supplied.
Note on C145: Select the manifold type. "2-valve" is normally specified for pressure transmitter applications and "5-valve" for differential pressure. Select "not applicable" if a diaphragm seal is selected.
Note on C146: Select either bottom entry or side entry for connection to transmitter.
Note on C147: Specify the manifold material, normally 316L stainless steel minimum to meet process requirements.
Note on C148: Specify the material used in packing material.
Note on C149: Select the connection size at the boundary point of supplier interface to the process.
Note on C150: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C151: Select the pressure rating of flanged connection.
Note on C152: Select the connection size at the boundary point of suppliers interface to the process.
Note on C153: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C154: Select the pressure rating of vent/drain connection.
Note on C155: Select whether for the manifold the capability to lock the valves in the position is required.
Note on C157: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C158: Select "yes" When remote mount or "no" if direct mount.
Note on C159: Select the mounting bracket material. Minimum material 316 stainless steel but "other" can be selected when more suitable.
Note on C160: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C161: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS TempGauge
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Temperature Gauge | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
19 |  | Installation conditions
20 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
21 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
22 |  | Process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF
23 |  | Process connection material type : | input data |  | input data
24 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
25 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
26 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
27 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
28 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
29 | 7.2.1.3 | Insulation thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
30 |  | Connection length : | input data | select | input data | select |  |  |  |  | select | mm | in
31 |  | Thermowell shielded length (Lo) : | input data | select | input data | select |  |  |  |  | select | mm | in
32 |  | Operating conditions
33 |  | Process fluid(s) : | input data |  | input data
34 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
35 |  | Service description : | input data |  | input data
36 |  | Process fluid corrosive compounds : | input data |  | input data
37 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
38 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
39 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
40 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
41 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
42 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
43 |  | Maximum operating liquid specific gravity : | input data |  | input data
44 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
45 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
46 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
47 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
48 |  | TW Case 1
49 |  | Case 1 description : | input data |  | input data
50 |  | Case 1 pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
51 |  | Case 1 temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
52 |  | Case 1 velocity : | input data | m/s | input data | m/s
53 |  | Case 1 density : | input data | kg/m³ | input data | kg/m³
54 |  | Case 1 viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
55 |  | Case 1 process fluid : | input data |  | input data
56 |  | Case 1 process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
57 |  | TW Case 2
58 |  | Case 2 description : | input data |  | input data
59 |  | Case 2 pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
60 |  | Case 2 temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
61 |  | Case 2 velocity : | input data | m/s | input data | m/s
62 |  | Case 2 density : | input data | kg/m³ | input data | kg/m³
63 |  | Case 2 viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
64 |  | Case 2 process fluid : | input data |  | input data
65 |  | Case 2 process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
66 |  | TW Case 3
67 |  | Case 3 description : | input data |  | input data
68 |  | Case 3 pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
69 |  | Case 3 temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
70 |  | Case 3 velocity : | input data | m/s | input data | m/s
71 |  | Case 3 density : | input data | kg/m³ | input data | kg/m³
72 |  | Case 3 viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
73 |  | Case 3 process fluid : | input data |  | input data
74 |  | Case 3 process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
75 |  | TW Case 4
76 |  | Case 4 description : | input data |  | input data
77 |  | Case 4 pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
78 |  | Case 4 temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
79 |  | Case 4 velocity : | input data | m/s | input data | m/s
80 |  | Case 4 density : | input data | kg/m³ | input data | kg/m³
81 |  | Case 4 viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
82 |  | Case 4 process fluid : | input data |  | input data
83 |  | Case 4 process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
84 |  | TW Case 5
85 |  | Case 5 description : | input data |  | input data
86 |  | Case 5 pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
87 |  | Case 5 temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
88 |  | Case 5 velocity : | input data | m/s | input data | m/s
89 |  | Case 5 density : | input data | kg/m³ | input data | kg/m³
90 |  | Case 5 viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
91 |  | Case 5 process fluid : | input data |  | input data
92 |  | Case 5 process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
93 |  | TW Case 6
94 |  | Case 6 description : | input data |  | input data
95 |  | Case 6 pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
96 |  | Case 6 temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
97 |  | Case 6 velocity : | input data | m/s | input data | m/s
98 |  | Case 6 density : | input data | kg/m³ | input data | kg/m³
99 |  | Case 6 viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
100 |  | Case 6 process fluid : | input data |  | input data
101 |  | Case 6 process fluid state : | select |  | select | [5 empty] | select | liquid | vapour
102 |  | Body/element/sensor
103 |  | Body/element/sensor manufacturer model number : | input data |  | input data
104 |  | Temperature gauge element type : | bi-metallic (helix) |  | bi-metallic (helix) | [5 empty] | select | bi-metallic - helix | bi-metallic - strip | bi-metallic - coil | other
105 |  | Temperature element sheath outside diameter : | 6 mm |  | 6 mm | [5 empty] | select | 6 mm | ¼ in | other
106 |  | Temperature element extension material : | input data |  | input data
107 |  | Temperature element extension type : | input data |  | input data
108 |  | Temperature element sensitive portion length : | input data | select | input data | select |  |  |  |  | select | mm | in
109 |  | Thermowell type (seamless) : | select |  | select | [5 empty] | select | single piece bar | single piece forged | Van Stone
110 |  | Thermowell design : | tapered |  | tapered | [5 empty] | select | tapered | straight | stepped
111 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.5 | Thermowell material : | input data |  | input data
112 |  | Thermowell process connection size : | input data | select | input data | select |  |  |  |  | select | mm | in
113 |  | Thermowell process connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF
114 |  | Thermowell process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
115 |  | Thermowell insertion length (U) : | input data | select | input data | select |  |  |  |  | select | mm | in
116 |  | Thermowell lagging extension length (T) : | input data | select | input data | select |  |  |  |  | select | mm | in
117 |  | Thermowell root diameter (A) : | input data | select | input data | select |  |  |  |  | select | mm | in
118 |  | Thermowell tip diameter (B) : | input data | select | input data | select |  |  |  |  | select | mm | in
119 |  | Thermowell bore diameter (d) : | 6,6 mm |  | 6,6 mm | [5 empty] | select | 6,6 mm | 0,26 in | other
120 |  | Thermowell tip thickness (t) : | input data | select | input data | select |  |  |  |  | select | mm | in
121 |  | Thermowell fillet radius (b) : | input data | select | input data | select |  |  |  |  | select | mm | in
122 |  | Gauge dial size : | select |  | select | [5 empty] | select | 63 mm (2,5 in) | 80 mm (3 in) | 100 mm (4 in) | 113 mm (4,5 in) | 130 mm (5 in) | 150 mm (6 in)
123 |  | Gauge range - minimum : | input data | select | input data | select |  |  |  |  | select | bar | kPa | Mpa | psi | inH2O
124 |  | Gauge range - minimum : | input data | select | input data | select |  |  |  |  | select | ºC | ºF
125 |  | Gauge range - maximum : | input data | select | input data | select |  |  |  |  | select | bar | kPa | Mpa | psi | inH2O
126 |  | Gauge range - maximum : | input data | select | input data | select |  |  |  |  | select | ºC | ºF
127 |  | Case material : | 316 stainless steel |  | 316 stainless steel | [5 empty] | select | 316 stainless steel | polymer | other
128 |  | Connection orientation : | bottom |  | bottom | [5 empty] | select | bottom | rear | 2 o'clock (side) | 9 o'clock (side) | 3 o'clock (side)
129 |  | Ring style : | bayonet ring |  | bayonet ring | [5 empty] | select | bayonet ring | crimp ring | profile ring | standoff ring | friction ring
130 |  | Ring material : | 316 stainless steel |  | 316 stainless steel | [5 empty] | select | 316 stainless steel | other
131 |  | Window material : | safety glass |  | safety glass | [5 empty] | select | ​​​​​​​safety glass | plastic
132 |  | Pointer colour : | black |  | black | [5 empty] | select | black | other
133 |  | Dial colour : | select |  | select | [5 empty] | select | white
134 |  | Pointer zero adjustment : | external |  | external | [5 empty] | select | external | other
135 |  | Performance
136 |  | Temperature gauge accuracy : | select |  | select | [5 empty] | select | Grade A (ASME B40.200) | Grade B (ASME B40.200) | Class 1 (BS EN 13190) | Class 2 (BS EN 13190)
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the ingress protection rating in IP or NEMA.
Note on C20: Specify the size of the connection to the process.
Note on C21: Select the pressure rating of the system connected.
Note on C22: Select the type of the connection to the process.
Note on C23: Specify the material of the process flange.
Note on C24: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C25: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C26: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C27: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C28: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C29: Specify the insulation material thickness of the process pipe, vessel or equipment where the thermowell or orifice plate is connected.
Note on C30: Specify the length from flange face of nozzle to inner face of equipment/line.
Note on C31: Specify the shielded length of the model supplied and figure to be used in calculations.
Note on C33: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C34: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C35: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C36: Specify any corrosive elements in the process stream.
Note on C37: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C38: Specify the temperature of the process at the minimum sizing case.
Note on C39: Specify the differential pressure of the process at the minimum sizing case.
Note on C40: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C41: Specify the temperature of the process at the maximum sizing case.
Note on C42: Specify the pressure of the process for the maximum operating case.
Note on C43: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C44: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C45: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C46: Specify the vapour actual density at the maximum sizing conditions.
Note on C47: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C49: Specify on what basis the process data submitted would occur.
Note on C50: Specify the pressure of the process for case 1.
Note on C51: Specify the temperature of the process at case 1.
Note on C52: Specify the operating velocity of the system at case 1.
Note on C53: Specify the density for case 1.
Note on C54: Specify the viscosity of the process fluid for case 1.
Note on C55: Specify the process fluid for case 1.
Note on C56: Select whether it is a liquid or vapour phase.
Note on C58: Specify on what basis the process data submitted would occur.
Note on C59: Specify the pressure of the process for case 2.
Note on C60: Specify the temperature of the process at case 2.
Note on C61: Specify the operating velocity of the system at case 2.
Note on C62: Specify the density for case 2.
Note on C63: Specify the viscosity of the process fluid for case 2.
Note on C64: Specify the process fluid for case 2.
Note on C65: Select whether it is a liquid or vapour phase.
Note on C67: Specify on what basis the process data submitted would occur.
Note on C68: Specify the pressure of the process at case 3.
Note on C69: Specify the temperature of the process at case 3.
Note on C70: Specify the operating velocity of the system at case 3.
Note on C71: Specify the density for case 3.
Note on C72: Specify the viscosity of the process fluid for case 3.
Note on C73: Specify the process fluid for case 3.
Note on C74: Select whether it is a liquid or vapour phase.
Note on C76: Specify on what basis the process data submitted would occur.
Note on C77: Specify the pressure of the process for case 4.
Note on C78: Specify the temperature of the process at case 4.
Note on C79: Specify the operating velocity of the system at case 4.
Note on C80: Specify the density for case 4.
Note on C81: Specify the viscosity of the process fluid for case 4.
Note on C82: Specify the process fluid for case 4.
Note on C83: Select whether it is a liquid or vapour phase.
Note on C85: Specify on what basis the process data submitted would occur.
Note on C86: Specify the pressure of the process for case 5.
Note on C87: Specify the temperature of the process at case 5.
Note on C88: Specify the operating velocity of the system at case 5.
Note on C89: Specify the density for case 5.
Note on C90: Specify the viscosity of the process fluid for case 5.
Note on C91: Specify the process fluid for case 5.
Note on C92: Select whether it is a liquid or vapour phase.
Note on C94: Specify on what basis the process data submitted would occur.
Note on C95: Specify the pressure of the process for case 6.
Note on C96: Specify the temperature of the process at case 6.
Note on C97: Specify the operating velocity of the system at case 6.
Note on C98: Specify the density for case 6.
Note on C99: Specify the viscosity of the process fluid for case 6.
Note on C100: Specify the process fluid for case 6.
Note on C101: Select whether it is a liquid or vapour phase.
Note on C103: Specify the model number of the body/element/sensor.
Note on C104: Select the temperature gauge element type. Default value : bi-metallic (helix)
Note on C105: Select the OD of the element to fit inside the thermowell. Default value : 6 mm
Note on C106: Specify the nipple material suitable for the environment conditions.
Note on C107: Specify the type of extension selected for the purchaser declared service conditions.
Note on C108: Specify how much of the end of the sensor is deemed the sensitive portion and hence active in measuring the temperature.
Note on C109: Select "single piece bar", "single piece forged" or "Van Stone" type thermowell of seamless construction.
Note on C110: Select "tapered", "straight" or "stepped" fabricated from a single piece bar stock. Geometry of thermowell to be in accordance with ASME PTC 19.3 TW. Default value : tapered
Note on C111: Specify the material of the thermowell suitable for the process fluids. The thermowell is a wetted part.
Note on C112: Specify the flange size that is compatible with process connection flange.
Note on C113: Select the standard flange connections. Default value : RF
Note on C114: Select the flange rating as per the piping specification.
Note on C115: Specify the length measured from the bottom of the flange to the tip of the thermowell. ASME PTC 19.3 TW uses the term "unsupported length"' with variable "L".
Note on C116: Specify the length measured from the bottom of the flange to the top of the thermowell assembly, including any nipple extension, to ensure that terminal heads attached to thermowells with extension pieces provide space for at least 80 mm (3 in) insulation
Note on C117: Specify the root diameter of the model supplied and figure to be used in calculations.
Note on C118: Specify the tip diameter of the model supplied and figure to be used in calculations.
Note on C119: Select the bore diameter and figure to be used in calculations, the standard size in industry being 6,6 mm (0,26 in). Test thermowells can be 9,8 mm (0,385 in) to allow easy insertion and removal. Default value : 6,6 mm
Note on C120: Specify the tip thickness of the model supplied and figure to be used in calculations.
Note on C121: Specify the fillet radius (b) of the model supplied and figure to be used in calculations.
Note on C122: Select the required diameter of gauge required for the application.
Note on C123: Specify the minimum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating pressure to be within 50 % to 70 % of the scale.
Note on C124: Specify the minimum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating temperature to be within 50 % to 70 % of the scale.
Note on C125: Specify the maximum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating pressure to be within 50 % to 70 % of the scale.
Note on C126: Specify the maximum gauge range suitable from the allowable ranges in the relevant code and aiming for normal operating temperature to be within 50 % to 70 % of the scale.
Note on C127: Specify the case material from which the case is to be manufactured. Default value : 316 stainless steel
Note on C128: Select the process connection position in relation to the pressure gauge. Default value : bottom
Note on C129: Select the type of ring style. Default value : bayonet ring
Note on C130: Specify the ring material from which the ring is to be manufactured. Default value : 316 stainless steel
Note on C131: Select the material to be supplied for the gauge window. Default value : safety glass
Note on C132: Select the required colour of the pointer. Default value : black
Note on C133: Select the required colour of the dial.
Note on C134: Select whether the pointer requires the function to adjust the zero setting externally. Default value : external
Note on C136: Select the class or grade tolerances as per the applicable code being used.
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS TempTrans
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Temperature Transmitter | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
19 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
20 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
21 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
22 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
23 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
24 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
25 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
26 |  | Installation conditions
27 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
28 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
29 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
30 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
31 |  | Process connection material type : | input data |  | input data
32 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
33 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
34 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
35 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
36 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
37 | 7.2.1.3 | Insulation thickness : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
38 |  | Connection length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
39 |  | Thermowell shielded length (Lo) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
40 |  | Operating conditions
41 |  | Process fluid(s) : | input data |  | input data
42 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
43 |  | Service description : | input data |  | input data
44 |  | Process fluid corrosive compounds : | input data |  | input data
45 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
46 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
47 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
48 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
49 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
50 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
51 |  | Maximum operating liquid specific gravity : | input data |  | input data
52 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
53 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
54 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
55 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
56 |  | TW Case 1
57 |  | Case 1 description : | input data |  | input data
58 |  | Case 1 pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
59 |  | Case 1 temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
60 |  | Case 1 velocity : | input data | m/s | input data | m/s
61 |  | Case 1 density : | input data | kg/m³ | input data | kg/m³
62 |  | Case 1 viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
63 |  | Case 1 process fluid : | input data |  | input data
64 |  | Case 1 process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
65 |  | TW Case 2
66 |  | Case 2 description : | input data |  | input data
67 |  | Case 2 pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
68 |  | Case 2 temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
69 |  | Case 2 velocity : | input data | m/s | input data | m/s
70 |  | Case 2 density : | input data | kg/m³ | input data | kg/m³
71 |  | Case 2 viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
72 |  | Case 2 process fluid : | input data |  | input data
73 |  | Case 2 process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
74 |  | TW Case 3
75 |  | Case 3 description : | input data |  | input data
76 |  | Case 3 pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
77 |  | Case 3 temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
78 |  | Case 3 velocity : | input data | m/s | input data | m/s
79 |  | Case 3 density : | input data | kg/m³ | input data | kg/m³
80 |  | Case 3 viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
81 |  | Case 3 process fluid : | input data |  | input data
82 |  | Case 3 process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
83 |  | TW Case 4
84 |  | Case 4 description : | input data |  | input data
85 |  | Case 4 pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
86 |  | Case 4 temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
87 |  | Case 4 velocity : | input data | m/s | input data | m/s
88 |  | Case 4 density : | input data | kg/m³ | input data | kg/m³
89 |  | Case 4 viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
90 |  | Case 4 process fluid : | input data |  | input data
91 |  | Case 4 process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
92 |  | TW Case 5
93 |  | Case 5 description : | input data |  | input data
94 |  | Case 5 pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
95 |  | Case 5 temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
96 |  | Case 5 velocity : | input data | m/s | input data | m/s
97 |  | Case 5 density : | input data | kg/m³ | input data | kg/m³
98 |  | Case 5 viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
99 |  | Case 5 process fluid : | input data |  | input data
100 |  | Case 5 process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
101 |  | TW Case 6
102 |  | Case 6 description : | input data |  | input data
103 |  | Case 6 pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
104 |  | Case 6 temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
105 |  | Case 6 velocity : | input data | m/s | input data | m/s
106 |  | Case 6 density : | input data | kg/m³ | input data | kg/m³
107 |  | Case 6 viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
108 |  | Case 6 process fluid : | input data |  | input data
109 |  | Case 6 process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
110 |  | Body/element/sensor
111 |  | Body/element/sensor manufacturer model number : | input data |  | input data
112 |  | Temperature element type : | select |  | select | [5 empty] | select | RTD Pt-100 3-wire | RTD Pt-100 4-wire | TC type J | TC type B | TC type E | TC type K | TC type N | TC type R | TC type S | TC type T | TC type C
113 |  | Temperature element tolerance class : | select |  | select | [5 empty] | select | Class AA (IEC 60751) | Class BB (IEC 60751) | Class A | Class B (IEC 60751) | Grade A (ASTM E1137/E1137M) | Grade B (ASTM E1137/E1137M) | Class 1 (IEC 60584) | Class 2 (IEC 60584) | special tolerance (ASTM E230/E230M) | standard tolerance (ASTM E230/E230M)
114 |  | Temperature element sheath material : | input data |  | input data
115 | 6.1.9 | Temperature element - simplex or duplex : | duplex |  | duplex | [5 empty] | select | T1: duplex; T2: simplex
116 |  | Temperature element sheath outside diameter : | 6 mm |  | 6 mm | [5 empty] | select | T1: 6 mm; T2: ¼ in; T3: other
117 |  | Temperature element extension material : | input data |  | input data
118 |  | Temperature element extension type : | input data |  | input data
119 |  | Temperature element number of terminals : | 6 |  | 6 | [5 empty] | select | T1: 6; T2: 8
120 |  | Thermocouple tip : | ungrounded |  | ungrounded | [5 empty] | select | T1: grounded; T2: ungrounded
121 |  | Thermowell type (seamless) : | select |  | select | [5 empty] | select | T1: single piece bar; T2: single piece forged; T3: Van Stone
122 |  | Thermowell design : | tapered |  | tapered | [5 empty] | select | T1: tapered; T2: straight; T3: stepped
123 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.5 | Thermowell material : | input data |  | input data
124 |  | Thermowell process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
125 |  | Thermowell process connection type : | RF |  | RF | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
126 |  | Thermowell process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
127 |  | Thermowell insertion length (U) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
128 |  | Thermowell lagging extension length (T) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
129 |  | Thermowell root diameter (A) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
130 |  | Thermowell tip diameter (B) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
131 |  | Thermowell bore diameter (d) : | 6,6 mm |  | 6,6 mm | [5 empty] | select | T1: 6,6 mm; T2: 0,26 in; T3: other
132 |  | Thermowell tip thickness (t) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
133 |  | Thermowell fillet radius (b) : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
134 |  | Pipe clamp material : | input data |  | input data
135 |  | Transmitter
136 |  | Transmitter model number : | input data |  | input data
137 |  | Transmitter enclosure material : | input data |  | input data
138 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
139 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
140 | 6.1.9 | Hot swap : | select |  | select | [5 empty] | select | T1: yes; T2: no
141 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
142 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
143 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
144 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
145 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
146 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
147 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
148 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
149 |  | Protocol version : | input data |  | input data
150 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
151 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
152 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
153 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
154 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
155 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
156 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
157 |  | Performance
158 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
159 |  | Long term drift : | input data |  | input data
160 |  | Long term stability : | input data |  | input data
161 |  | Accessories
162 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
163 |  | Mounting bracket : | select |  | select | [5 empty] | select | T1: yes; T2: no
164 |  | Mounting bracket material : | select |  | select | [5 empty] | select | T1: 316 SS; T2: other
165 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
166 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the required project painting durability level.
Note on C19: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C20: Select the ingress protection rating in IP or NEMA.
Note on C21: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C22: Select the code to be followed for the hazardous area classification.
Note on C23: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C24: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C25: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C27: Select the pipe schedule in accordance with the pipe specification.
Note on C28: Specify the size of the connection to the process.
Note on C29: Select the pressure rating of the system connected.
Note on C30: Select the type of the connection to the process.
Note on C31: Specify the material of the process flange.
Note on C32: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C33: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C34: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C35: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C36: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C37: Specify the insulation material thickness of the process pipe, vessel or equipment where the thermowell or orifice plate is connected.
Note on C38: Specify the length from flange face of nozzle to inner face of equipment/line.
Note on C39: Specify the shielded length of the model supplied and figure to be used in calculations.
Note on C41: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C42: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C43: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C44: Specify any corrosive elements in the process stream.
Note on C45: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C46: Specify the temperature of the process at the minimum sizing case.
Note on C47: Specify the differential pressure of the process at the minimum sizing case.
Note on C48: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C49: Specify the temperature of the process at the maximum sizing case.
Note on C50: Specify the pressure of the process for the maximum operating case.
Note on C51: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C52: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C53: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C54: Specify the vapour actual density at the maximum sizing conditions.
Note on C55: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C57: Specify on what basis the process data submitted would occur.
Note on C58: Specify the pressure of the process for case 1.
Note on C59: Specify the temperature of the process at case 1.
Note on C60: Specify the operating velocity of the system at case 1.
Note on C61: Specify the density for case 1.
Note on C62: Specify the viscosity of the process fluid for case 1.
Note on C63: Specify the process fluid for case 1.
Note on C64: Select whether it is a liquid or vapour phase.
Note on C66: Specify on what basis the process data submitted would occur.
Note on C67: Specify the pressure of the process for case 2.
Note on C68: Specify the temperature of the process at case 2.
Note on C69: Specify the operating velocity of the system at case 2.
Note on C70: Specify the density for case 2.
Note on C71: Specify the viscosity of the process fluid for case 2.
Note on C72: Specify the process fluid for case 2.
Note on C73: Select whether it is a liquid or vapour phase.
Note on C75: Specify on what basis the process data submitted would occur.
Note on C76: Specify the pressure of the process at case 3.
Note on C77: Specify the temperature of the process at case 3.
Note on C78: Specify the operating velocity of the system at case 3.
Note on C79: Specify the density for case 3.
Note on C80: Specify the viscosity of the process fluid for case 3.
Note on C81: Specify the process fluid for case 3.
Note on C82: Select whether it is a liquid or vapour phase.
Note on C84: Specify on what basis the process data submitted would occur.
Note on C85: Specify the pressure of the process for case 4.
Note on C86: Specify the temperature of the process at case 4.
Note on C87: Specify the operating velocity of the system at case 4.
Note on C88: Specify the density for case 4.
Note on C89: Specify the viscosity of the process fluid for case 4.
Note on C90: Specify the process fluid for case 4.
Note on C91: Select whether it is a liquid or vapour phase.
Note on C93: Specify on what basis the process data submitted would occur.
Note on C94: Specify the pressure of the process for case 5.
Note on C95: Specify the temperature of the process at case 5.
Note on C96: Specify the operating velocity of the system at case 5.
Note on C97: Specify the density for case 5.
Note on C98: Specify the viscosity of the process fluid for case 5.
Note on C99: Specify the process fluid for case 5.
Note on C100: Select whether it is a liquid or vapour phase.
Note on C102: Specify on what basis the process data submitted would occur.
Note on C103: Specify the pressure of the process for case 6.
Note on C104: Specify the temperature of the process at case 6.
Note on C105: Specify the operating velocity of the system at case 6.
Note on C106: Specify the density for case 6.
Note on C107: Specify the viscosity of the process fluid for case 6.
Note on C108: Specify the process fluid for case 6.
Note on C109: Select whether it is a liquid or vapour phase.
Note on C111: Specify the model number of the body/element/sensor.
Note on C112: Select the temperature element type required.
Note on C113: Select the class or grade tolerances as per the applicable standard.
Note on C114: Specify the sheath material (metal or others) are to be suitable for the specified operating environment.
Note on C115: Select whether a single or duplex element is required. The specification mandates duplex hence only single option and any deviation would need to be stated in notes field. Default value : duplex
Note on C116: Select the OD of the element to fit inside the thermowell. Default value : 6 mm
Note on C117: Specify the nipple material suitable for the environment conditions.
Note on C118: Specify the type of extension selected for the purchaser declared service conditions.
Note on C119: Select the terminal block to cater for duplex installations and selection from six or eight terminals. Minimum 3-wire RTD. Default value : 6
Note on C120: Select "Grounded" or "Ungrounded". Default value : ungrounded
Note on C121: Select "single piece bar", "single piece forged" or "Van Stone" type thermowell of seamless construction.
Note on C122: Select "tapered", "straight" or "stepped" fabricated from a single piece bar stock. Geometry of thermowell to be in accordance with ASME PTC 19.3 TW. Default value : tapered
Note on C123: Specify the material of the thermowell suitable for the process fluids. The thermowell is a wetted part.
Note on C124: Specify the flange size that is compatible with process connection flange.
Note on C125: Select the standard flange connections. Default value : RF
Note on C126: Select the flange rating as per the piping specification.
Note on C127: Specify the length measured from the bottom of the flange to the tip of the thermowell. ASME PTC 19.3 TW uses the term "unsupported length"' with variable "L".
Note on C128: Specify the length measured from the bottom of the flange to the top of the thermowell assembly, including any nipple extension, to ensure that terminal heads attached to thermowells with extension pieces provide space for at least 80 mm (3 in) insulation
Note on C129: Specify the root diameter of the model supplied and figure to be used in calculations.
Note on C130: Specify the tip diameter of the model supplied and figure to be used in calculations.
Note on C131: Select the bore diameter and figure to be used in calculations, the standard size in industry being 6,6 mm (0,26 in). Test thermowells can be 9,8 mm (0,385 in) to allow easy insertion and removal. Default value : 6,6 mm
Note on C132: Specify the tip thickness of the model supplied and figure to be used in calculations.
Note on C133: Specify the fillet radius (b) of the model supplied and figure to be used in calculations.
Note on C134: Specify the pipe clamp material.
Note on C136: Specify the model number for the transmitter only.
Note on C137: Specify the material offered to meet the minimum requirements.
Note on C138: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C139: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C140: Select whether the transmitter is able to switch to redundant element automatically in operation.
Note on C141: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C142: Select the required signal type.
Note on C143: Select the type of power supply to the instrument. Default value : hardwired
Note on C144: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C145: Select the type of connection for the cable to the transmitter head.
Note on C146: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C147: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C148: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C149: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C150: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C151: Specify the bespoke range when supplier non-standard calibration is required.
Note on C152: Specify the lowest measured point for the instrument.
Note on C153: Specify the highest measured point for the instrument.
Note on C154: Select where the functionality is to be located.
Note on C155: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C156: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C158: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C159: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C160: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C162: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C163: Select "yes" When remote mount or "no" if direct mount.
Note on C164: Select the mounting bracket material. Minimum material 316 stainless steel but "other" can be selected when more suitable.
Note on C165: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C166: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS TempTransClamp
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Temperature Transmitter Clamp-on | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
19 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
20 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
21 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
22 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
23 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
24 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
25 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
26 |  | Installation conditions
27 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
28 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
29 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
30 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
31 |  | Process connection material type : | input data |  | input data
32 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
33 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
34 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
35 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
36 | 7.2.1.3 | Insulation thickness : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
37 |  | Operating conditions
38 |  | Process fluid(s) : | input data |  | input data
39 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
40 |  | Service description : | input data |  | input data
41 |  | Process fluid corrosive compounds : | input data |  | input data
42 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
43 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
44 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
45 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
46 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
47 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
48 |  | Maximum operating liquid specific gravity : | input data |  | input data
49 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
50 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
51 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
52 |  | Body/element/sensor
53 |  | Body/element/sensor manufacturer model number : | input data |  | input data
54 |  | Temperature element type : | select |  | select | [5 empty] | select | RTD Pt-100 3-wire | RTD Pt-100 4-wire | TC type J | TC type B | TC type E | TC type K | TC type N | TC type R | TC type S | TC type T | TC type C
55 |  | Temperature element tolerance class : | select |  | select | [5 empty] | select | Class AA (IEC 60751) | Class BB (IEC 60751) | Class A | Class B (IEC 60751) | Grade A (ASTM E1137/E1137M) | Grade B (ASTM E1137/E1137M) | Class 1 (IEC 60584) | Class 2 (IEC 60584) | special tolerance (ASTM E230/E230M) | standard tolerance (ASTM E230/E230M)
56 |  | Temperature element sheath material : | input data |  | input data
57 | 6.1.9 | Temperature element - simplex or duplex : | duplex |  | duplex | [5 empty] | select | T1: duplex; T2: simplex
58 |  | Temperature element sheath outside diameter : | 6 mm |  | 6 mm | [5 empty] | select | T1: 6 mm; T2: ¼ in; T3: other
59 |  | Temperature element extension material : | input data |  | input data
60 |  | Temperature element extension type : | input data |  | input data
61 |  | Temperature element number of terminals : | 6 |  | 6 | [5 empty] | select | T1: 6; T2: 8
62 |  | Pipe clamp material : | input data |  | input data
63 |  | Transmitter
64 |  | Transmitter model number : | input data |  | input data
65 |  | Transmitter enclosure material : | input data |  | input data
66 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
67 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
68 | 6.1.9 | Hot swap : | select |  | select | [5 empty] | select | T1: yes; T2: no
69 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
70 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
71 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
72 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
73 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
74 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
75 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
76 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
77 |  | Protocol version : | input data |  | input data
78 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
79 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
80 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
81 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
82 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
83 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
84 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
85 |  | Performance
86 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
87 |  | Long term drift : | input data |  | input data
88 |  | Long term stability : | input data |  | input data
89 |  | Accessories
90 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
91 |  | Mounting bracket : | select |  | select | [5 empty] | select | T1: yes; T2: no
92 |  | Mounting bracket material : | select |  | select | [5 empty] | select | T1: 316 SS; T2: other
93 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
94 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the required project painting durability level.
Note on C19: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C20: Select the ingress protection rating in IP or NEMA.
Note on C21: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C22: Select the code to be followed for the hazardous area classification.
Note on C23: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C24: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C25: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C27: Select the pipe schedule in accordance with the pipe specification.
Note on C28: Specify the size of the connection to the process.
Note on C29: Select the pressure rating of the system connected.
Note on C30: Select the type of the connection to the process.
Note on C31: Specify the material of the process flange.
Note on C32: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C33: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C34: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C35: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C36: Specify the insulation material thickness of the process pipe, vessel or equipment where the thermowell or orifice plate is connected.
Note on C38: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C39: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C40: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C41: Specify any corrosive elements in the process stream.
Note on C42: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C43: Specify the temperature of the process at the minimum sizing case.
Note on C44: Specify the differential pressure of the process at the minimum sizing case.
Note on C45: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C46: Specify the temperature of the process at the maximum sizing case.
Note on C47: Specify the pressure of the process for the maximum operating case.
Note on C48: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C49: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C50: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C51: Specify the vapour actual density at the maximum sizing conditions.
Note on C53: Specify the model number of the body/element/sensor.
Note on C54: Select the temperature element type required.
Note on C55: Select the class or grade tolerances as per the applicable standard.
Note on C56: Specify the sheath material (metal or others) are to be suitable for the specified operating environment.
Note on C57: Select whether a single or duplex element is required. The specification mandates duplex hence only single option and any deviation would need to be stated in notes field. Default value : duplex
Note on C58: Select the OD of the element to fit inside the thermowell. Default value : 6 mm
Note on C59: Specify the nipple material suitable for the environment conditions.
Note on C60: Specify the type of extension selected for the purchaser declared service conditions.
Note on C61: Select the terminal block to cater for duplex installations and selection from six or eight terminals. Minimum 3-wire RTD. Default value : 6
Note on C62: Specify the pipe clamp material.
Note on C64: Specify the model number for the transmitter only.
Note on C65: Specify the material offered to meet the minimum requirements.
Note on C66: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C67: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C68: Select whether the transmitter is able to switch to redundant element automatically in operation.
Note on C69: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C70: Select the required signal type.
Note on C71: Select the type of power supply to the instrument. Default value : hardwired
Note on C72: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C73: Select the type of connection for the cable to the transmitter head.
Note on C74: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C75: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C76: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C77: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C78: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C79: Specify the bespoke range when supplier non-standard calibration is required.
Note on C80: Specify the lowest measured point for the instrument.
Note on C81: Specify the highest measured point for the instrument.
Note on C82: Select where the functionality is to be located.
Note on C83: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C84: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C86: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C87: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C88: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C90: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C91: Select "yes" When remote mount or "no" if direct mount.
Note on C92: Select the mounting bracket material. Minimum material 316 stainless steel but "other" can be selected when more suitable.
Note on C93: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C94: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowOrifice
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Orifice | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Instrumentation type : | select |  | select | [5 empty] | select | restriction orifice | orifice plate (square edge concentric) | orifice plate (conical entrance) | orifice plate (quarter circle) | orifice plate (eccentric) | restriction orifice paddle type | orifice plate paddle type (square edge concentric) | orifice plate paddle type (conical entrance) | orifice plate paddle type (quarter circle) | orifice plate paddle type (eccentric) | multi-hole orifice | integral orifice run
5 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
6 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
7 | 4.1.2.1 | Tag number : | input data |  | input data
8 |  | Service description : | input data |  | input data
9 |  | Manufacturer : | input data |  | input data
10 | 8.3.4.1 | Model number : | input data |  | input data
11 |  | Equipment manufacturer serial number : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
13 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
14 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
15 |  | P&ID number : | input data |  | input data
16 |  | Line or equipment number : | input data |  | input data
17 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
19 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
20 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
21 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
22 |  | Installation conditions
23 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
24 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
25 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
26 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
27 |  | Upstream (high-side) connection orientation : | input data |  | input data
28 |  | Upstream (high-side) material type : | input data |  | input data
29 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
30 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
31 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
32 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
33 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
34 | 7.2.1.3 | Insulation thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
35 |  | Operating conditions
36 |  | Process fluid(s) : | input data |  | input data
37 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
38 |  | Service description : | input data |  | input data
39 |  | Process fluid corrosive compounds : | input data |  | input data
40 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
41 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
42 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
43 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa
44 |  | Process fluid plugging : | no |  | no | [5 empty] | select | yes | no
45 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
46 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
47 |  | Minimum operating velocity : | input data | m/s | input data | m/s
48 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
49 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
50 |  | Minimum operating liquid specific gravity : | input data |  | input data
51 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
52 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
53 |  | Minimum operating vapour compressibility factor : | input data |  | input data
54 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
55 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
56 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
57 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
58 |  | Normal operating velocity : | input data | m/s | input data | m/s
59 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
60 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
61 |  | Normal operating liquid specific gravity : | input data |  | input data
62 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
63 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
64 |  | Normal operating vapour compressibility factor : | input data |  | input data
65 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
66 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
67 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
68 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
69 |  | Maximum operating velocity : | input data | m/s | input data | m/s
70 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
71 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
72 |  | Maximum operating liquid specific gravity : | input data |  | input data
73 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
74 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
75 |  | Maximum operating vapour compressibility factor : | input data |  | input data
76 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
77 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
78 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
79 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
80 |  | Body/element/sensor
81 |  | Body material : | input data |  | input data
82 |  | Orifice bore diameter : | input data | select | input data | select |  |  |  |  | select | mm | in
83 |  | Beta ratio (d/D) : | input data |  | input data
84 |  | Minimum differential pressure: | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
85 |  | Maximum differential pressure : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
86 |  | Orifice vent or drain hole : | not applicable |  | not applicable | [5 empty] | select | vent only | drain only | both | not applicable
87 |  | Orifice plate thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
88 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
89 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
90 |  | Integral orifice run
91 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
92 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
93 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
94 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
95 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
96 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
97 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
98 |  | Downstream (bottom-side) material type : | input data |  | input data
99 |  | Flange material : | input data |  | input data
100 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
101 |  | End connection flange type : | select |  | select | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
102 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
103 |  | Pressure tap number : | select |  | select | [5 empty] | select | 2 | 3 | 4
104 |  | Pressure tap size : | select |  | select | [5 empty] | select | ½ in | 1 in
105 |  | Pressure tap connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | NPT(F)
106 |  | Pressure tap rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
107 |  | Pressure tap orientation : | input data | deg | input data | deg
108 |  | Quick change fitting (option)
109 |  | Manufacturer : | input data |  | input data
110 |  | Manufacturer model number : | input data |  | input data
111 |  | Quick change fitting rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
112 |  | Removal under line pressure : | select |  | select | [5 empty] | select | yes | no
113 |  | Pressure containing material : | input data |  | input data
114 |  | Internals material : | input data |  | input data
115 |  | Gasket material : | input data |  | input data
116 |  | Taps number : | select |  | select | [5 empty] | select | 2 | 4
117 |  | Pressure tap size : | select |  | select | [5 empty] | select | ½ in | 1 in
118 |  | Pressure tap connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | NPT(F)
119 |  | Pressure tap rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
120 |  | Pressure tap orientation : | input data | deg | input data | deg
Note on C4: Select the instrument type (technology) to be purchased.
Note on C5: Select the code compliance for the region where the instrument is to be installed.
Note on C6: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C7: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C8: Specify a functional description of the tag.
Note on C9: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C10: Specify the model number of the offered instrument assembly/unit.
Note on C11: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C12: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C13: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C14: Select the location of the facility where the equipment is to be permanently installed.
Note on C15: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C16: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C17: Specify as per process data.
Note on C18: Specify as per process data.
Note on C19: Select the units to be used, either "normal" or "standard".
Note on C20: Specify the temperature to be used for base units.
Note on C21: Specify the pressure to be used to support the base units.
Note on C23: Select the pipe schedule in accordance with the pipe specification.
Note on C24: Specify the process line size to support sizing and selection by the supplier.
Note on C25: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C26: Select the instrument process connection compatible with that declared by the purchaser.
Note on C27: Specify the orientation of the inlet to the instrument or insertion point.
Note on C28: Specify the material which the instrument connects to on the upstream face.
Note on C29: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C30: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C31: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C32: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C33: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C34: Specify the insulation material thickness of the process pipe, vessel or equipment where the thermowell or orifice plate is connected.
Note on C36: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C37: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C38: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C39: Specify any corrosive elements in the process stream.
Note on C40: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C41: Specify the input details to support sizing.
Note on C42: Select whether the instrument could see a vacuum.
Note on C43: Specify the vapour pressure of the flowing fluid.
Note on C44: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C45: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C46: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C47: Specify the operating velocity of the system at the minimum sizing case.
Note on C48: Specify the temperature of the process at the minimum sizing case.
Note on C49: Specify the differential pressure of the process at the minimum sizing case.
Note on C50: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C51: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C52: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C53: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C54: Specify the vapour actual density at minimum sizing conditions.
Note on C55: Specify the vapour viscosity at minimum sizing conditions.
Note on C56: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C57: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C58: Specify the operating velocity of the system at the normal sizing case.
Note on C59: Specify the temperature of the process at the minimum sizing case.
Note on C60: Specify the pressure of the process for the normal operating case.
Note on C61: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C62: Specify the viscosity of the process fluid at the normal sizing case.
Note on C63: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C64: Specify the vapour compressibility factor at normal sizing conditions.
Note on C65: Specify the vapour actual density at normal sizing conditions.
Note on C66: Specify the vapour viscosity at normal sizing conditions.
Note on C67: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C68: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C69: Specify the operating velocity of the system at the maximum sizing case.
Note on C70: Specify the temperature of the process at the maximum sizing case.
Note on C71: Specify the pressure of the process for the maximum operating case.
Note on C72: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C73: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C74: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C75: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C76: Specify the vapour actual density at the maximum sizing conditions.
Note on C77: Specify the vapour viscosity at the maximum sizing conditions.
Note on C78: Specify the worst case pressure loss that the system can accept.
Note on C79: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C81: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C82: Specify the estimated dimension. Supplier to confirm the final diameter after approval of the sizing calculations.
Note on C83: Specify the ratio of d/D after orifice sizing calculations.
Note on C84: Specify the differential pressure associated with the minimum flow rates of the fluid being measured.
Note on C85: Specify the differential pressure associated with the maximum flow rates of the fluid being measured.
Note on C86: Select the orifice vent or drain hole. Select "not applicable" when not required. Default value : not applicable
Note on C87: Specify the plate thickness. Follow the recommendations from ISO 5167-2 to ensure the minimum thickness is met.
Note on C88: Specify the lowest measured point for the instrument.
Note on C89: Specify the highest measured point for the instrument.
Note on C91: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C92: Select the nut material as detailed in IOGP S-563.
Note on C93: Select the pipe schedule in accordance with the pipe specification.
Note on C94: Specify the process line size downstream to be declared to support sizing and selection by the supplier.
Note on C95: Select the pressure rating of the system connected.
Note on C96: Select the process connection to the system.
Note on C97: Specify the orientation of the inlet or insertion point of the instrument.
Note on C98: Specify the material for the instrument to connect to on the downstream face.
Note on C99: Specify the flange material to be compatible with process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, select "not applicable".
Note on C100: Specify the size of the connection to the process line or equipment.
Note on C101: Select the flange type for the selected instrument to be declared, normally ASME B16.5 RF.
Note on C102: Select the flange rating to match the rating of the system to which it is connected.
Note on C103: Select the number of pressure taps. The default number is normally 2.
Note on C104: Select the size for the differential pressure sensing lines. The default value is normally 1 in.
Note on C105: Select the pressure tap connection type. The default type is normally RF.
Note on C106: Select the pressure rating of the process connection.
Note on C107: Specify the orientation from the vertical plane e.g. when installed vertically, the orientation will be 0 deg.
Note on C109: Specify the manufacturer. It can be third-party party supply.
Note on C110: Specify the model number for quick change fitting assembly.
Note on C111: Select the rating of the quick change fitting unit to be supplied.
Note on C112: Select "yes" for change of orifice without interruption to service. Select "no" when the isolation and depressurization of the holder is required.
Note on C113: Specify all components subject to the line pressure, e.g. body, bonnet.
Note on C114: Specify the internals material of the quick change fitting. Input "not applicable" when not required.
Note on C115: Specify the O-ring material to meet the specified process requirements, and when ED then relevant type.
Note on C116: Select the number of tapping points for the differential pressure transmitter.
Note on C117: Select the connection size for the differential pressure sensing lines. The default value is normally 1 in.
Note on C118: Select the pressure tap connection type. The default type is normally RF.
Note on C119: Select the pressure rating of the process connection. The default value is normally Cl-150.
Note on C120: Specify the orientation from the vertical plane. When installed vertically, the orientation will be 0 deg.
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowPitot
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Pitot | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
23 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
24 |  | Fire safe design : | no |  | no | [5 empty] | select | yes | no
25 |  | Installation conditions
26 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
27 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
28 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
29 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
30 |  | Upstream (high-side) connection orientation : | input data |  | input data
31 |  | Upstream (high-side) material type : | input data |  | input data
32 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
33 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
34 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
35 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
36 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
37 |  | Downstream (bottom-side) material type : | input data |  | input data
38 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
39 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
40 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
41 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
42 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
43 |  | Operating conditions
44 |  | Process fluid(s) : | input data |  | input data
45 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
46 |  | Service description : | input data |  | input data
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
49 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
50 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
51 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa
52 |  | Process fluid plugging : | no |  | no | [5 empty] | select | yes | no
53 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
54 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
55 |  | Minimum operating velocity : | input data | m/s | input data | m/s
56 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
57 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
58 |  | Minimum operating liquid specific gravity : | input data |  | input data
59 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
60 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
61 |  | Minimum operating vapour compressibility factor : | input data |  | input data
62 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
63 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
64 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
65 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
66 |  | Normal operating velocity : | input data | m/s | input data | m/s
67 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
68 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
69 |  | Normal operating liquid specific gravity : | input data |  | input data
70 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
71 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
72 |  | Normal operating vapour compressibility factor : | input data |  | input data
73 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
74 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
75 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
76 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
77 |  | Maximum operating velocity : | input data | m/s | input data | m/s
78 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
79 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
80 |  | Maximum operating liquid specific gravity : | input data |  | input data
81 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
82 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
83 |  | Maximum operating vapour compressibility factor : | input data |  | input data
84 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
85 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
86 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
87 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
88 |  | Body/element/sensor
89 |  | Body/element/sensor manufacturer model number : | input data |  | input data
90 |  | Body material : | input data |  | input data
91 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
92 |  | Flange material : | input data |  | input data
93 |  | Pitot type : | select |  | select | [5 empty] | select | averaging pitot (retractable) | averaging pitot
94 |  | Minimum differential pressure: | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
95 |  | Maximum differential pressure : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
96 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
97 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
98 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
99 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
100 |  | Interface gasket material : | input data |  | input data
101 |  | Insertion assembly
102 |  | Process connection nominal size : | input data |  | input data
103 |  | Process connection nominal rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
104 |  | Process connection termination type : | input data |  | input data
105 |  | Isolation valve style : | input data |  | input data
106 |  | Valve nominal pressure rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
107 |  | Valve body material : | input data |  | input data
108 |  | Valve seat material : | input data |  | input data
109 |  | Packing material : | input data |  | input data
110 |  | Transmitter
111 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | integrated | remote
112 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
113 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
114 |  | Performance
115 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
116 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | mm | %
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C23: Select the nut material as detailed in IOGP S-563.
Note on C24: Select whether a fire safe design is required for the seals for both element extraction and isolation valving. Default value : no
Note on C26: Select the pipe schedule in accordance with the pipe specification.
Note on C27: Specify the process line size to support sizing and selection by the supplier.
Note on C28: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C29: Select the instrument process connection compatible with that declared by the purchaser.
Note on C30: Specify the orientation of the inlet to the instrument or insertion point.
Note on C31: Specify the material which the instrument connects to on the upstream face.
Note on C32: Select the pipe schedule in accordance with the pipe specification.
Note on C33: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C34: Select the pressure rating of the system connected.
Note on C35: Select the process connection to the system.
Note on C36: Specify the orientation of the inlet or insertion point of the instrument.
Note on C37: Specify the material which the instrument connects to on the downstream face.
Note on C38: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C39: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C40: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C41: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C42: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C44: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C45: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C46: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C47: Specify any corrosive elements in the process stream.
Note on C48: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C49: Specify the input details to support sizing.
Note on C50: Select whether the instrument could see a vacuum.
Note on C51: Specify the vapour pressure of the flowing fluid.
Note on C52: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C53: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C54: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C55: Specify the operating velocity of the system at the minimum sizing case.
Note on C56: Specify the temperature of the process at the minimum sizing case.
Note on C57: Specify the differential pressure of the process at the minimum sizing case.
Note on C58: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C59: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C60: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C61: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C62: Specify the vapour actual density at minimum sizing conditions.
Note on C63: Specify the vapour viscosity at minimum sizing conditions.
Note on C64: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C65: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C66: Specify the operating velocity of the system at the normal sizing case.
Note on C67: Specify the temperature of the process at the minimum sizing case.
Note on C68: Specify the pressure of the process for the normal operating case.
Note on C69: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C70: Specify the viscosity of the process fluid at the normal sizing case.
Note on C71: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C72: Specify the vapour compressibility factor at normal sizing conditions.
Note on C73: Specify the vapour actual density at normal sizing conditions.
Note on C74: Specify the vapour viscosity at normal sizing conditions.
Note on C75: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C76: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C77: Specify the operating velocity of the system at the maximum sizing case.
Note on C78: Specify the temperature of the process at the maximum sizing case.
Note on C79: Specify the pressure of the process for the maximum operating case.
Note on C80: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C81: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C82: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C83: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C84: Specify the vapour actual density at the maximum sizing conditions.
Note on C85: Specify the vapour viscosity at the maximum sizing conditions.
Note on C86: Specify the worst case pressure loss that the system can accept.
Note on C87: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C89: Specify the model number of the body/element/sensor.
Note on C90: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C91: Select the material to be selected for the sensor.
Note on C92: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C93: Select the type of pitot tube for the service conditions supplied.
Note on C94: Specify the differential pressure associated with the minimum flow rates of the fluid being measured.
Note on C95: Specify the differential pressure associated with the maximum flow rates of the fluid being measured.
Note on C96: Specify the selected instrument body size.
Note on C97: Specify the size of the connection to the process line or equipment.
Note on C98: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C99: Select the flange rating to match the rating of the system to which it is connected.
Note on C100: Specify the material of the interface gasket
Note on C102: Specify the process connection nominal size for the insertion assembly.
Note on C103: Select the rating of the insertion assembly.
Note on C104: Specify the type of connection between the insertion assembly and the body.
Note on C105: Specify the design of isolation supplied.
Note on C106: Select the nominal pressure rating of the valve.
Note on C107: Specify the valve body material.
Note on C108: Specify the seat material.
Note on C109: Specify the details of the material used in the valve packing.
Note on C111: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C112: Specify the lowest measured point for the instrument.
Note on C113: Specify the highest measured point for the instrument.
Note on C115: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C116: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowVA
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Variable Area | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Installation conditions
22 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
23 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
24 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
25 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
26 |  | Upstream (high-side) connection orientation : | input data |  | input data
27 |  | Upstream (high-side) material type : | input data |  | input data
28 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
29 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
30 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
31 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
32 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
33 |  | Downstream (bottom-side) material type : | input data |  | input data
34 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
35 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
36 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
37 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
38 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
39 |  | Operating conditions
40 |  | Process fluid(s) : | input data |  | input data
41 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
42 |  | Service description : | input data |  | input data
43 |  | Process fluid corrosive compounds : | input data |  | input data
44 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
45 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
46 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
47 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa
48 |  | Process fluid plugging : | no |  | no | [5 empty] | select | yes | no
49 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
50 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
51 |  | Minimum operating velocity : | input data | m/s | input data | m/s
52 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
53 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
54 |  | Minimum operating liquid specific gravity : | input data |  | input data
55 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
56 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
57 |  | Minimum operating vapour compressibility factor : | input data |  | input data
58 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
59 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
60 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
61 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
62 |  | Normal operating velocity : | input data | m/s | input data | m/s
63 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
64 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
65 |  | Normal operating liquid specific gravity : | input data |  | input data
66 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
67 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
68 |  | Normal operating vapour compressibility factor : | input data |  | input data
69 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
70 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
71 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
72 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
73 |  | Maximum operating velocity : | input data | m/s | input data | m/s
74 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
75 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
76 |  | Maximum operating liquid specific gravity : | input data |  | input data
77 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
78 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
79 |  | Maximum operating vapour compressibility factor : | input data |  | input data
80 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
81 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
82 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
83 |  | Body/element/sensor
84 |  | Body/element/sensor manufacturer model number : | input data |  | input data
85 |  | Body material : | input data |  | input data
86 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
87 |  | VA meter type : | metal type |  | metal type | [5 empty] | select | direct reading type | metal type
88 |  | Float type : | input data |  | input data
89 |  | Scale design : | percentage |  | percentage | [5 empty] | select | direct reading | percentage | bar graph
90 |  | Scale minimum : | input data | select | input data | select |  |  |  |  | select | scfh | USgal/h | l/h | %
91 |  | Scale maximum : | input data | select | input data | select |  |  |  |  | select | scfh | USgal/h | l/h | %
92 |  | Float material : | input data |  | input data
93 |  | Flange material : | input data |  | input data
94 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
95 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
96 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
97 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
98 |  | Transmitter
99 |  | Transmitter model number : | input data |  | input data
100 |  | Transmitter enclosure material : | input data |  | input data
101 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | integrated | remote
102 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | integral LCD display | remote indicator | not applicable
103 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | 24 V DC loop power | external
104 |  | Signal type : | select |  | select | [5 empty] | select | ​​​​​​​24 Vdc | 4-20 mA | mV
105 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | ½-14 NPTF | M20 x 1.5
106 |  | Cable termination : | select |  | select | [5 empty] | select | screwed | spring loaded
107 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | fail high (NAMUR) | fail low (NAMUR)
108 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
109 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
110 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
111 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | local | remote | both
112 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
113 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
114 |  | Performance
115 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
116 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | mm | %
117 |  | Accessories
118 |  | Needle valve : | none |  | none | [5 empty] | select | inlet | outlet | none
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C22: Select the pipe schedule in accordance with the pipe specification.
Note on C23: Specify the process line size to support sizing and selection by the supplier.
Note on C24: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C25: Select the instrument process connection compatible with that declared by the purchaser.
Note on C26: Specify the orientation of the inlet to the instrument or insertion point.
Note on C27: Specify the material which the instrument connects to on the upstream face.
Note on C28: Select the pipe schedule in accordance with the pipe specification.
Note on C29: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C30: Select the pressure rating of the system connected.
Note on C31: Select the process connection to the system.
Note on C32: Specify the orientation of the inlet or insertion point of the instrument.
Note on C33: Specify the material which the instrument connects to on the downstream face.
Note on C34: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C35: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C36: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C37: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C38: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C40: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C41: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C42: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C43: Specify any corrosive elements in the process stream.
Note on C44: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C45: Specify the input details to support sizing.
Note on C46: Select whether the instrument could see a vacuum.
Note on C47: Specify the vapour pressure of the flowing fluid.
Note on C48: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C49: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C50: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C51: Specify the operating velocity of the system at the minimum sizing case.
Note on C52: Specify the temperature of the process at the minimum sizing case.
Note on C53: Specify the differential pressure of the process at the minimum sizing case.
Note on C54: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C55: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C56: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C57: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C58: Specify the vapour actual density at minimum sizing conditions.
Note on C59: Specify the vapour viscosity at minimum sizing conditions.
Note on C60: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C61: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C62: Specify the operating velocity of the system at the normal sizing case.
Note on C63: Specify the temperature of the process at the minimum sizing case.
Note on C64: Specify the pressure of the process for the normal operating case.
Note on C65: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C66: Specify the viscosity of the process fluid at the normal sizing case.
Note on C67: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C68: Specify the vapour compressibility factor at normal sizing conditions.
Note on C69: Specify the vapour actual density at normal sizing conditions.
Note on C70: Specify the vapour viscosity at normal sizing conditions.
Note on C71: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C72: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C73: Specify the operating velocity of the system at the maximum sizing case.
Note on C74: Specify the temperature of the process at the maximum sizing case.
Note on C75: Specify the pressure of the process for the maximum operating case.
Note on C76: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C77: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C78: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C79: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C80: Specify the vapour actual density at the maximum sizing conditions.
Note on C81: Specify the vapour viscosity at the maximum sizing conditions.
Note on C82: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C84: Specify the model number of the body/element/sensor.
Note on C85: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C86: Select the material to be selected for the sensor.
Note on C87: Select the VA meter type, either direct reading type (glass or clear plastic tube) or metal type (with magnetic feedback). Default value : metal type
Note on C88: Specify the most suitable float type for the process.
Note on C89: Select the type of scale to be supplied with the VA meter. Default value : percentage
Note on C90: Specify the scale minimum value. Selection to aim for normal operating flow to be within 50 % to 70 % of the scale.
Note on C91: Specify the scale maximum value. Selection to aim for normal operating flow to be within 50 % to 70 % of the scale.
Note on C92: Specify the float material for the process application.
Note on C93: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C94: Specify the selected instrument body size.
Note on C95: Specify the size of the connection to the process line or equipment.
Note on C96: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C97: Select the flange rating to match the rating of the system to which it is connected.
Note on C99: Specify the model number for the transmitter only.
Note on C100: Specify the material offered to meet the minimum requirements.
Note on C101: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C102: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C103: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C104: Select the required signal type.
Note on C105: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C106: Select the type of connection for the cable to the transmitter head.
Note on C107: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C108: Specify the bespoke range when supplier non-standard calibration is required.
Note on C109: Specify the lowest measured point for the instrument.
Note on C110: Specify the highest measured point for the instrument.
Note on C111: Select where the functionality is to be located.
Note on C112: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C113: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C115: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C116: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Note on C118: Specify whether the process application requires a needle to be provided with the VA meter. If a needle is to be provided, specify whether is to be on the inlet or outlet side. Default value : none
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowCone
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Cone Meter | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
23 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
24 |  | Installation conditions
25 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
26 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
27 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
28 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
29 |  | Upstream (high-side) connection orientation : | input data |  | input data
30 |  | Upstream (high-side) material type : | input data |  | input data
31 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
32 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
33 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
34 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
35 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
36 |  | Downstream (bottom-side) material type : | input data |  | input data
37 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
38 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
39 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
40 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
41 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
42 |  | Operating conditions
43 |  | Process fluid(s) : | input data |  | input data
44 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
45 |  | Service description : | input data |  | input data
46 |  | Process fluid corrosive compounds : | input data |  | input data
47 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
48 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
49 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
50 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa
51 |  | Process fluid plugging : | no |  | no | [5 empty] | select | yes | no
52 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
53 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
54 |  | Minimum operating velocity : | input data | m/s | input data | m/s
55 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
56 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
57 |  | Minimum operating liquid specific gravity : | input data |  | input data
58 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
59 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
60 |  | Minimum operating vapour compressibility factor : | input data |  | input data
61 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
62 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
63 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
64 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
65 |  | Normal operating velocity : | input data | m/s | input data | m/s
66 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
67 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
68 |  | Normal operating liquid specific gravity : | input data |  | input data
69 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
70 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
71 |  | Normal operating vapour compressibility factor : | input data |  | input data
72 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
73 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
74 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
75 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
76 |  | Maximum operating velocity : | input data | m/s | input data | m/s
77 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
78 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
79 |  | Maximum operating liquid specific gravity : | input data |  | input data
80 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
81 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
82 |  | Maximum operating vapour compressibility factor : | input data |  | input data
83 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
84 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
85 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
86 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
87 |  | Body/element/sensor
88 |  | Body/element/sensor manufacturer model number : | input data |  | input data
89 |  | Body material : | input data |  | input data
90 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
91 |  | Sensor support material : | input data |  | input data
92 |  | Flange material : | input data |  | input data
93 |  | Beta ratio (d/D) : | input data |  | input data
94 |  | Minimum differential pressure: | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
95 |  | Maximum differential pressure : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
96 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
97 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
98 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
99 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
100 |  | Number of pressure taps : | 1 pair |  | 1 pair | [5 empty] | select | 1 pair | 2 pairs
101 |  | Pressure tap size : | select |  | select | [5 empty] | select | 12 mm (½ in) | 19 mm (¾ in) | 25 mm (1 in) | 50 mm (2 in)
102 |  | Pressure tap connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF | NPT(F)
103 |  | Pressure tap rating : | CI-150 |  | CI-150 | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
104 |  | Pressure tap orientation : | input data | deg | input data | deg
105 |  | Transmitter
106 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
107 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
108 |  | Performance
109 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
110 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | mm | %
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C23: Select the nut material as detailed in IOGP S-563.
Note on C25: Select the pipe schedule in accordance with the pipe specification.
Note on C26: Specify the process line size to support sizing and selection by the supplier.
Note on C27: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C28: Select the instrument process connection compatible with that declared by the purchaser.
Note on C29: Specify the orientation of the inlet to the instrument or insertion point.
Note on C30: Specify the material which the instrument connects to on the upstream face.
Note on C31: Select the pipe schedule in accordance with the pipe specification.
Note on C32: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C33: Select the pressure rating of the system connected.
Note on C34: Select the process connection to the system.
Note on C35: Specify the orientation of the inlet or insertion point of the instrument.
Note on C36: Specify the material which the instrument connects to on the downstream face.
Note on C37: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C38: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C39: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C40: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C41: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C43: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C44: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C45: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C46: Specify any corrosive elements in the process stream.
Note on C47: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C48: Specify the input details to support sizing.
Note on C49: Select whether the instrument could see a vacuum.
Note on C50: Specify the vapour pressure of the flowing fluid.
Note on C51: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C52: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C53: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C54: Specify the operating velocity of the system at the minimum sizing case.
Note on C55: Specify the temperature of the process at the minimum sizing case.
Note on C56: Specify the differential pressure of the process at the minimum sizing case.
Note on C57: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C58: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C59: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C60: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C61: Specify the vapour actual density at minimum sizing conditions.
Note on C62: Specify the vapour viscosity at minimum sizing conditions.
Note on C63: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C64: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C65: Specify the operating velocity of the system at the normal sizing case.
Note on C66: Specify the temperature of the process at the minimum sizing case.
Note on C67: Specify the pressure of the process for the normal operating case.
Note on C68: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C69: Specify the viscosity of the process fluid at the normal sizing case.
Note on C70: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C71: Specify the vapour compressibility factor at normal sizing conditions.
Note on C72: Specify the vapour actual density at normal sizing conditions.
Note on C73: Specify the vapour viscosity at normal sizing conditions.
Note on C74: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C75: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C76: Specify the operating velocity of the system at the maximum sizing case.
Note on C77: Specify the temperature of the process at the maximum sizing case.
Note on C78: Specify the pressure of the process for the maximum operating case.
Note on C79: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C80: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C81: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C82: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C83: Specify the vapour actual density at the maximum sizing conditions.
Note on C84: Specify the vapour viscosity at the maximum sizing conditions.
Note on C85: Specify the worst case pressure loss that the system can accept.
Note on C86: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C88: Specify the model number of the body/element/sensor.
Note on C89: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C90: Select the material to be selected for the sensor.
Note on C91: Specify the material required to provide a structural support between the sensor and the instrument body.
Note on C92: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C93: Specify the ratio of d/D after orifice sizing calculations.
Note on C94: Specify the differential pressure associated with the minimum flow rates of the fluid being measured.
Note on C95: Specify the differential pressure associated with the maximum flow rates of the fluid being measured.
Note on C96: Specify the selected instrument body size.
Note on C97: Specify the size of the connection to the process line or equipment.
Note on C98: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C99: Select the flange rating to match the rating of the system to which it is connected.
Note on C100: Select the number of pressure taps. Default value : 1 pair
Note on C101: Select the size for the differential pressure sensing lines.
Note on C102: Select the connection type. Default value : RF
Note on C103: Select the pressure rating of the process connection. Default value : CI-150
Note on C104: Specify the orientation of the tapping with 0 deg being a tapping in the vertical plane from the top. As an example, ISO 5167-6 requires the tappings to be 0 deg.
Note on C106: Specify the lowest measured point for the instrument.
Note on C107: Specify the highest measured point for the instrument.
Note on C109: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C110: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowVent
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Venturi | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
23 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
24 |  | Installation conditions
25 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
26 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
27 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
28 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
29 |  | Upstream (high-side) connection orientation : | input data |  | input data
30 |  | Upstream (high-side) material type : | input data |  | input data
31 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
32 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
33 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
34 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
35 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
36 |  | Downstream (bottom-side) material type : | input data |  | input data
37 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
38 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
39 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
40 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
41 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
42 |  | Operating conditions
43 |  | Process fluid(s) : | input data |  | input data
44 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
45 |  | Service description : | input data |  | input data
46 |  | Process fluid corrosive compounds : | input data |  | input data
47 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
48 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
49 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
50 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa
51 |  | Process fluid plugging : | no |  | no | [5 empty] | select | yes | no
52 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
53 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
54 |  | Minimum operating velocity : | input data | m/s | input data | m/s
55 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
56 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
57 |  | Minimum operating liquid specific gravity : | input data |  | input data
58 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
59 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
60 |  | Minimum operating vapour compressibility factor : | input data |  | input data
61 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
62 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
63 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
64 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
65 |  | Normal operating velocity : | input data | m/s | input data | m/s
66 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
67 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
68 |  | Normal operating liquid specific gravity : | input data |  | input data
69 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
70 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
71 |  | Normal operating vapour compressibility factor : | input data |  | input data
72 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
73 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
74 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
75 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
76 |  | Maximum operating velocity : | input data | m/s | input data | m/s
77 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
78 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
79 |  | Maximum operating liquid specific gravity : | input data |  | input data
80 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
81 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
82 |  | Maximum operating vapour compressibility factor : | input data |  | input data
83 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
84 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
85 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
86 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
87 |  | Body/element/sensor
88 |  | Body/element/sensor manufacturer model number : | input data |  | input data
89 |  | Body material : | input data |  | input data
90 |  | Flange material : | input data |  | input data
91 |  | Venturi throat diameter : | input data | select | input data | select |  |  |  |  | select | mm | in
92 |  | Beta ratio (d/D) : | input data |  | input data
93 |  | Minimum differential pressure: | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
94 |  | Maximum differential pressure : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
95 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
96 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
97 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
98 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
99 |  | Number of pressure taps : | 1 pair |  | 1 pair | [5 empty] | select | 1 pair | 2 pairs
100 |  | Pressure tap size : | select |  | select | [5 empty] | select | 12 mm (½ in) | 19 mm (¾ in) | 25 mm (1 in) | 50 mm (2 in)
101 |  | Pressure tap connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF | NPT(F)
102 |  | Pressure tap rating : | CI-150 |  | CI-150 | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
103 |  | Pressure tap orientation : | input data | deg | input data | deg
104 |  | Transmitter
105 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
106 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C23: Select the nut material as detailed in IOGP S-563.
Note on C25: Select the pipe schedule in accordance with the pipe specification.
Note on C26: Specify the process line size to support sizing and selection by the supplier.
Note on C27: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C28: Select the instrument process connection compatible with that declared by the purchaser.
Note on C29: Specify the orientation of the inlet to the instrument or insertion point.
Note on C30: Specify the material which the instrument connects to on the upstream face.
Note on C31: Select the pipe schedule in accordance with the pipe specification.
Note on C32: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C33: Select the pressure rating of the system connected.
Note on C34: Select the process connection to the system.
Note on C35: Specify the orientation of the inlet or insertion point of the instrument.
Note on C36: Specify the material which the instrument connects to on the downstream face.
Note on C37: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C38: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C39: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C40: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C41: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C43: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C44: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C45: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C46: Specify any corrosive elements in the process stream.
Note on C47: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C48: Specify the input details to support sizing.
Note on C49: Select whether the instrument could see a vacuum.
Note on C50: Specify the vapour pressure of the flowing fluid.
Note on C51: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C52: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C53: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C54: Specify the operating velocity of the system at the minimum sizing case.
Note on C55: Specify the temperature of the process at the minimum sizing case.
Note on C56: Specify the differential pressure of the process at the minimum sizing case.
Note on C57: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C58: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C59: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C60: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C61: Specify the vapour actual density at minimum sizing conditions.
Note on C62: Specify the vapour viscosity at minimum sizing conditions.
Note on C63: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C64: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C65: Specify the operating velocity of the system at the normal sizing case.
Note on C66: Specify the temperature of the process at the minimum sizing case.
Note on C67: Specify the pressure of the process for the normal operating case.
Note on C68: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C69: Specify the viscosity of the process fluid at the normal sizing case.
Note on C70: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C71: Specify the vapour compressibility factor at normal sizing conditions.
Note on C72: Specify the vapour actual density at normal sizing conditions.
Note on C73: Specify the vapour viscosity at normal sizing conditions.
Note on C74: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C75: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C76: Specify the operating velocity of the system at the maximum sizing case.
Note on C77: Specify the temperature of the process at the maximum sizing case.
Note on C78: Specify the pressure of the process for the maximum operating case.
Note on C79: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C80: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C81: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C82: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C83: Specify the vapour actual density at the maximum sizing conditions.
Note on C84: Specify the vapour viscosity at the maximum sizing conditions.
Note on C85: Specify the worst case pressure loss that the system can accept.
Note on C86: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C88: Specify the model number of the body/element/sensor.
Note on C89: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C90: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C91: Specify the throat diameter after venturi sizing calculations.
Note on C92: Specify the ratio of d/D after orifice sizing calculations.
Note on C93: Specify the differential pressure associated with the minimum flow rates of the fluid being measured.
Note on C94: Specify the differential pressure associated with the maximum flow rates of the fluid being measured.
Note on C95: Specify the selected instrument body size.
Note on C96: Specify the size of the connection to the process line or equipment.
Note on C97: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C98: Select the flange rating to match the rating of the system to which it is connected.
Note on C99: Select the number of pressure taps. Default value : 1 pair
Note on C100: Select the size for the differential pressure sensing lines.
Note on C101: Select the connection type. Default value : RF
Note on C102: Select the pressure rating of the process connection. Default value : CI-150
Note on C103: Specify the orientation of the tapping with 0 deg being a tapping in the vertical plane from the top. As an example, ISO 5167-6 requires the tappings to be 0 deg.
Note on C105: Specify the lowest measured point for the instrument.
Note on C106: Specify the highest measured point for the instrument.
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowNoz
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Nozzle | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Installation conditions
22 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
23 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
24 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
25 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
26 |  | Upstream (high-side) connection orientation : | input data |  | input data
27 |  | Upstream (high-side) material type : | input data |  | input data
28 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
29 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
30 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
31 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
32 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
33 |  | Downstream (bottom-side) material type : | input data |  | input data
34 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
35 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
36 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
37 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
38 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
39 |  | Operating conditions
40 |  | Process fluid(s) : | input data |  | input data
41 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
42 |  | Service description : | input data |  | input data
43 |  | Process fluid corrosive compounds : | input data |  | input data
44 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
45 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
46 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
47 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa
48 |  | Process fluid plugging : | no |  | no | [5 empty] | select | yes | no
49 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
50 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
51 |  | Minimum operating velocity : | input data | m/s | input data | m/s
52 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
53 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
54 |  | Minimum operating liquid specific gravity : | input data |  | input data
55 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
56 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
57 |  | Minimum operating vapour compressibility factor : | input data |  | input data
58 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
59 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
60 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
61 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
62 |  | Normal operating velocity : | input data | m/s | input data | m/s
63 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
64 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
65 |  | Normal operating liquid specific gravity : | input data |  | input data
66 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
67 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
68 |  | Normal operating vapour compressibility factor : | input data |  | input data
69 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
70 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
71 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
72 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
73 |  | Maximum operating velocity : | input data | m/s | input data | m/s
74 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
75 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
76 |  | Maximum operating liquid specific gravity : | input data |  | input data
77 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
78 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
79 |  | Maximum operating vapour compressibility factor : | input data |  | input data
80 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
81 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
82 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
83 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
84 |  | Body/element/sensor
85 |  | Body/element/sensor manufacturer model number : | input data |  | input data
86 |  | Body material : | input data |  | input data
87 |  | Flange material : | input data |  | input data
88 |  | Beta ratio (d/D) : | input data |  | input data
89 |  | Minimum differential pressure: | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
90 |  | Maximum differential pressure : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
91 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
92 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
93 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
94 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
95 |  | Number of pressure taps : | 1 pair |  | 1 pair | [5 empty] | select | 1 pair | 2 pairs
96 |  | Pressure tap size : | select |  | select | [5 empty] | select | 12 mm (½ in) | 19 mm (¾ in) | 25 mm (1 in) | 50 mm (2 in)
97 |  | Pressure tap connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF | NPT(F)
98 |  | Pressure tap rating : | CI-150 |  | CI-150 | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
99 |  | Pressure tap orientation : | input data | deg | input data | deg
100 |  | Transmitter
101 |  | Nozzle type : | ISA 1932 |  | ISA 1932 | [5 empty] | select | ISA 1932 | long radius | throat-tapped | venturi nozzle
102 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
103 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C22: Select the pipe schedule in accordance with the pipe specification.
Note on C23: Specify the process line size to support sizing and selection by the supplier.
Note on C24: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C25: Select the instrument process connection compatible with that declared by the purchaser.
Note on C26: Specify the orientation of the inlet to the instrument or insertion point.
Note on C27: Specify the material which the instrument connects to on the upstream face.
Note on C28: Select the pipe schedule in accordance with the pipe specification.
Note on C29: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C30: Select the pressure rating of the system connected.
Note on C31: Select the process connection to the system.
Note on C32: Specify the orientation of the inlet or insertion point of the instrument.
Note on C33: Specify the material which the instrument connects to on the downstream face.
Note on C34: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C35: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C36: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C37: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C38: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C40: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C41: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C42: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C43: Specify any corrosive elements in the process stream.
Note on C44: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C45: Specify the input details to support sizing.
Note on C46: Select whether the instrument could see a vacuum.
Note on C47: Specify the vapour pressure of the flowing fluid.
Note on C48: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C49: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C50: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C51: Specify the operating velocity of the system at the minimum sizing case.
Note on C52: Specify the temperature of the process at the minimum sizing case.
Note on C53: Specify the differential pressure of the process at the minimum sizing case.
Note on C54: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C55: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C56: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C57: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C58: Specify the vapour actual density at minimum sizing conditions.
Note on C59: Specify the vapour viscosity at minimum sizing conditions.
Note on C60: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C61: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C62: Specify the operating velocity of the system at the normal sizing case.
Note on C63: Specify the temperature of the process at the minimum sizing case.
Note on C64: Specify the pressure of the process for the normal operating case.
Note on C65: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C66: Specify the viscosity of the process fluid at the normal sizing case.
Note on C67: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C68: Specify the vapour compressibility factor at normal sizing conditions.
Note on C69: Specify the vapour actual density at normal sizing conditions.
Note on C70: Specify the vapour viscosity at normal sizing conditions.
Note on C71: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C72: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C73: Specify the operating velocity of the system at the maximum sizing case.
Note on C74: Specify the temperature of the process at the maximum sizing case.
Note on C75: Specify the pressure of the process for the maximum operating case.
Note on C76: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C77: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C78: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C79: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C80: Specify the vapour actual density at the maximum sizing conditions.
Note on C81: Specify the vapour viscosity at the maximum sizing conditions.
Note on C82: Specify the worst case pressure loss that the system can accept.
Note on C83: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C85: Specify the model number of the body/element/sensor.
Note on C86: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C87: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C88: Specify the ratio of d/D after orifice sizing calculations.
Note on C89: Specify the differential pressure associated with the minimum flow rates of the fluid being measured.
Note on C90: Specify the differential pressure associated with the maximum flow rates of the fluid being measured.
Note on C91: Specify the selected instrument body size.
Note on C92: Specify the size of the connection to the process line or equipment.
Note on C93: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C94: Select the flange rating to match the rating of the system to which it is connected.
Note on C95: Select the number of pressure taps. Default value : 1 pair
Note on C96: Select the size for the differential pressure sensing lines.
Note on C97: Select the connection type. Default value : RF
Note on C98: Select the pressure rating of the process connection. Default value : CI-150
Note on C99: Specify the orientation of the tapping with 0 deg being a tapping in the vertical plane from the top. As an example, ISO 5167-6 requires the tappings to be 0 deg.
Note on C101: Select the type of nozzle to be supplied. Default value : ISA 1932
Note on C102: Specify the lowest measured point for the instrument.
Note on C103: Specify the highest measured point for the instrument.
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowWedge
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Wedge | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Installation conditions
22 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
23 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
24 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
25 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
26 |  | Upstream (high-side) connection orientation : | input data |  | input data
27 |  | Upstream (high-side) material type : | input data |  | input data
28 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
29 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | mm | in
30 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
31 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
32 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
33 |  | Downstream (bottom-side) material type : | input data |  | input data
34 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
35 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | barg | psig | kPag
36 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
37 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
38 |  | Sour service specification : | select |  | select | [5 empty] | select | NACE MR0175/ISO 15156 | NACE MR0103/ISO 17945 | not applicable
39 |  | Operating conditions
40 |  | Process fluid(s) : | input data |  | input data
41 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | liquid | vapour | gas
42 |  | Service description : | input data |  | input data
43 |  | Process fluid corrosive compounds : | input data |  | input data
44 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | yes | no
45 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
46 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | yes | no
47 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa
48 |  | Process fluid plugging : | no |  | no | [5 empty] | select | yes | no
49 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
50 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
51 |  | Minimum operating velocity : | input data | m/s | input data | m/s
52 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
53 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
54 |  | Minimum operating liquid specific gravity : | input data |  | input data
55 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
56 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
57 |  | Minimum operating vapour compressibility factor : | input data |  | input data
58 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
59 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
60 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
61 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
62 |  | Normal operating velocity : | input data | m/s | input data | m/s
63 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
64 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
65 |  | Normal operating liquid specific gravity : | input data |  | input data
66 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
67 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
68 |  | Normal operating vapour compressibility factor : | input data |  | input data
69 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
70 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
71 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | kg/h | lb/h
72 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
73 |  | Maximum operating velocity : | input data | m/s | input data | m/s
74 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
75 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
76 |  | Maximum operating liquid specific gravity : | input data |  | input data
77 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
78 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
79 |  | Maximum operating vapour compressibility factor : | input data |  | input data
80 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
81 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | cP | cS
82 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
83 |  | Bi-directional flow : | no |  | no | [5 empty] | select | yes | no
84 |  | Pulsating flow : | no |  | no | [5 empty] | select | yes | no
85 |  | Body/element/sensor
86 |  | Body/element/sensor manufacturer model number : | input data |  | input data
87 |  | Body material : | input data |  | input data
88 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
89 |  | Flange material : | input data |  | input data
90 |  | H/D ratio : | input data |  | input data
91 |  | Minimum differential pressure: | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
92 |  | Maximum differential pressure : | input data | select | input data | select |  |  |  |  | select | bar | psi | mbar | inH2O
93 |  | Body size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
94 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | mm | in | not applicable
95 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
96 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
97 |  | Number of pressure taps : | 1 pair |  | 1 pair | [5 empty] | select | 1 pair | 2 pairs
98 |  | Pressure tap size : | select |  | select | [5 empty] | select | 12 mm (½ in) | 19 mm (¾ in) | 25 mm (1 in) | 50 mm (2 in)
99 |  | Pressure tap connection type : | RF |  | RF | [5 empty] | select | RF | RTJ | FF | NPT(F)
100 |  | Pressure tap rating : | CI-150 |  | CI-150 | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
101 |  | Pressure tap orientation : | input data | deg | input data | deg
102 |  | Transmitter
103 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
104 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
105 |  | Performance
106 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
107 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | mm | %
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C22: Select the pipe schedule in accordance with the pipe specification.
Note on C23: Specify the process line size to support sizing and selection by the supplier.
Note on C24: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C25: Select the instrument process connection compatible with that declared by the purchaser.
Note on C26: Specify the orientation of the inlet to the instrument or insertion point.
Note on C27: Specify the material which the instrument connects to on the upstream face.
Note on C28: Select the pipe schedule in accordance with the pipe specification.
Note on C29: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C30: Select the pressure rating of the system connected.
Note on C31: Select the process connection to the system.
Note on C32: Specify the orientation of the inlet or insertion point of the instrument.
Note on C33: Specify the material which the instrument connects to on the downstream face.
Note on C34: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C35: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C36: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C37: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C38: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C40: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C41: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C42: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C43: Specify any corrosive elements in the process stream.
Note on C44: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C45: Specify the input details to support sizing.
Note on C46: Select whether the instrument could see a vacuum.
Note on C47: Specify the vapour pressure of the flowing fluid.
Note on C48: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C49: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C50: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C51: Specify the operating velocity of the system at the minimum sizing case.
Note on C52: Specify the temperature of the process at the minimum sizing case.
Note on C53: Specify the differential pressure of the process at the minimum sizing case.
Note on C54: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C55: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C56: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C57: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C58: Specify the vapour actual density at minimum sizing conditions.
Note on C59: Specify the vapour viscosity at minimum sizing conditions.
Note on C60: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C61: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C62: Specify the operating velocity of the system at the normal sizing case.
Note on C63: Specify the temperature of the process at the minimum sizing case.
Note on C64: Specify the pressure of the process for the normal operating case.
Note on C65: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C66: Specify the viscosity of the process fluid at the normal sizing case.
Note on C67: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C68: Specify the vapour compressibility factor at normal sizing conditions.
Note on C69: Specify the vapour actual density at normal sizing conditions.
Note on C70: Specify the vapour viscosity at normal sizing conditions.
Note on C71: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C72: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C73: Specify the operating velocity of the system at the maximum sizing case.
Note on C74: Specify the temperature of the process at the maximum sizing case.
Note on C75: Specify the pressure of the process for the maximum operating case.
Note on C76: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C77: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C78: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C79: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C80: Specify the vapour actual density at the maximum sizing conditions.
Note on C81: Specify the vapour viscosity at the maximum sizing conditions.
Note on C82: Specify the worst case pressure loss that the system can accept.
Note on C83: Select whether the bi-directional flow is to be considered. If "yes" selected, specify details in the "Additional notes" column. Default value : no
Note on C84: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C86: Specify the model number of the body/element/sensor.
Note on C87: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C88: Select the material to be selected for the sensor.
Note on C89: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C90: Specify the height of the wedge in relation to the internal diameter.
Note on C91: Specify the differential pressure associated with the minimum flow rates of the fluid being measured.
Note on C92: Specify the differential pressure associated with the maximum flow rates of the fluid being measured.
Note on C93: Specify the selected instrument body size.
Note on C94: Specify the size of the connection to the process line or equipment.
Note on C95: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C96: Select the flange rating to match the rating of the system to which it is connected.
Note on C97: Select the number of pressure taps. Default value : 1 pair
Note on C98: Select the size for the differential pressure sensing lines.
Note on C99: Select the connection type. Default value : RF
Note on C100: Select the pressure rating of the process connection. Default value : CI-150
Note on C101: Specify the orientation of the tapping with 0 deg being a tapping in the vertical plane from the top. As an example, ISO 5167-6 requires the tappings to be 0 deg.
Note on C103: Specify the lowest measured point for the instrument.
Note on C104: Specify the highest measured point for the instrument.
Note on C106: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C107: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowEM
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Electromagnetic | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
23 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
24 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
25 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
26 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
27 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
28 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
29 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
30 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
31 |  | Installation conditions
32 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
33 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
34 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
35 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
36 |  | Upstream (high-side) connection orientation : | input data |  | input data
37 |  | Upstream (high-side) material type : | input data |  | input data
38 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
39 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
40 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
41 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
42 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
43 |  | Operating conditions
44 |  | Process fluid(s) : | input data |  | input data
45 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
46 |  | Service description : | input data |  | input data
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
49 | 8.3.3.3 | Process fluid conductivity : | input data | µS | input data | µS
50 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
51 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
52 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
53 |  | Minimum operating velocity : | input data | m/s | input data | m/s
54 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
55 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
56 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
57 |  | Normal operating velocity : | input data | m/s | input data | m/s
58 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
59 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
60 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
61 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
62 |  | Maximum operating velocity : | input data | m/s | input data | m/s
63 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
64 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
65 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
66 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
67 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
68 |  | Body/element/sensor
69 |  | Body/element/sensor manufacturer model number : | input data |  | input data
70 |  | Body material : | input data |  | input data
71 |  | Flange material : | input data |  | input data
72 |  | Liner material : | input data |  | input data
73 |  | Coil cover material : | input data |  | input data
74 | 4.3.1.3.1 | Junction box material : | input data |  | input data
75 |  | Electrode type : | input data |  | input data
76 |  | Electrode material : | input data |  | input data
77 |  | Meter minimum conductivity : | input data |  | input data
78 |  | Grounding ring : | select |  | select | [5 empty] | select | T1: yes; T2: no
79 |  | Grounding ring material : | input data |  | input data
80 |  | Lining protector : | select |  | select | [5 empty] | select | T1: yes; T2: no
81 |  | Body size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
82 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
83 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
84 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
85 |  | Transmitter
86 |  | Transmitter model number : | input data |  | input data
87 |  | Transmitter enclosure material : | input data |  | input data
88 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
89 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
90 |  | Transmitter connecting cables : | no |  | no | [5 empty] | select | T1: yes; T2: no
91 |  | Transmitter connecting cable length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
92 |  | Transmitter connecting cable quantity : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4
93 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
94 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
95 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
96 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
97 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
98 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
99 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
100 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
101 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
102 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
103 |  | Protocol version : | input data |  | input data
104 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
105 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
106 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
107 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
108 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
109 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
110 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
111 |  | Performance
112 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
113 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
114 |  | Long term drift : | input data |  | input data
115 |  | Long term stability : | input data |  | input data
116 |  | Accessories
117 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
118 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
119 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C23: Select the nut material as detailed in IOGP S-563.
Note on C24: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C25: Select the ingress protection rating in IP or NEMA.
Note on C26: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C27: Select the code to be followed for the hazardous area classification.
Note on C28: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C29: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C30: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C32: Select the pipe schedule in accordance with the pipe specification.
Note on C33: Specify the process line size to support sizing and selection by the supplier.
Note on C34: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C35: Select the instrument process connection compatible with that declared by the purchaser.
Note on C36: Specify the orientation of the inlet to the instrument or insertion point.
Note on C37: Specify the material which the instrument connects to on the upstream face.
Note on C38: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C39: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C40: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C41: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C42: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C44: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C45: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C46: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C47: Specify any corrosive elements in the process stream.
Note on C48: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C49: Specify the conductivity of the process fluid.
Note on C50: Specify the input details to support sizing.
Note on C51: Select whether the instrument could see a vacuum.
Note on C52: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C53: Specify the operating velocity of the system at the minimum sizing case.
Note on C54: Specify the temperature of the process at the minimum sizing case.
Note on C55: Specify the differential pressure of the process at the minimum sizing case.
Note on C56: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C57: Specify the operating velocity of the system at the normal sizing case.
Note on C58: Specify the temperature of the process at the minimum sizing case.
Note on C59: Specify the pressure of the process for the normal operating case.
Note on C60: Specify the viscosity of the process fluid at the normal sizing case.
Note on C61: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C62: Specify the operating velocity of the system at the maximum sizing case.
Note on C63: Specify the temperature of the process at the maximum sizing case.
Note on C64: Specify the pressure of the process for the maximum operating case.
Note on C65: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C66: Specify the worst case pressure loss that the system can accept.
Note on C67: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C69: Specify the model number of the body/element/sensor.
Note on C70: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C71: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C72: Specify the state of the liner material when required.
Note on C73: Specify the external cover material surrounding the wiring coils.
Note on C74: Specify the material for the junction box mounted on the flow body (used to terminate the coils).
Note on C75: Specify the electrode type.
Note on C76: Specify the electrode material that is in contact with the process medium.
Note on C77: Specify the minimum conductivity of the process fluid that the electrodes are able to measure.
Note on C78: Select whether a grounding ring is needed for correct operation of the electromagnetic flow meter.
Note on C79: Specify the material when a grounding ring is required.
Note on C80: Select whether a lining protector is needed to protect sensor from abrasive fluids.
Note on C81: Specify the selected instrument body size.
Note on C82: Specify the size of the connection to the process line or equipment.
Note on C83: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C84: Select the flange rating to match the rating of the system to which it is connected.
Note on C86: Specify the model number for the transmitter only.
Note on C87: Specify the material offered to meet the minimum requirements.
Note on C88: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C89: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C90: Select whether external cables are required for connection between the sensor and the transmitter housing or whether they are they integral. Default value : no
Note on C91: Specify the length of cable to support routing from the flow meter body to the transmitter housing.
Note on C92: Select the number of cables needed between the body and the transmitter head.
Note on C93: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C94: Select the required signal type.
Note on C95: Select the type of power supply to the instrument. Default value : hardwired
Note on C96: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C97: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C98: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C99: Select the type of connection for the cable to the transmitter head.
Note on C100: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C101: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C102: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C103: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C104: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C105: Specify the bespoke range when supplier non-standard calibration is required.
Note on C106: Specify the lowest measured point for the instrument.
Note on C107: Specify the highest measured point for the instrument.
Note on C108: Select where the functionality is to be located.
Note on C109: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C110: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C112: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C113: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Note on C114: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C115: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C117: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C118: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C119: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowTurb
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Turbine | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
23 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
24 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
25 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
26 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
27 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
28 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
29 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
30 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
31 |  | Installation conditions
32 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
33 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
34 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
35 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
36 |  | Upstream (high-side) connection orientation : | input data |  | input data
37 |  | Upstream (high-side) material type : | input data |  | input data
38 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
39 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
40 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
41 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
42 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
43 |  | Operating conditions
44 |  | Process fluid(s) : | input data |  | input data
45 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
46 |  | Service description : | input data |  | input data
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
49 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
50 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
51 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | T1: bara; T2: psia; T3: kPaa
52 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
53 |  | Minimum operating velocity : | input data | m/s | input data | m/s
54 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
55 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
56 |  | Minimum operating liquid specific gravity : | input data |  | input data
57 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
58 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
59 |  | Minimum operating vapour compressibility factor : | input data |  | input data
60 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
61 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
62 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
63 |  | Normal operating velocity : | input data | m/s | input data | m/s
64 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
65 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
66 |  | Normal operating liquid specific gravity : | input data |  | input data
67 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
68 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
69 |  | Normal operating vapour compressibility factor : | input data |  | input data
70 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
71 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
72 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
73 |  | Maximum operating velocity : | input data | m/s | input data | m/s
74 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
75 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
76 |  | Maximum operating liquid specific gravity : | input data |  | input data
77 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
78 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
79 |  | Maximum operating vapour compressibility factor : | input data |  | input data
80 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
81 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
82 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
83 |  | Body/element/sensor
84 |  | Body/element/sensor manufacturer model number : | input data |  | input data
85 |  | Body material : | input data |  | input data
86 |  | Flange material : | input data |  | input data
87 |  | Pickup type : | magnetic inductive |  | magnetic inductive | [5 empty] | select | T1: magnetic inductive; T2: magnetic reluctance; T3: modulated carrier frequency
88 |  | Number of pickups : | 1 |  | 1 | [5 empty] | select | T1: 1; T2: 2
89 |  | Rotor type : | blade |  | blade | [5 empty] | select | T1: rim; T2: blade
90 |  | K-factor : | select |  | select | [5 empty] | select | T1: US gallon; T2: litre; T3: other
91 |  | Body size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
92 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
93 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
94 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
95 |  | Transmitter
96 |  | Transmitter model number : | input data |  | input data
97 |  | Transmitter enclosure material : | input data |  | input data
98 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
99 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
100 |  | Transmitter connecting cables : | no |  | no | [5 empty] | select | T1: yes; T2: no
101 |  | Transmitter connecting cable length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
102 |  | Transmitter connecting cable quantity : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4
103 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
104 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
105 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
106 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
107 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
108 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
109 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
110 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
111 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
112 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
113 |  | Protocol version : | input data |  | input data
114 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
115 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
116 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
117 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
118 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
119 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
120 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
121 |  | Performance
122 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
123 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
124 |  | Linearity : | input data | % | input data | %
125 |  | Accessories
126 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
127 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
128 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C23: Select the nut material as detailed in IOGP S-563.
Note on C24: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C25: Select the ingress protection rating in IP or NEMA.
Note on C26: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C27: Select the code to be followed for the hazardous area classification.
Note on C28: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C29: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C30: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C32: Select the pipe schedule in accordance with the pipe specification.
Note on C33: Specify the process line size to support sizing and selection by the supplier.
Note on C34: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C35: Select the instrument process connection compatible with that declared by the purchaser.
Note on C36: Specify the orientation of the inlet to the instrument or insertion point.
Note on C37: Specify the material which the instrument connects to on the upstream face.
Note on C38: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C39: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C40: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C41: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C42: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C44: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C45: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C46: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C47: Specify any corrosive elements in the process stream.
Note on C48: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C49: Specify the input details to support sizing.
Note on C50: Select whether the instrument could see a vacuum.
Note on C51: Specify the vapour pressure of the flowing fluid.
Note on C52: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C53: Specify the operating velocity of the system at the minimum sizing case.
Note on C54: Specify the temperature of the process at the minimum sizing case.
Note on C55: Specify the differential pressure of the process at the minimum sizing case.
Note on C56: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C57: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C58: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C59: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C60: Specify the vapour actual density at minimum sizing conditions.
Note on C61: Specify the vapour viscosity at minimum sizing conditions.
Note on C62: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C63: Specify the operating velocity of the system at the normal sizing case.
Note on C64: Specify the temperature of the process at the minimum sizing case.
Note on C65: Specify the pressure of the process for the normal operating case.
Note on C66: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C67: Specify the viscosity of the process fluid at the normal sizing case.
Note on C68: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C69: Specify the vapour compressibility factor at normal sizing conditions.
Note on C70: Specify the vapour actual density at normal sizing conditions.
Note on C71: Specify the vapour viscosity at normal sizing conditions.
Note on C72: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C73: Specify the operating velocity of the system at the maximum sizing case.
Note on C74: Specify the temperature of the process at the maximum sizing case.
Note on C75: Specify the pressure of the process for the maximum operating case.
Note on C76: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C77: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C78: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C79: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C80: Specify the vapour actual density at the maximum sizing conditions.
Note on C81: Specify the vapour viscosity at the maximum sizing conditions.
Note on C82: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C84: Specify the model number of the body/element/sensor.
Note on C85: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C86: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C87: Select the pickup type required. Default value : magnetic inductive
Note on C88: Select the quantity of pickup sensors to be declared. Default value : 1
Note on C89: Select the rotor type for the turbine flow meter. Default value : blade
Note on C90: Select the volume of process fluid that passes for each rotation.
Note on C91: Specify the selected instrument body size.
Note on C92: Specify the size of the connection to the process line or equipment.
Note on C93: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C94: Select the flange rating to match the rating of the system to which it is connected.
Note on C96: Specify the model number for the transmitter only.
Note on C97: Specify the material offered to meet the minimum requirements.
Note on C98: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C99: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C100: Select whether external cables are required for connection between the sensor and the transmitter housing or whether they are they integral. Default value : no
Note on C101: Specify the length of cable to support routing from the flow meter body to the transmitter housing.
Note on C102: Select the number of cables needed between the body and the transmitter head.
Note on C103: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C104: Select the required signal type.
Note on C105: Select the type of power supply to the instrument. Default value : hardwired
Note on C106: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C107: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C108: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C109: Select the type of connection for the cable to the transmitter head.
Note on C110: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C111: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C112: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C113: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C114: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C115: Specify the bespoke range when supplier non-standard calibration is required.
Note on C116: Specify the lowest measured point for the instrument.
Note on C117: Specify the highest measured point for the instrument.
Note on C118: Select where the functionality is to be located.
Note on C119: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C120: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C122: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C123: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Note on C124: Specify the linearity figure in accordance with IEC 62828 (all parts).
Note on C126: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C127: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C128: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowUltSon
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Ultrasonic | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Instrumentation type : | select |  | select | [5 empty] | select | ultrasonic flow meter (multi-path inline) | ultrasonic flow meter (clamp-on)
5 |  | Ultrasonic technology type : | select |  | select | [5 empty] | select | doppler | time of flight (transit time)
6 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 | 4.1.2.1 | Tag number : | input data |  | input data
9 |  | Service description : | input data |  | input data
10 |  | Manufacturer : | input data |  | input data
11 | 8.3.4.1 | Model number : | input data |  | input data
12 |  | Equipment manufacturer serial number : | input data |  | input data
13 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
14 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
15 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
16 |  | P&ID number : | input data |  | input data
17 |  | Line or equipment number : | input data |  | input data
18 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
19 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
21 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
22 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
23 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
24 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
25 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
26 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
27 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
28 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
29 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
30 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
31 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
32 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
33 |  | Installation conditions
34 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
35 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
36 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
37 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
38 |  | Upstream (high-side) connection orientation : | input data |  | input data
39 |  | Upstream (high-side) material type : | input data |  | input data
40 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
41 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
42 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
43 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
44 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
45 |  | Operating conditions
46 |  | Process fluid(s) : | input data |  | input data
47 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
48 |  | Service description : | input data |  | input data
49 |  | Process fluid corrosive compounds : | input data |  | input data
50 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
51 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
52 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
53 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | T1: bara; T2: psia; T3: kPaa
54 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
55 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
56 |  | Minimum operating velocity : | input data | m/s | input data | m/s
57 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
58 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
59 |  | Minimum operating liquid specific gravity : | input data |  | input data
60 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
61 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
62 |  | Minimum operating vapour compressibility factor : | input data |  | input data
63 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
64 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
65 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
66 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
67 |  | Normal operating velocity : | input data | m/s | input data | m/s
68 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
69 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
70 |  | Normal operating liquid specific gravity : | input data |  | input data
71 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
72 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
73 |  | Normal operating vapour compressibility factor : | input data |  | input data
74 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
75 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
76 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
77 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
78 |  | Maximum operating velocity : | input data | m/s | input data | m/s
79 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
80 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
81 |  | Maximum operating liquid specific gravity : | input data |  | input data
82 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
83 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
84 |  | Maximum operating vapour compressibility factor : | input data |  | input data
85 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
86 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
87 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
88 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
89 |  | Body/element/sensor
90 |  | Body/element/sensor manufacturer model number : | input data |  | input data
91 |  | Body material : | input data |  | input data
92 |  | Flange material : | input data |  | input data
93 |  | Ultrasonic number of beams : | input data |  | input data
94 |  | Ultrasonic number of transducers : | input data |  | input data
95 |  | Body size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
96 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
97 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
98 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
99 |  | Ultrasonic transducer material : | input data |  | input data
100 |  | Interface gasket material : | input data |  | input data
101 |  | Probe retraction mechanism : | no |  | no | [5 empty] | select | T1: yes; T2: no
102 |  | Transmitter
103 |  | Transmitter model number : | input data |  | input data
104 |  | Transmitter enclosure material : | input data |  | input data
105 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
106 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
107 |  | Transmitter connecting cables : | no |  | no | [5 empty] | select | T1: yes; T2: no
108 |  | Transmitter connecting cable length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
109 |  | Transmitter connecting cable quantity : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4
110 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
111 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
112 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
113 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
114 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
115 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
116 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
117 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
118 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
119 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
120 |  | Protocol version : | input data |  | input data
121 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
122 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
123 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
124 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
125 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
126 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
127 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
128 |  | Performance
129 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
130 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
131 |  | Long term drift : | input data |  | input data
132 |  | Long term stability : | input data |  | input data
133 |  | Accessories
134 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
135 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
136 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the instrument type (technology) to be purchased.
Note on C5: Select the technology used for the ultrasonic measurement.
Note on C6: Select the code compliance for the region where the instrument is to be installed.
Note on C7: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C8: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C9: Specify a functional description of the tag.
Note on C10: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C11: Specify the model number of the offered instrument assembly/unit.
Note on C12: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C13: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C14: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C15: Select the location of the facility where the equipment is to be permanently installed.
Note on C16: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C17: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C18: Specify as per process data.
Note on C19: Specify as per process data.
Note on C20: Select the units to be used, either "normal" or "standard".
Note on C21: Specify the temperature to be used for base units.
Note on C22: Specify the pressure to be used to support the base units.
Note on C23: Select the required project painting durability level.
Note on C24: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C25: Select the nut material as detailed in IOGP S-563.
Note on C26: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C27: Select the ingress protection rating in IP or NEMA.
Note on C28: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C29: Select the code to be followed for the hazardous area classification.
Note on C30: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C31: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C32: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C34: Select the pipe schedule in accordance with the pipe specification.
Note on C35: Specify the process line size to support sizing and selection by the supplier.
Note on C36: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C37: Select the instrument process connection compatible with that declared by the purchaser.
Note on C38: Specify the orientation of the inlet to the instrument or insertion point.
Note on C39: Specify the material which the instrument connects to on the upstream face.
Note on C40: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C41: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C42: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C43: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C44: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C46: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C47: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C48: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C49: Specify any corrosive elements in the process stream.
Note on C50: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C51: Specify the input details to support sizing.
Note on C52: Select whether the instrument could see a vacuum.
Note on C53: Specify the vapour pressure of the flowing fluid.
Note on C54: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C55: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C56: Specify the operating velocity of the system at the minimum sizing case.
Note on C57: Specify the temperature of the process at the minimum sizing case.
Note on C58: Specify the differential pressure of the process at the minimum sizing case.
Note on C59: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C60: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C61: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C62: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C63: Specify the vapour actual density at minimum sizing conditions.
Note on C64: Specify the vapour viscosity at minimum sizing conditions.
Note on C65: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C66: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C67: Specify the operating velocity of the system at the normal sizing case.
Note on C68: Specify the temperature of the process at the minimum sizing case.
Note on C69: Specify the pressure of the process for the normal operating case.
Note on C70: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C71: Specify the viscosity of the process fluid at the normal sizing case.
Note on C72: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C73: Specify the vapour compressibility factor at normal sizing conditions.
Note on C74: Specify the vapour actual density at normal sizing conditions.
Note on C75: Specify the vapour viscosity at normal sizing conditions.
Note on C76: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C77: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C78: Specify the operating velocity of the system at the maximum sizing case.
Note on C79: Specify the temperature of the process at the maximum sizing case.
Note on C80: Specify the pressure of the process for the maximum operating case.
Note on C81: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C82: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C83: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C84: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C85: Specify the vapour actual density at the maximum sizing conditions.
Note on C86: Specify the vapour viscosity at the maximum sizing conditions.
Note on C87: Specify the worst case pressure loss that the system can accept.
Note on C88: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C90: Specify the model number of the body/element/sensor.
Note on C91: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C92: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C93: Specify the number of beams to be in the supplied design.
Note on C94: Specify the number of transducers in the supplied instrument.
Note on C95: Specify the selected instrument body size.
Note on C96: Specify the size of the connection to the process line or equipment.
Note on C97: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C98: Select the flange rating to match the rating of the system to which it is connected.
Note on C99: Specify the transducer holder material and supporting components.
Note on C100: Specify the material of the interface gasket
Note on C101: Select whether the probe is to be designed allowing removal. Default value : no
Note on C103: Specify the model number for the transmitter only.
Note on C104: Specify the material offered to meet the minimum requirements.
Note on C105: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C106: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C107: Select whether external cables are required for connection between the sensor and the transmitter housing or whether they are they integral. Default value : no
Note on C108: Specify the length of cable to support routing from the flow meter body to the transmitter housing.
Note on C109: Select the number of cables needed between the body and the transmitter head.
Note on C110: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C111: Select the required signal type.
Note on C112: Select the type of power supply to the instrument. Default value : hardwired
Note on C113: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C114: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C115: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C116: Select the type of connection for the cable to the transmitter head.
Note on C117: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C118: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C119: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C120: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C121: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C122: Specify the bespoke range when supplier non-standard calibration is required.
Note on C123: Specify the lowest measured point for the instrument.
Note on C124: Specify the highest measured point for the instrument.
Note on C125: Select where the functionality is to be located.
Note on C126: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C127: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C129: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C130: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Note on C131: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C132: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C134: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C135: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C136: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowVortex
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Vortex | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
23 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
24 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
25 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
26 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
27 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
28 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
29 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
30 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
31 |  | Installation conditions
32 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
33 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
34 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
35 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
36 |  | Upstream (high-side) connection orientation : | input data |  | input data
37 |  | Upstream (high-side) material type : | input data |  | input data
38 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
39 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
40 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
41 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
42 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
43 |  | Operating conditions
44 |  | Process fluid(s) : | input data |  | input data
45 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
46 |  | Service description : | input data |  | input data
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
49 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
50 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
51 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | T1: bara; T2: psia; T3: kPaa
52 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
53 | 7.3.3.1 | Minimum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
54 |  | Minimum operating velocity : | input data | m/s | input data | m/s
55 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
56 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
57 |  | Minimum operating liquid specific gravity : | input data |  | input data
58 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
59 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
60 |  | Minimum operating vapour compressibility factor : | input data |  | input data
61 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
62 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
63 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
64 |  | Normal operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h | Sm³/h | Sft³/h | Nm³/h | Nft³/h
65 |  | Normal operating velocity : | input data | m/s | input data | m/s
66 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
67 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
68 |  | Normal operating liquid specific gravity : | input data |  | input data
69 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
70 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
71 |  | Normal operating vapour compressibility factor : | input data |  | input data
72 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
73 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
74 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
75 |  | Maximum operating volumetric flow : | input data | select | input data | select |  |  |  |  | select | Am³/h | Aft³/h, Sm³/h | Sft³/h, Nm³/h | Nft³/h
76 |  | Maximum operating velocity : | input data | m/s | input data | m/s
77 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
78 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
79 |  | Maximum operating liquid specific gravity : | input data |  | input data
80 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
81 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
82 |  | Maximum operating vapour compressibility factor : | input data |  | input data
83 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
84 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
85 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
86 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
87 |  | Body/element/sensor
88 |  | Body/element/sensor manufacturer model number : | input data |  | input data
89 |  | Body material : | input data |  | input data
90 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
91 |  | Flange material : | input data |  | input data
92 |  | Sensor type : | select |  | select | [5 empty] | select | capacitive sensor | piezoelectric sensor | strain gauge sensor | ultrasonic sensor
93 |  | Body size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
94 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
95 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
96 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
97 |  | Online extraction of vortex sensor : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
98 |  | Online extraction integrity check port : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
99 |  | Interface gasket material : | input data |  | input data
100 |  | Mean k-factor : | input data |  | input data
101 |  | Redundant sensors : | no |  | no | [5 empty] | select | T1: yes; T2: no
102 |  | Transmitter
103 |  | Transmitter model number : | input data |  | input data
104 |  | Transmitter enclosure material : | input data |  | input data
105 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
106 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
107 |  | Transmitter connecting cables : | no |  | no | [5 empty] | select | T1: yes; T2: no
108 |  | Transmitter connecting cable length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
109 |  | Transmitter connecting cable quantity : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4
110 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
111 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
112 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
113 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
114 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
115 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
116 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
117 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
118 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
119 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
120 |  | Protocol version : | input data |  | input data
121 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
122 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
123 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
124 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
125 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
126 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
127 |  | Performance
128 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
129 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
130 |  | Long term drift : | input data |  | input data
131 |  | Long term stability : | input data |  | input data
132 |  | Accessories
133 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
134 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
135 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C23: Select the nut material as detailed in IOGP S-563.
Note on C24: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C25: Select the ingress protection rating in IP or NEMA.
Note on C26: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C27: Select the code to be followed for the hazardous area classification.
Note on C28: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C29: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C30: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C32: Select the pipe schedule in accordance with the pipe specification.
Note on C33: Specify the process line size to support sizing and selection by the supplier.
Note on C34: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C35: Select the instrument process connection compatible with that declared by the purchaser.
Note on C36: Specify the orientation of the inlet to the instrument or insertion point.
Note on C37: Specify the material which the instrument connects to on the upstream face.
Note on C38: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C39: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C40: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C41: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C42: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C44: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C45: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C46: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C47: Specify any corrosive elements in the process stream.
Note on C48: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C49: Specify the input details to support sizing.
Note on C50: Select whether the instrument could see a vacuum.
Note on C51: Specify the vapour pressure of the flowing fluid.
Note on C52: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C53: Specify the operating volumetric flow rate of the system at the minimum sizing case.
Note on C54: Specify the operating velocity of the system at the minimum sizing case.
Note on C55: Specify the temperature of the process at the minimum sizing case.
Note on C56: Specify the differential pressure of the process at the minimum sizing case.
Note on C57: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C58: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C59: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C60: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C61: Specify the vapour actual density at minimum sizing conditions.
Note on C62: Specify the vapour viscosity at minimum sizing conditions.
Note on C63: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C64: Specify the operating volumetric flow rate of the system at the normal sizing case.
Note on C65: Specify the operating velocity of the system at the normal sizing case.
Note on C66: Specify the temperature of the process at the minimum sizing case.
Note on C67: Specify the pressure of the process for the normal operating case.
Note on C68: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C69: Specify the viscosity of the process fluid at the normal sizing case.
Note on C70: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C71: Specify the vapour compressibility factor at normal sizing conditions.
Note on C72: Specify the vapour actual density at normal sizing conditions.
Note on C73: Specify the vapour viscosity at normal sizing conditions.
Note on C74: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C75: Specify the operating volumetric flow rate of the system at the maximum sizing case.
Note on C76: Specify the operating velocity of the system at the maximum sizing case.
Note on C77: Specify the temperature of the process at the maximum sizing case.
Note on C78: Specify the pressure of the process for the maximum operating case.
Note on C79: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C80: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C81: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C82: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C83: Specify the vapour actual density at the maximum sizing conditions.
Note on C84: Specify the vapour viscosity at the maximum sizing conditions.
Note on C85: Specify the worst case pressure loss that the system can accept.
Note on C86: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C88: Specify the model number of the body/element/sensor.
Note on C89: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C90: Select the material to be selected for the sensor.
Note on C91: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C92: Select the sensor technology.
Note on C93: Specify the selected instrument body size.
Note on C94: Specify the size of the connection to the process line or equipment.
Note on C95: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C96: Select the flange rating to match the rating of the system to which it is connected.
Note on C97: Select whether the vortex meter is to allow online extraction of the transducer to maintain availability of the process while the instrument is maintained. Default value : yes
Note on C98: Select whether the port will enable the chamber to be tested to ensure no pressure is in the cavity prior to removal of the sensor. Default value : yes
Note on C99: Specify the material of the interface gasket
Note on C100: Specify the figure as detailed ISO 12764.
Note on C101: Select whether redundant sensors and electronics are required. Default value : no
Note on C103: Specify the model number for the transmitter only.
Note on C104: Specify the material offered to meet the minimum requirements.
Note on C105: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C106: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C107: Select whether external cables are required for connection between the sensor and the transmitter housing or whether they are they integral. Default value : no
Note on C108: Specify the length of cable to support routing from the flow meter body to the transmitter housing.
Note on C109: Select the number of cables needed between the body and the transmitter head.
Note on C110: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C111: Select the required signal type.
Note on C112: Select the type of power supply to the instrument. Default value : hardwired
Note on C113: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C114: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C115: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C116: Select the type of connection for the cable to the transmitter head.
Note on C117: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C118: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C119: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C120: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C121: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C122: Specify the bespoke range when supplier non-standard calibration is required.
Note on C123: Specify the lowest measured point for the instrument.
Note on C124: Specify the highest measured point for the instrument.
Note on C125: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C126: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C128: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C129: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Note on C130: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C131: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C133: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C134: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C135: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowCoriolis
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Coriolis | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
23 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
24 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
25 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
26 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
27 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
28 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
29 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
30 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
31 |  | Installation conditions
32 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
33 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
34 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
35 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
36 |  | Upstream (high-side) connection orientation : | input data |  | input data
37 |  | Upstream (high-side) material type : | input data |  | input data
38 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
39 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
40 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
41 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
42 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
43 |  | Operating conditions
44 |  | Process fluid(s) : | input data |  | input data
45 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
46 |  | Service description : | input data |  | input data
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
49 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
50 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
51 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | T1: bara; T2: psia; T3: kPaa
52 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
53 |  | Minimum operating velocity : | input data | m/s | input data | m/s
54 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
55 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
56 |  | Minimum operating liquid specific gravity : | input data |  | input data
57 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
58 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
59 |  | Minimum operating vapour compressibility factor : | input data |  | input data
60 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
61 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
62 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
63 |  | Normal operating velocity : | input data | m/s | input data | m/s
64 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
65 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
66 |  | Normal operating liquid specific gravity : | input data |  | input data
67 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
68 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
69 |  | Normal operating vapour compressibility factor : | input data |  | input data
70 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
71 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
72 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
73 |  | Maximum operating velocity : | input data | m/s | input data | m/s
74 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
75 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
76 |  | Maximum operating liquid specific gravity : | input data |  | input data
77 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
78 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
79 |  | Maximum operating vapour compressibility factor : | input data |  | input data
80 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
81 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
82 |  | Maximum unrecoverable pressure loss : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | mmH2O | inH2O
83 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
84 |  | Body/element/sensor
85 |  | Body/element/sensor manufacturer model number : | input data |  | input data
86 |  | Body material : | input data |  | input data
87 |  | Coriolis tube material : | input data |  | input data
88 |  | Coriolis tube type : | select |  | select | [5 empty] | select | T1: bent; T2: straight
89 |  | Flange material : | input data |  | input data
90 |  | Body size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
91 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
92 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
93 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
94 |  | Coriolis outer casing material : | input data |  | input data
95 |  | Coriolis outer casing burst pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kpag
96 |  | Rupture disc burst pressure : | input data | select | input data | select |  |  |  |  | select | T1: psig; T2: barg; T3: kPag
97 |  | Process secondary containment : | select |  | select | [5 empty] | select | T1: fully rated; T2: with rupture disc; T3: not rated
98 |  | Transmitter
99 |  | Transmitter model number : | input data |  | input data
100 |  | Transmitter enclosure material : | input data |  | input data
101 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
102 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
103 |  | Transmitter connecting cables : | no |  | no | [5 empty] | select | T1: yes; T2: no
104 |  | Transmitter connecting cable length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
105 |  | Transmitter connecting cable quantity : | select |  | select | [5 empty] | select | 1 | 2 | 3 | 4
106 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
107 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
108 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
109 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
110 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
111 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
112 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
113 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
114 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
115 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
116 |  | Protocol version : | input data |  | input data
117 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
118 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
119 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
120 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
121 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
122 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
123 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
124 |  | Performance
125 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
126 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
127 |  | Long term drift : | input data |  | input data
128 |  | Long term stability : | input data |  | input data
129 |  | Accessories
130 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
131 |  | Mounting bracket : | select |  | select | [5 empty] | select | T1: yes; T2: no
132 |  | Mounting bracket material : | select |  | select | [5 empty] | select | T1: 316 SS; T2: other
133 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
134 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C23: Select the nut material as detailed in IOGP S-563.
Note on C24: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C25: Select the ingress protection rating in IP or NEMA.
Note on C26: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C27: Select the code to be followed for the hazardous area classification.
Note on C28: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C29: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C30: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C32: Select the pipe schedule in accordance with the pipe specification.
Note on C33: Specify the process line size to support sizing and selection by the supplier.
Note on C34: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C35: Select the instrument process connection compatible with that declared by the purchaser.
Note on C36: Specify the orientation of the inlet to the instrument or insertion point.
Note on C37: Specify the material which the instrument connects to on the upstream face.
Note on C38: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C39: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C40: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C41: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C42: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C44: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C45: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C46: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C47: Specify any corrosive elements in the process stream.
Note on C48: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C49: Specify the input details to support sizing.
Note on C50: Select whether the instrument could see a vacuum.
Note on C51: Specify the vapour pressure of the flowing fluid.
Note on C52: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C53: Specify the operating velocity of the system at the minimum sizing case.
Note on C54: Specify the temperature of the process at the minimum sizing case.
Note on C55: Specify the differential pressure of the process at the minimum sizing case.
Note on C56: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C57: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C58: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C59: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C60: Specify the vapour actual density at minimum sizing conditions.
Note on C61: Specify the vapour viscosity at minimum sizing conditions.
Note on C62: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C63: Specify the operating velocity of the system at the normal sizing case.
Note on C64: Specify the temperature of the process at the minimum sizing case.
Note on C65: Specify the pressure of the process for the normal operating case.
Note on C66: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C67: Specify the viscosity of the process fluid at the normal sizing case.
Note on C68: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C69: Specify the vapour compressibility factor at normal sizing conditions.
Note on C70: Specify the vapour actual density at normal sizing conditions.
Note on C71: Specify the vapour viscosity at normal sizing conditions.
Note on C72: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C73: Specify the operating velocity of the system at the maximum sizing case.
Note on C74: Specify the temperature of the process at the maximum sizing case.
Note on C75: Specify the pressure of the process for the maximum operating case.
Note on C76: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C77: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C78: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C79: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C80: Specify the vapour actual density at the maximum sizing conditions.
Note on C81: Specify the vapour viscosity at the maximum sizing conditions.
Note on C82: Specify the worst case pressure loss that the system can accept.
Note on C83: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C85: Specify the model number of the body/element/sensor.
Note on C86: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C87: Specify the material for the tube to ensure compatibility with process conditions and mechanical response requirements.
Note on C88: Select whether the tube is bent or straight.
Note on C89: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C90: Specify the selected instrument body size.
Note on C91: Specify the size of the connection to the process line or equipment.
Note on C92: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C93: Select the flange rating to match the rating of the system to which it is connected.
Note on C94: Specify the material of the outer casing surrounding the tubes.
Note on C95: Specify the burst pressure to which the casing is designed.
Note on C96: Specify the burst pressure of the rupture disc integral to the Coriolis flow meter secondary containment.
Note on C97: Select whether process secondary containment is required. Requirement to be based upon a risk assessment considering service conditions, pressure rating, etc.
Note on C99: Specify the model number for the transmitter only.
Note on C100: Specify the material offered to meet the minimum requirements.
Note on C101: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C102: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C103: Select whether external cables are required for connection between the sensor and the transmitter housing or whether they are they integral. Default value : no
Note on C104: Specify the length of cable to support routing from the flow meter body to the transmitter housing.
Note on C105: Select the number of cables needed between the body and the transmitter head.
Note on C106: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C107: Select the required signal type.
Note on C108: Select the type of power supply to the instrument. Default value : hardwired
Note on C109: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C110: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C111: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C112: Select the type of connection for the cable to the transmitter head.
Note on C113: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C114: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C115: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C116: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C117: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C118: Specify the bespoke range when supplier non-standard calibration is required.
Note on C119: Specify the lowest measured point for the instrument.
Note on C120: Specify the highest measured point for the instrument.
Note on C121: Select where the functionality is to be located.
Note on C122: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C123: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C125: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C126: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Note on C127: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C128: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C130: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C131: Select "yes" When remote mount or "no" if direct mount.
Note on C132: Select the mounting bracket material. Minimum material 316 stainless steel but "other" can be selected when more suitable.
Note on C133: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C134: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS FlowThermMass
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Flow Thermal Mass | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
23 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
24 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
25 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
26 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
27 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
28 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
29 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
30 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
31 |  | Fire safe design : | no |  | no | [5 empty] | select | T1: yes; T2: no
32 |  | Installation conditions
33 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
34 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
35 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
36 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
37 |  | Upstream (high-side) connection orientation : | input data |  | input data
38 |  | Upstream (high-side) material type : | input data |  | input data
39 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
40 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
41 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
42 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
43 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
44 |  | Operating conditions
45 |  | Process fluid(s) : | input data |  | input data
46 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
47 |  | Service description : | input data |  | input data
48 |  | Process fluid corrosive compounds : | input data |  | input data
49 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
50 |  | Process fluid specific heat ratio Cp/Cv : | input data |  | input data
51 |  | Process vacuum possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
52 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | T1: bara; T2: psia; T3: kPaa
53 |  | Process fluid plugging : | no |  | no | [5 empty] | select | T1: yes; T2: no
54 |  | Minimum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
55 |  | Minimum operating velocity : | input data | m/s | input data | m/s
56 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
57 |  | Minimum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
58 |  | Minimum operating liquid specific gravity : | input data |  | input data
59 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
60 |  | Minimum operating vapour molecular weight : | input data | g/mol | input data | g/mol
61 |  | Minimum operating vapour compressibility factor : | input data |  | input data
62 |  | Minimum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
63 |  | Minimum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
64 |  | Normal operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
65 |  | Normal operating velocity : | input data | m/s | input data | m/s
66 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
67 |  | Normal operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
68 |  | Normal operating liquid specific gravity : | input data |  | input data
69 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
70 |  | Normal operating vapour molecular weight : | input data | g/mol | input data | g/mol
71 |  | Normal operating vapour compressibility factor : | input data |  | input data
72 |  | Normal operating vapour actual density : | input data | kg/m³ | input data | kg/m³
73 |  | Normal operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
74 |  | Maximum operating mass flow : | input data | select | input data | select |  |  |  |  | select | T1: kg/h; T2: lb/h
75 |  | Maximum operating velocity : | input data | m/s | input data | m/s
76 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
77 |  | Maximum operating pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
78 |  | Maximum operating liquid specific gravity : | input data |  | input data
79 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
80 |  | Maximum operating vapour molecular weight : | input data | g/mol | input data | g/mol
81 |  | Maximum operating vapour compressibility factor : | input data |  | input data
82 |  | Maximum operating vapour actual density : | input data | kg/m³ | input data | kg/m³
83 |  | Maximum operating vapour viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
84 |  | Pulsating flow : | no |  | no | [5 empty] | select | T1: yes; T2: no
85 |  | Body/element/sensor
86 |  | Body/element/sensor manufacturer model number : | input data |  | input data
87 |  | Body material : | input data |  | input data
88 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
89 |  | Sensor type : | select |  | select | [5 empty] | select | T1: constant temperature; T2: constant power
90 |  | Sensing element temperature lower range limit : | input data |  | input data
91 |  | Sensing element temperature upper range limit : | input data |  | input data
92 |  | Sensor insertion length : | input data |  | input data
93 |  | Flange material : | input data |  | input data
94 |  | Body size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
95 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
96 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
97 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
98 |  | Insertion assembly
99 |  | Process connection nominal size : | input data |  | input data
100 |  | Process connection nominal rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
101 |  | Process connection termination type : | input data |  | input data
102 |  | Isolation valve style : | input data |  | input data
103 |  | Valve nominal pressure rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
104 |  | Valve body material : | input data |  | input data
105 |  | Valve seat material : | input data |  | input data
106 |  | Packing material : | input data |  | input data
107 |  | Transmitter
108 |  | Transmitter model number : | input data |  | input data
109 |  | Transmitter enclosure material : | input data |  | input data
110 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
111 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
112 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
113 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
114 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
115 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
116 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
117 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
118 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
119 |  | Protocol version : | input data |  | input data
120 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
121 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
122 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
123 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
124 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
125 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
126 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
127 |  | Performance
128 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
129 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C23: Select the nut material as detailed in IOGP S-563.
Note on C24: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C25: Select the ingress protection rating in IP or NEMA.
Note on C26: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C27: Select the code to be followed for the hazardous area classification.
Note on C28: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C29: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C30: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C31: Select whether a fire safe design is required for the seals for both element extraction and isolation valving. Default value : no
Note on C33: Select the pipe schedule in accordance with the pipe specification.
Note on C34: Specify the process line size to support sizing and selection by the supplier.
Note on C35: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C36: Select the instrument process connection compatible with that declared by the purchaser.
Note on C37: Specify the orientation of the inlet to the instrument or insertion point.
Note on C38: Specify the material which the instrument connects to on the upstream face.
Note on C39: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C40: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C41: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C42: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C43: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C45: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C46: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C47: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C48: Specify any corrosive elements in the process stream.
Note on C49: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C50: Specify the input details to support sizing.
Note on C51: Select whether the instrument could see a vacuum.
Note on C52: Specify the vapour pressure of the flowing fluid.
Note on C53: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C54: Specify the operating mass flow rate of the system at the minimum sizing case.
Note on C55: Specify the operating velocity of the system at the minimum sizing case.
Note on C56: Specify the temperature of the process at the minimum sizing case.
Note on C57: Specify the differential pressure of the process at the minimum sizing case.
Note on C58: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C59: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C60: Specify the vapour molecular weight of the process fluid at minimum sizing conditions.
Note on C61: Specify the vapour compressibility factor at minimum sizing conditions.
Note on C62: Specify the vapour actual density at minimum sizing conditions.
Note on C63: Specify the vapour viscosity at minimum sizing conditions.
Note on C64: Specify the normal operating flow rate of the system into which the instrument is installed.
Note on C65: Specify the operating velocity of the system at the normal sizing case.
Note on C66: Specify the temperature of the process at the minimum sizing case.
Note on C67: Specify the pressure of the process for the normal operating case.
Note on C68: Specify the specific gravity of the process fluid at the normal sizing case.
Note on C69: Specify the viscosity of the process fluid at the normal sizing case.
Note on C70: Specify the vapour molecular weight of the process fluid at normal sizing conditions.
Note on C71: Specify the vapour compressibility factor at normal sizing conditions.
Note on C72: Specify the vapour actual density at normal sizing conditions.
Note on C73: Specify the vapour viscosity at normal sizing conditions.
Note on C74: Specify the operating mass flow rate of the system at the maximum sizing case.
Note on C75: Specify the operating velocity of the system at the maximum sizing case.
Note on C76: Specify the temperature of the process at the maximum sizing case.
Note on C77: Specify the pressure of the process for the maximum operating case.
Note on C78: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C79: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C80: Specify the vapour molecular weight of the process fluid at the maximum sizing conditions.
Note on C81: Specify the vapour compressibility factor at the maximum sizing conditions.
Note on C82: Specify the vapour actual density at the maximum sizing conditions.
Note on C83: Specify the vapour viscosity at the maximum sizing conditions.
Note on C84: Select whether the instrument is to be subjected to pulsating flow. Default value : no
Note on C86: Specify the model number of the body/element/sensor.
Note on C87: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C88: Select the material to be selected for the sensor.
Note on C89: Select how the sensor operates to monitor the flow e.g. will it keep the temperature constant.
Note on C90: Specify the lower range limit of the temperature element.
Note on C91: Specify the upper range limit of the temperature element.
Note on C92: Specify the length that the sensor passes into the system past the internal wall.
Note on C93: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C94: Specify the selected instrument body size.
Note on C95: Specify the size of the connection to the process line or equipment.
Note on C96: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C97: Select the flange rating to match the rating of the system to which it is connected.
Note on C99: Specify the process connection nominal size for the insertion assembly.
Note on C100: Select the rating of the insertion assembly.
Note on C101: Specify the type of connection between the insertion assembly and the body.
Note on C102: Specify the design of isolation supplied.
Note on C103: Select the nominal pressure rating of the valve.
Note on C104: Specify the valve body material.
Note on C105: Specify the seat material.
Note on C106: Specify the details of the material used in the valve packing.
Note on C108: Specify the model number for the transmitter only.
Note on C109: Specify the material offered to meet the minimum requirements.
Note on C110: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C111: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C112: Select the required signal type.
Note on C113: Select the type of power supply to the instrument. Default value : hardwired
Note on C114: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C115: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C116: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C117: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C118: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C119: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C120: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C121: Specify the bespoke range when supplier non-standard calibration is required.
Note on C122: Specify the lowest measured point for the instrument.
Note on C123: Specify the highest measured point for the instrument.
Note on C124: Select where the functionality is to be located.
Note on C125: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C126: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C128: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C129: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelMagGauge
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level Magnetic Gauge | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
19 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
20 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
21 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
22 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
23 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
24 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
25 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
26 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
27 |  | Installation conditions
28 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
29 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
30 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
31 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
32 |  | Upstream (high-side) connection orientation : | input data |  | input data
33 |  | Upstream (high-side) material type : | input data |  | input data
34 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
35 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
36 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
37 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
38 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
39 |  | Downstream (bottom-side) material type : | input data |  | input data
40 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
41 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
42 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
43 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
44 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
45 |  | Operating conditions
46 |  | Service description : | input data |  | input data
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | T1: bara; T2: psia; T3: kPaa
49 |  | Process fluid plugging : | no |  | no | [5 empty] | select | T1: yes; T2: no
50 |  | Minimum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
51 |  | Minimum operating upper fluid specific gravity : | input data |  | input data
52 |  | Minimum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
53 |  | Minimum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kpag
54 |  | Minimum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
55 |  | Minimum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
56 |  | Minimum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
57 |  | Minimum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
58 |  | Minimum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
59 |  | Minimum operating lower fluid specific gravity : | input data |  | input data
60 |  | Minimum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
61 |  | Normal operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
62 |  | Normal operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
63 |  | Normal operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
64 |  | Normal operating upper fluid specific gravity : | input data |  | input data
65 |  | Normal operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
66 |  | Normal operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
67 |  | Normal operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
68 |  | Normal operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
69 |  | Normal operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
70 |  | Normal operating lower fluid density : | input data | kg/m³ | input data | kg/m³
71 |  | Normal operating lower fluid specific gravity : | input data |  | input data
72 |  | Maximum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
73 |  | Maximum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
74 |  | Maximum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
75 |  | Maximum operating upper fluid specific gravity : | input data |  | input data
76 |  | Maximum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
77 |  | Maximum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
78 |  | Maximum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
79 |  | Maximum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
80 |  | Maximum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
81 |  | Maximum operating lower fluid specific gravity : | input data |  | input data
82 |  | Maximum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
83 |  | Interface level
84 |  | Upper level / low pressure process fluid : | input data |  | input data
85 |  | Lower level / high pressure process fluid : | input data |  | input data
86 |  | Upper fluid minimum specific gravity : | input data |  | input data
87 |  | Upper fluid maximum specific gravity : | input data |  | input data
88 |  | Lower fluid minimum specific gravity : | input data |  | input data
89 |  | Lower fluid maximum specific gravity : | input data |  | input data
90 |  | Body/element/sensor
91 |  | Body/element/sensor manufacturer model number : | input data |  | input data
92 |  | Gauge glass type : | select |  | select | [5 empty] | select | T1: reflex; T2: transparent
93 |  | Body material : | input data |  | input data
94 |  | Glass gasket material : | input data |  | input data
95 |  | Glass material : | borosilicate |  | borosilicate | [5 empty] | select | borosilicate | aluminosilicate | quartz | other
96 |  | Glass shield material : | select |  | select | [5 empty] | select | T1: mica; T2: kel-f; T3: not applicable
97 |  | Entire visible length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
98 |  | Flange material : | input data |  | input data
99 |  | Body size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
100 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
101 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
102 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
103 |  | Connection orientation : | select |  | select | [5 empty] | select | side-side | side-top | side-bottom | bottom-top
104 |  | Connection centre-to-centre distance : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
105 |  | High measurement : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
106 |  | Low measurement : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
107 |  | Float stop design : | input data |  | input data
108 |  | Float stop material : | input data |  | input data
109 |  | Chamber vent : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
110 |  | Chamber drain : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
111 |  | Level gauge float model number/type : | input data |  | input data
112 |  | Level gauge scale divisions : | input data | select | input data | select |  |  |  |  | select | T1: in; T2: mm; T3: cm
113 |  | Level gauge indicator casing material : | input data |  | input data
114 |  | Level gauge indicator visible length : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: ft
115 |  | Level gauge indicator wafer bi-colours : | input data |  | input data
116 |  | Transmitter
117 |  | Transmitter accessory required : | no |  | no | [5 empty] | select | T1: yes; T2: no
118 |  | Transmitter model number : | input data |  | input data
119 |  | Transmitter enclosure material : | input data |  | input data
120 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
121 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
122 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
123 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
124 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
125 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
126 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
127 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
128 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
129 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
130 |  | Protocol version : | input data |  | input data
131 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
132 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
133 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
134 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
135 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
136 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
137 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
138 |  | Valves
139 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
140 |  | Connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
141 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
142 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
143 |  | Isolation valve body type : | offset |  | offset | [5 empty] | select | T1: offset; T2: other
144 |  | Isolation valve bonnet style : | bolted |  | bolted | [5 empty] | select | T1: bolted; T2: screwed
145 |  | Excess flow check valve : | no |  | no | [5 empty] | select | T1: no; T2: yes (upper and lower)
146 |  | Vent/drain connection size : | ¾ in |  | ¾ in | [5 empty] | select | T1: 20 mm; T2: ¾ in
147 |  | Vent/drain connection rating : | select |  | select | [5 empty] | select | T1: 3000 psi; T2: 6000 psi; T3: 10000 psi
148 |  | Vent/drain connection type : | select |  | select | [5 empty] | select | T1: NPT(F); T2: other
149 |  | Performance
150 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
151 |  | Long term stability : | input data |  | input data
152 |  | Accessories
153 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
154 |  | Non-frost extension : | no |  | no | [5 empty] | select | T1: yes; T2: no
155 |  | Side arm gauge : | no |  | no | [5 empty] | select | T1: yes; T2: no
156 |  | Level gauge illumination : | select |  | select | [5 empty] | select | T1: yes; T2: no
157 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
158 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
159 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C19: Select the nut material as detailed in IOGP S-563.
Note on C20: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C21: Select the ingress protection rating in IP or NEMA.
Note on C22: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C23: Select the code to be followed for the hazardous area classification.
Note on C24: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C25: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C26: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C28: Select the pipe schedule in accordance with the pipe specification.
Note on C29: Specify the process line size to support sizing and selection by the supplier.
Note on C30: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C31: Select the instrument process connection compatible with that declared by the purchaser.
Note on C32: Specify the orientation of the inlet to the instrument or insertion point.
Note on C33: Specify the material which the instrument connects to on the upstream face.
Note on C34: Select the pipe schedule in accordance with the pipe specification.
Note on C35: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C36: Select the pressure rating of the system connected.
Note on C37: Select the process connection to the system.
Note on C38: Specify the orientation of the inlet or insertion point of the instrument.
Note on C39: Specify the material which the instrument connects to on the downstream face.
Note on C40: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C41: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C42: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C43: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C44: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C46: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C47: Specify any corrosive elements in the process stream.
Note on C48: Specify the vapour pressure of the flowing fluid.
Note on C49: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C50: Select the phase at the upper location.
Note on C51: Specify the specific gravity of the process fluid in the upper section.
Note on C52: Specify the viscosity of the process fluid in the upper section.
Note on C53: Specify the pressure at the upper location.
Note on C54: Specify the upper location temperature.
Note on C55: Specify the pressure at the lower location.
Note on C56: Specify the lower location temperature.
Note on C57: Select the phase at the upper location.
Note on C58: Specify the lower fluid density.
Note on C59: Specify the specific gravity of the process fluid in the upper section.
Note on C60: Specify the viscosity of the process fluid in the upper section.
Note on C61: Specify the pressure at the upper location.
Note on C62: Specify the upper location temperature.
Note on C63: Select the phase at the upper location.
Note on C64: Specify the specific gravity of the process fluid in the upper section.
Note on C65: Specify the viscosity of the process fluid in the upper section.
Note on C66: Specify the pressure at the upper location.
Note on C67: Specify the lower location temperature.
Note on C68: Select the phase at the lower location.
Note on C69: Specify the viscosity of the process fluid in the upper section.
Note on C70: Specify the lower fluid density.
Note on C71: Specify the specific gravity of the process fluid in the upper section.
Note on C72: Specify the pressure at the upper location.
Note on C73: Specify the upper location temperature.
Note on C74: Select the phase at the upper location.
Note on C75: Specify the specific gravity of the process fluid in the upper section.
Note on C76: Specify the viscosity of the process fluid in the upper section.
Note on C77: Specify the phase at the lower location.
Note on C78: Specify the lower location temperature.
Note on C79: Select the phase at the lower location.
Note on C80: Specify the lower fluid density
Note on C81: Specify the specific gravity of the process fluid in the upper section.
Note on C82: Specify the viscosity of the process fluid in the upper section.
Note on C84: Specify the process fluid that resides in the upper process connection.
Note on C85: Specify the process fluid that resides in the lower process connection.
Note on C86: Specify the minimum specific gravity for the upper fluid.
Note on C87: Specify the maximum specific gravity for the upper fluid.
Note on C88: Specify the minimum specific gravity for the lower fluid.
Note on C89: Specify the maximum specific gravity for the lower fluid.
Note on C91: Specify the model number of the body/element/sensor.
Note on C92: Select the type of gauge glass.
Note on C93: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C94: Specify the gasket material providing the seal between the glass and the metal gauge body.
Note on C95: Select the glass material. The most common choice is borosilicate. Default value : borosilicate
Note on C96: Select the glass shield material.
Note on C97: Specify the full visible length of the offered design.
Note on C98: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C99: Specify the selected instrument body size.
Note on C100: Specify the size of the connection to the process line or equipment.
Note on C101: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C102: Select the flange rating to match the rating of the system to which it is connected.
Note on C103: Select the location of flanges for the connection of chamber to process.
Note on C104: Specify the separation distance between process connections, either centreline to centreline or centreline to flange face depending on the orientation of the flanges.
Note on C105: Specify the required high level measurement within the separation range.
Note on C106: Specify the required low level measurement within the separation range.
Note on C107: Specify whether float stops are provided and the method, e.g. dampening springs.
Note on C108: Specify the material for the float stop.
Note on C109: Select to confirm whether the vent is required or leave sealed. Default value : yes
Note on C110: Select to confirm whether the drain is required or leave sealed. Default value : yes
Note on C111: Specify the catalogue part number for float.
Note on C112: Specify the units of measure to be used to mark on the gauge.
Note on C113: Specify the material of the gauge indicator.
Note on C114: Specify the visible length of the indicator. This will confirm what is able to be measured.
Note on C115: Specify the colour requirement for the wafers on the indicator.
Note on C117: Select whether the magnetic level gauge is to be supplied with a transmitter. Default value : no
Note on C118: Specify the model number for the transmitter only.
Note on C119: Specify the material offered to meet the minimum requirements.
Note on C120: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C121: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C122: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C123: Select the required signal type.
Note on C124: Select the type of power supply to the instrument. Default value : hardwired
Note on C125: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C126: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C127: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C128: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C129: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C130: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C131: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C132: Specify the bespoke range when supplier non-standard calibration is required.
Note on C133: Specify the lowest measured point for the instrument.
Note on C134: Specify the highest measured point for the instrument.
Note on C135: Select where the functionality is to be located.
Note on C136: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C137: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C139: Select the pipe schedule in accordance with the pipe specification.
Note on C140: Specify the connection size to the process.
Note on C141: Select the pressure rating of the system connected.
Note on C142: Select the connection type to the process.
Note on C143: Specify the type of valve supplied. Default value : offset
Note on C144: Specify the bonnet style. Default value : bolted
Note on C145: Select whether excess flow check valves are required. Excess flow check valves are generally considered for applications on clean fluid and when fluid vapourizes at atmospheric conditions. Default value : no
Note on C146: Specify the connection size to the level gauge valve. Default value : ¾ in
Note on C147: Select the pressure rating of the system connected.
Note on C148: Select the connection type to the process.
Note on C150: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C151: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C153: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C154: Select whether a non-frost extension is required. When the process fluid is below freezing point, the extension is advisable as frost build is likely to form on the glass, making level reading difficult. Default value : no
Note on C155: Select whether side arms are to be added so that the liquid level is visible along its entire length, i.e. with no blind spots. Default value : no
Note on C156: Select whether the gauge itself is required to have illumination to be able to read the scale.
Note on C157: Select the power supply to the instrument, typically 24V DC loop power. Default value : 24 V DC loop power
Note on C158: Select the required signal type.
Note on C159: Select the type of power supply to the instrument. Default value : hardwired
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelGaugeGlass
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level Gauge Glass | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
19 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
20 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
21 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
22 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
23 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
24 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
25 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
26 |  | Installation conditions
27 |  | Upstream (high-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
28 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
29 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
30 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
31 |  | Upstream (high-side) connection orientation : | input data |  | input data
32 |  | Upstream (high-side) material type : | input data |  | input data
33 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
34 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
35 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
36 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
37 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
38 |  | Downstream (bottom-side) material type : | input data |  | input data
39 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
40 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
41 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
42 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
43 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
44 |  | Operating conditions
45 |  | Service description : | input data |  | input data
46 |  | Process fluid corrosive compounds : | input data |  | input data
47 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | T1: bara; T2: psia; T3: kPaa
48 |  | Process fluid plugging : | no |  | no | [5 empty] | select | T1: yes; T2: no
49 |  | Minimum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
50 |  | Minimum operating upper fluid specific gravity : | input data |  | input data
51 |  | Minimum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
52 |  | Minimum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kpag
53 |  | Minimum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
54 |  | Minimum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
55 |  | Minimum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
56 |  | Minimum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
57 |  | Minimum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
58 |  | Minimum operating lower fluid specific gravity : | input data |  | input data
59 |  | Minimum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
60 |  | Normal operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
61 |  | Normal operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
62 |  | Normal operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
63 |  | Normal operating upper fluid specific gravity : | input data |  | input data
64 |  | Normal operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
65 |  | Normal operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
66 |  | Normal operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
67 |  | Normal operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
68 |  | Normal operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
69 |  | Normal operating lower fluid density : | input data | kg/m³ | input data | kg/m³
70 |  | Normal operating lower fluid specific gravity : | input data |  | input data
71 |  | Maximum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
72 |  | Maximum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
73 |  | Maximum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
74 |  | Maximum operating upper fluid specific gravity : | input data |  | input data
75 |  | Maximum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
76 |  | Maximum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
77 |  | Maximum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
78 |  | Maximum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
79 |  | Maximum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
80 |  | Maximum operating lower fluid specific gravity : | input data |  | input data
81 |  | Maximum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
82 |  | Body/element/sensor manufacturer model number : | input data |  | input data
83 |  | Gauge glass type : | select |  | select | [5 empty] | select | T1: reflex; T2: transparent
84 |  | Body material : | input data |  | input data
85 |  | Glass gasket material : | input data |  | input data
86 |  | Glass material : | borosilicate |  | borosilicate | [5 empty] | select | borosilicate | aluminosilicate | quartz | other
87 |  | Glass shield material : | select |  | select | [5 empty] | select | T1: mica; T2: kel-f; T3: not applicable
88 |  | Entire visible length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
89 |  | Flange material : | input data |  | input data
90 |  | Body size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
91 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
92 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
93 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
94 |  | Connection orientation : | select |  | select | [5 empty] | select | side-side | side-top | side-bottom | bottom-top
95 |  | Connection centre-to-centre distance : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
96 |  | High measurement : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
97 |  | Low measurement : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
98 |  | Chamber vent : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
99 |  | Chamber drain : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
100 |  | Level gauge scale divisions : | input data | select | input data | select |  |  |  |  | select | T1: in; T2: mm; T3: cm
101 |  | Level gauge indicator casing material : | input data |  | input data
102 |  | Valves
103 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
104 |  | Connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
105 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
106 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
107 |  | Isolation valve body type : | offset |  | offset | [5 empty] | select | T1: offset; T2: other
108 |  | Isolation valve bonnet style : | bolted |  | bolted | [5 empty] | select | T1: bolted; T2: screwed
109 |  | Excess flow check valve : | no |  | no | [5 empty] | select | T1: no; T2: yes (upper and lower)
110 |  | Vent/drain connection size : | ¾ in |  | ¾ in | [5 empty] | select | T1: 20 mm; T2: ¾ in
111 |  | Vent/drain connection rating : | select |  | select | [5 empty] | select | T1: 3000 psi; T2: 6000 psi; T3: 10000 psi
112 |  | Vent/drain connection type : | select |  | select | [5 empty] | select | T1: NPT(F); T2: other
113 |  | Accessories
114 |  | Non-frost extension : | no |  | no | [5 empty] | select | T1: yes; T2: no
115 |  | Side arm gauge : | no |  | no | [5 empty] | select | T1: yes; T2: no
116 |  | Level gauge illumination : | select |  | select | [5 empty] | select | T1: yes; T2: no
117 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
118 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
119 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C19: Select the nut material as detailed in IOGP S-563.
Note on C20: Select the ingress protection rating in IP or NEMA.
Note on C21: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C22: Select the code to be followed for the hazardous area classification.
Note on C23: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C24: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C25: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C27: Select the pipe schedule in accordance with the pipe specification.
Note on C28: Specify the process line size to support sizing and selection by the supplier.
Note on C29: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C30: Select the instrument process connection compatible with that declared by the purchaser.
Note on C31: Specify the orientation of the inlet to the instrument or insertion point.
Note on C32: Specify the material which the instrument connects to on the upstream face.
Note on C33: Select the pipe schedule in accordance with the pipe specification.
Note on C34: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C35: Select the pressure rating of the system connected.
Note on C36: Select the process connection to the system.
Note on C37: Specify the orientation of the inlet or insertion point of the instrument.
Note on C38: Specify the material which the instrument connects to on the downstream face.
Note on C39: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C40: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C41: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C42: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C43: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C45: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C46: Specify any corrosive elements in the process stream.
Note on C47: Specify the vapour pressure of the flowing fluid.
Note on C48: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C49: Select the phase at the upper location.
Note on C50: Specify the specific gravity of the process fluid in the upper section.
Note on C51: Specify the viscosity of the process fluid in the upper section.
Note on C52: Specify the pressure at the upper location.
Note on C53: Specify the upper location temperature.
Note on C54: Specify the pressure at the lower location.
Note on C55: Specify the lower location temperature.
Note on C56: Select the phase at the upper location.
Note on C57: Specify the lower fluid density.
Note on C58: Specify the specific gravity of the process fluid in the upper section.
Note on C59: Specify the viscosity of the process fluid in the upper section.
Note on C60: Specify the pressure at the upper location.
Note on C61: Specify the upper location temperature.
Note on C62: Select the phase at the upper location.
Note on C63: Specify the specific gravity of the process fluid in the upper section.
Note on C64: Specify the viscosity of the process fluid in the upper section.
Note on C65: Specify the pressure at the upper location.
Note on C66: Specify the lower location temperature.
Note on C67: Select the phase at the lower location.
Note on C68: Specify the viscosity of the process fluid in the upper section.
Note on C69: Specify the lower fluid density.
Note on C70: Specify the specific gravity of the process fluid in the upper section.
Note on C71: Specify the pressure at the upper location.
Note on C72: Specify the upper location temperature.
Note on C73: Select the phase at the upper location.
Note on C74: Specify the specific gravity of the process fluid in the upper section.
Note on C75: Specify the viscosity of the process fluid in the upper section.
Note on C76: Specify the phase at the lower location.
Note on C77: Specify the lower location temperature.
Note on C78: Select the phase at the lower location.
Note on C79: Specify the lower fluid density
Note on C80: Specify the specific gravity of the process fluid in the upper section.
Note on C81: Specify the viscosity of the process fluid in the upper section.
Note on C82: Specify the model number of the body/element/sensor.
Note on C83: Select the type of gauge glass.
Note on C84: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C85: Specify the gasket material providing the seal between the glass and the metal gauge body.
Note on C86: Select the glass material. The most common choice is borosilicate. Default value : borosilicate
Note on C87: Select the glass shield material.
Note on C88: Specify the full visible length of the offered design.
Note on C89: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C90: Specify the selected instrument body size.
Note on C91: Specify the size of the connection to the process line or equipment.
Note on C92: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C93: Select the flange rating to match the rating of the system to which it is connected.
Note on C94: Select the location of flanges for the connection of chamber to process.
Note on C95: Specify the separation distance between process connections, either centreline to centreline or centreline to flange face depending on the orientation of the flanges.
Note on C96: Specify the required high level measurement within the separation range.
Note on C97: Specify the required low level measurement within the separation range.
Note on C98: Select to confirm whether the vent is required or leave sealed. Default value : yes
Note on C99: Select to confirm whether the drain is required or leave sealed. Default value : yes
Note on C100: Specify the units of measure to be used to mark on the gauge.
Note on C101: Specify the material of the gauge indicator.
Note on C103: Select the pipe schedule in accordance with the pipe specification.
Note on C104: Specify the connection size to the process.
Note on C105: Select the pressure rating of the system connected.
Note on C106: Select the connection type to the process.
Note on C107: Specify the type of valve supplied. Default value : offset
Note on C108: Specify the bonnet style. Default value : bolted
Note on C109: Select whether excess flow check valves are required. Excess flow check valves are generally considered for applications on clean fluid and when fluid vapourizes at atmospheric conditions. Default value : no
Note on C110: Specify the connection size to the level gauge valve. Default value : ¾ in
Note on C111: Select the pressure rating of the system connected.
Note on C112: Select the connection type to the process.
Note on C114: Select whether a non-frost extension is required. When the process fluid is below freezing point, the extension is advisable as frost build is likely to form on the glass, making level reading difficult. Default value : no
Note on C115: Select whether side arms are to be added so that the liquid level is visible along its entire length, i.e. with no blind spots. Default value : no
Note on C116: Select whether the gauge itself is required to have illumination to be able to read the scale.
Note on C117: Select the power supply to the instrument, typically 24V DC loop power. Default value : 24 V DC loop power
Note on C118: Select the required signal type.
Note on C119: Select the type of power supply to the instrument. Default value : hardwired
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelHydro
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level Hydrostatic | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
19 | 4.3.1.2.1 | Pressure-retaining bolt material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
20 | 4.3.1.2.1 | Pressure-retaining nut material : | select |  | select | [5 empty] | select | ID260 | IN100S | IS109 | IX100 | IX120 | not applicable
21 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
22 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
23 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
24 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
25 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
26 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
27 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
28 |  | Installation conditions
29 |  | Upstream (high-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
30 |  | Upstream (high-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
31 |  | Upstream (high-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
32 |  | Upstream (high-side) connection orientation : | input data |  | input data
33 |  | Upstream (high-side) material type : | input data |  | input data
34 |  | Downstream (bottom-side) pipe schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
35 |  | Downstream (bottom-side) line size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
36 |  | Downstream (bottom-side) line equipment rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
37 |  | Downstream (bottom-side) line connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
38 |  | Downstream (bottom-side) connection orientation : | input data |  | input data
39 |  | Downstream (bottom-side) material type : | input data |  | input data
40 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
41 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
42 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
43 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
44 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
45 |  | Operating conditions
46 |  | Process fluid(s) : | input data |  | input data
47 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
48 |  | Service description : | input data |  | input data
49 |  | Process fluid corrosive compounds : | input data |  | input data
50 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
51 |  | Process fluid plugging : | no |  | no | [5 empty] | select | T1: yes; T2: no
52 |  | Minimum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | T1: bar; T2: psi; T3: kPa
53 |  | Normal operating pressure differential : | input data | select | input data | select |  |  |  |  | select | T1: bar; T2: psi; T3: kPa
54 |  | Maximum operating pressure differential : | input data | select | input data | select |  |  |  |  | select | T1: bar; T2: psi; T3: kPa
55 |  | Minimum operating upper fluid density : | input data | kg/m³ | input data | kg/m³
56 |  | Minimum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
57 |  | Minimum operating upper fluid specific gravity : | input data |  | input data
58 |  | Minimum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
59 |  | Minimum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kpag
60 |  | Minimum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
61 |  | Minimum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
62 |  | Minimum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
63 |  | Minimum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
64 |  | Minimum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
65 |  | Minimum operating lower fluid specific gravity : | input data |  | input data
66 |  | Minimum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
67 |  | Normal operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
68 |  | Normal operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
69 |  | Normal operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
70 |  | Normal operating upper fluid density : | input data | kg/m³ | input data | kg/m³
71 |  | Normal operating upper fluid specific gravity : | input data |  | input data
72 |  | Normal operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
73 |  | Normal operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
74 |  | Normal operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
75 |  | Normal operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
76 |  | Normal operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
77 |  | Normal operating lower fluid density : | input data | kg/m³ | input data | kg/m³
78 |  | Normal operating lower fluid specific gravity : | input data |  | input data
79 |  | Maximum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
80 |  | Maximum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
81 |  | Maximum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
82 |  | Maximum operating upper fluid density : | input data | kg/m³ | input data | kg/m³
83 |  | Maximum operating upper fluid specific gravity : | input data |  | input data
84 |  | Maximum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
85 |  | Maximum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
86 |  | Maximum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
87 |  | Maximum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
88 |  | Maximum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
89 |  | Maximum operating lower fluid specific gravity : | input data |  | input data
90 |  | Maximum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
91 |  | Interface level
92 |  | Upper level / low pressure process fluid : | input data |  | input data
93 |  | Lower level / high pressure process fluid : | input data |  | input data
94 |  | Upper fluid minimum specific gravity : | input data |  | input data
95 |  | Upper fluid maximum specific gravity : | input data |  | input data
96 |  | Lower fluid minimum specific gravity : | input data |  | input data
97 |  | Lower fluid maximum specific gravity : | input data |  | input data
98 |  | Body/element/sensor
99 |  | Body/element/sensor manufacturer model number : | input data |  | input data
100 |  | Minimum differential pressure span : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | InH2O
101 |  | Maximum differential pressure span : | input data | select | input data | select |  |  |  |  | select | bar | psi | kPa | mbar | InH2O
102 |  | Transmitter
103 | 4.3.1.1.1 - 4.3.1.1.3, 4.3.1.1.5 | Transmitter body wetted material : | input data |  | input data
104 | 4.3.1.4 | O-ring material : | input data |  | input data
105 |  | Transmitter enclosure material : | input data |  | input data
106 | 4.3.1.1.1 - 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Isolating diaphragm (sensor) material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
107 |  | Isolating diaphragm fill fluid : | input data |  | input data
108 | 4.3.1.1.4 | Isolating diaphragm plating : | none |  | none | [5 empty] | select | T1: none; T2: gold
109 | 4.3.1.1.4 | Isolating diaphragm plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: µm; T2: µin
110 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
111 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
112 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
113 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
114 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
115 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
116 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
117 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
118 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
119 |  | Protocol version : | input data |  | input data
120 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
121 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
122 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
123 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
124 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
125 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
126 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
127 |  | Zero suppression or elevation : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
128 |  | Performance
129 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
130 |  | Long term drift : | input data |  | input data
131 |  | Long term stability : | input data |  | input data
132 |  | Influence of static pressure : | input data | % | input data | %
133 |  | Electronic remote seal (option)
134 |  | Diaphragm seal type - primary : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other
135 |  | Diaphragm seal type - secondary : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other | not applicable
136 |  | Diaphragm seal upper housing material : | input data |  | input data
137 |  | Diaphragm seal lower housing material : | input data |  | input data
138 |  | Connecting cable length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
139 |  | Tag number - secondary transmitter : | input data |  | input data
140 |  | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
141 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | T1: none; T2: gold
142 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: µm, µin
143 |  | Diaphragm seal process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in
144 |  | Diaphragm seal process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
145 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
146 |  | Diaphragm seal (option)
147 |  | Diaphragm seal type : | select |  | select | [5 empty] | select | 2-in extension | 4-in extension | 6-in extension | 8-in extension | flush | other | not applicable
148 | 5.2.5 | Diaphragm seal configuration : | select |  | select | [5 empty] | select | close coupled (single connection) | remote seal (single connection) | balanced system (both capillaries equal length) | unbalanced system (low side capillary - high side direct connected) | unbalanced system (high side seal - low side open to atmosphere) | not applicable
149 |  | Diaphragm seal - sealing material : | select |  | select | [5 empty] | select | graphite | FPM | PTFE | other
150 | 5.2.1, 5.2.2 | Diaphragm seal capillary / armour material : | input data |  | input data
151 |  | Diaphragm seal capillary length : | input data | select | input data | select |  |  |  |  | select | mm | in | m | ft
152 | 5.2.2, 5.2.4, 5.2.5 | Diaphragm seal capillary fill fluid : | input data |  | input data
153 |  | Diaphragm seal upper housing material : | input data |  | input data
154 | 4.3.1.1.1, 4.3.1.1.3, 4.3.1.1.5 | Diaphragm seal lower housing material : | input data |  | input data
155 | 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
156 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | T1: none; T2: gold
157 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: micro-inches; T2: nano-metres
158 |  | Diaphragm seal flushing connection : | select |  | select | [5 empty] | select | one 1/4-18 NPT(F) | two 1/4-18 NPT(F) | one 1/2 -14 NPT(F) | two 1/2-14 NPT(F)
159 |  | Diaphragm seal process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in | not applicable
160 |  | Diaphragm seal process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
161 |  | Diaphragm seal process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
162 |  | Direct connection, atmospheric (option)
163 |  | Process connection size : | select |  | select | [5 empty] | select | 25 mm | 50 mm | 75 mm | 100 mm | 1 in | 2 in | 3 in | 4 in | not applicable
164 |  | Process connection type : | select |  | select | [5 empty] | select | RF | RTJ | FF | not applicable
165 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
166 | 4.3.1.1.3, 4.3.1.1.5, 5.2.3 | Diaphragm seal diaphragm material : | select |  | select | [5 empty] | select | 316 stainless steel | alloy C-276 | alloy 400 | alloy 625 | tantalum
167 |  | Diaphragm seal plating : | select |  | select | [5 empty] | select | T1: none; T2: gold
168 |  | Diaphragm seal plating thickness : | input data | select | input data | select |  |  |  |  | select | T1: micro-inches; T2: micro-metres
169 |  | Manifold (option)
170 |  | Manifold manufacturer : | input data |  | input data
171 |  | Manifold model number : | input data |  | input data
172 |  | Manifold type : | select |  | select | [5 empty] | select | T1: 2-valve; T2: 5-valve; T3: not applicable
173 |  | Manifold assembly orientation : | select |  | select | [5 empty] | select | T1: bottom; T2: side
174 |  | Manifold material : | input data |  | input data
175 |  | Manifold packing material : | input data |  | input data
176 |  | Manifold assembly process connection size : | select |  | select | [5 empty] | select | T1: 12 mm; T2: ½ in; T3: 2 in
177 |  | Manifold assembly process connection type : | select |  | select | [5 empty] | select | NPT(F) | RF | RTJ | FF
178 |  | Manifold assembly process connection rating : | select |  | select | [5 empty] | select | T1: 3 000 psi; T2: 6 000 psi; T3: 10 000 psi
179 |  | Manifold assembly vent/drain connection size : | select |  | select | [5 empty] | select | 6 mm | 12 mm | ½ in | ¼ in
180 |  | Manifold assembly vent/drain connection type : | select |  | select | [5 empty] | select | T1: NPT(F); T2: other
181 |  | Manifold assembly vent/drain connection rating : | select |  | select | [5 empty] | select | T1: 3 000 psi; T2: 6 000 psi; T3: 10 000 psi
182 |  | Manifold valves lockable : | select |  | select | [5 empty] | select | T1: yes; T2: no
183 |  | Accessories
184 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
185 |  | Mounting bracket : | select |  | select | [5 empty] | select | T1: yes; T2: no
186 |  | Mounting bracket material : | select |  | select | [5 empty] | select | T1: 316 SS; T2: other
187 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
188 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the required project painting durability level.
Note on C19: Select the bolting material for pressure-retaining applications as detailed in IOGP S-563.
Note on C20: Select the nut material as detailed in IOGP S-563.
Note on C21: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C22: Select the ingress protection rating in IP or NEMA.
Note on C23: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C24: Select the code to be followed for the hazardous area classification.
Note on C25: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C26: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C27: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C29: Specify the process line size to support sizing and selection by the supplier.
Note on C30: Select the pressure rating of the system connected. ASME B16.36 starts at Cl-300 rating for orifice.
Note on C31: Select the instrument process connection compatible with that declared by the purchaser.
Note on C32: Specify the orientation of the inlet to the instrument or insertion point.
Note on C33: Specify the material which the instrument connects to on the upstream face.
Note on C34: Select the pipe schedule in accordance with the pipe specification.
Note on C35: Specify the downstream process line size to be declared to support sizing and selection by the supplier.
Note on C36: Select the pressure rating of the system connected.
Note on C37: Select the process connection to the system.
Note on C38: Specify the orientation of the inlet or insertion point of the instrument.
Note on C39: Specify the material which the instrument connects to on the downstream face.
Note on C40: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C41: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C42: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C43: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C44: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C46: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C47: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C48: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C49: Specify any corrosive elements in the process stream.
Note on C50: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C51: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C52: Specify the differential pressure of the process at the minimum sizing case.
Note on C53: Specify the differential pressure of the process at the normal sizing case.
Note on C54: Specify the differential pressure of the process at the maximum sizing case.
Note on C55: Specify the upper fluid density.
Note on C56: Select the phase at the upper location.
Note on C57: Specify the specific gravity of the process fluid in the upper section.
Note on C58: Specify the viscosity of the process fluid in the upper section.
Note on C59: Specify the pressure at the upper location.
Note on C60: Specify the upper location temperature.
Note on C61: Specify the pressure at the lower location.
Note on C62: Specify the lower location temperature.
Note on C63: Select the phase at the upper location.
Note on C64: Specify the lower fluid density.
Note on C65: Specify the specific gravity of the process fluid in the upper section.
Note on C66: Specify the viscosity of the process fluid in the upper section.
Note on C67: Specify the pressure at the upper location.
Note on C68: Specify the upper location temperature.
Note on C69: Select the phase at the upper location.
Note on C70: Specify the upper fluid density
Note on C71: Specify the specific gravity of the process fluid in the upper section.
Note on C72: Specify the viscosity of the process fluid in the upper section.
Note on C73: Specify the pressure at the upper location.
Note on C74: Specify the lower location temperature.
Note on C75: Select the phase at the lower location.
Note on C76: Specify the viscosity of the process fluid in the upper section.
Note on C77: Specify the lower fluid density.
Note on C78: Specify the specific gravity of the process fluid in the upper section.
Note on C79: Specify the pressure at the upper location.
Note on C80: Specify the upper location temperature.
Note on C81: Select the phase at the upper location.
Note on C82: Specify the upper fluid density.
Note on C83: Specify the specific gravity of the process fluid in the upper section.
Note on C84: Specify the viscosity of the process fluid in the upper section.
Note on C85: Specify the phase at the lower location.
Note on C86: Specify the lower location temperature.
Note on C87: Select the phase at the lower location.
Note on C88: Specify the lower fluid density
Note on C89: Specify the specific gravity of the process fluid in the upper section.
Note on C90: Specify the viscosity of the process fluid in the upper section.
Note on C92: Specify the process fluid that resides in the upper process connection.
Note on C93: Specify the process fluid that resides in the lower process connection.
Note on C94: Specify the minimum specific gravity for the upper fluid.
Note on C95: Specify the maximum specific gravity for the upper fluid.
Note on C96: Specify the minimum specific gravity for the lower fluid.
Note on C97: Specify the maximum specific gravity for the lower fluid.
Note on C99: Specify the model number of the body/element/sensor.
Note on C100: Specify the minimum differential span that the pressure element is capable of.
Note on C101: Specify the maximum differential span that the pressure element is capable of.
Note on C103: Specify the material of the socket inlet port (wetted part). Input "not applicable" when diaphragm seal type is selected.
Note on C104: Specify the O-ring material (pressure-containing) to meet the specified process requirements. Consider whether explosive decompression standards are to be complied with.
Note on C105: Specify the material offered to meet the minimum requirements.
Note on C106: Specify the material of the diaphragm or bellow (wetted part).
Note on C107: Specify the fill fluid within transmitter pressure capsule within the transmitter body.
Note on C108: Select whether there is hydrogen present, hence risk of embrittlement and therefore the need for gold plating. Default value : none
Note on C109: Specify the calculated thickness supported by calculations.
Note on C110: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C111: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C112: Select the required signal type.
Note on C113: Select the type of power supply to the instrument. Default value : hardwired
Note on C114: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C115: Select the type of connection for the cable to the transmitter head.
Note on C116: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C117: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C118: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C119: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C120: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C121: Specify the bespoke range when supplier non-standard calibration is required.
Note on C122: Specify the lowest measured point for the instrument.
Note on C123: Specify the highest measured point for the instrument.
Note on C124: Select where the functionality is to be located.
Note on C125: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C126: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C127: Specify requirement, if located above the zero point make the units positive or when located below the zero point make units negative, e.g. -100 mm (- 4 in). Supplier to ensure that this is translated to pressure units in the calculation.
Note on C129: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C130: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C131: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C132: Specify the test results in accordance with IEC 62828-2, 6.2.4.
Note on C134: Select the length to which the seal is to protrude (on the primary / high pressure side) to inside the nozzle or flush if no extension is required. If extension is selected, specify the length in the "Additional notes" column.
Note on C135: Select the length to which the seal is to protrude (on the secondary / low pressure) to inside the nozzle or flush if no extension is required.
Note on C136: Specify the upper housing (non wetted) material. Minimum 316 stainless steel is common but depending on the fill fluid, more exotic material selection can apply.
Note on C137: Specify the lower housing (wetted) material. Minimum 316 stainless steel is common but depending on the fill fluid, more exotic material selection can apply.
Note on C138: Specify the length of cable to connect between the primary and secondary transmitters.
Note on C139: Specify the unique tag number for the equipment and to follow the operator's philosophy for tagging globally.
Note on C140: Specify the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C141: Select the option for plating.
Note on C142: Specify the calculated thickness (to be supported by calculations).
Note on C143: Select the size for flanged connection. The default value is normally 50 mm (2 in).
Note on C144: Select the flange finish.
Note on C145: Select the diaphragm flange rating in line with the installed rating and as per piping specification.
Note on C147: Select the length that the seal is to protrude to inside the nozzle or flush if no extension is required.
Note on C148: Select the type of diaphragm seal configuration to be selected for chosen application.
Note on C149: Select the material of seal between the diaphragm and the process connection.
Note on C150: Specify the material suitable for the ambient conditions and fill fluid. Select "not applicable" when it is direct mount.
Note on C151: Specify the length. For a balanced system, the length is to be for both capillaries. For an unbalanced system, refer to the "instrumentation type" data sheet field to determine whether it is high or low pressure leg.
Note on C152: Specify the fill fluid. Silicon or glycerin are standard, subject to the operating temperature of the process. Ensure that it complies with API RP 551, 9.3.1.
Note on C153: Specify the upper housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C154: Specify the lower housing material. Minimum 316 stainless steel is common but depending on the fill fluid more exotic material selection can apply.
Note on C155: Select the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C156: Select the option for gold plating if required for hydrogen service.
Note on C157: Specify the calculated thickness (to be supported by calculations).
Note on C158: Select the size of threaded connection when the flushing function is required.
Note on C159: Select the size for the flanged connection.
Note on C160: Select the flange finish.
Note on C161: Select the diaphragm flange rating in line with the installed rating and as per the piping specification.
Note on C163: Select the size for the flanged connection.
Note on C164: Select the flange finish.
Note on C165: Select the diaphragm flange rating in line with the installed rating and as per the piping specification.
Note on C166: Specify the wetted part material suitable for process fluids requirement, normally 316 stainless steel or hastelloy C-276.
Note on C167: Select the option for plating. Select "yes" if there is hydrogen present and risk of embrittlement.
Note on C168: Specify the calculated thickness (to be supported by calculations).
Note on C170: Specify the manifold make.
Note on C171: Specify the full model number of the manifold being supplied.
Note on C172: Select the manifold type. "2-valve" is normally specified for pressure transmitter applications and "5-valve" for differential pressure. Select "not applicable" if a diaphragm seal is selected.
Note on C173: Select either bottom entry or side entry for connection to transmitter.
Note on C174: Specify the manifold material, normally 316L stainless steel minimum to meet process requirements.
Note on C175: Specify the material used in packing material.
Note on C176: Select the connection size at the boundary point of supplier interface to the process.
Note on C177: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C178: Select the pressure rating of flanged connection.
Note on C179: Select the connection size at the boundary point of suppliers interface to the process.
Note on C180: Select the connection of the manifold to the process. The standard is "NPT(F)" allowing for tubing and fitting connections.
Note on C181: Select the pressure rating of vent/drain connection.
Note on C182: Select whether for the manifold the capability to lock the valves in the position is required.
Note on C184: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C185: Select "yes" When remote mount or "no" if direct mount.
Note on C186: Select the mounting bracket material. Minimum material 316 stainless steel but "other" can be selected when more suitable.
Note on C187: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C188: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelDisp
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level Displacer | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 |  | P&ID number : | input data |  | input data
14 |  | Line or equipment number : | input data |  | input data
15 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
16 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
18 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
19 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
20 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
21 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
22 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
23 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
24 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
25 |  | Installation conditions
26 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
27 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
28 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
29 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
30 |  | Process connection orientation : | input data |  | input data
31 |  | Process connection material type : | input data |  | input data
32 |  | Process connection nozzle/standpipe size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
33 |  | Process connection nozzle/standpipe length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
34 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
35 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
36 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
37 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
38 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
39 |  | Operating conditions
40 |  | Process fluid(s) : | input data |  | input data
41 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
42 |  | Service description : | input data |  | input data
43 |  | Process fluid corrosive compounds : | input data |  | input data
44 |  | Process fluid vapour pressure : | input data | select | input data | select |  |  |  |  | select | T1: bara; T2: psia; T3: kPaa
45 |  | Process vapour operational density : | input data | select | input data | select |  |  |  |  | select | T1: kg/m3; T2: lb/in3
46 |  | Process fluid plugging : | no |  | no | [5 empty] | select | T1: yes; T2: no
47 |  | Minimum operating liquid specific gravity : | input data |  | input data
48 |  | Maximum operating liquid specific gravity : | input data |  | input data
49 |  | Minimum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
50 |  | Minimum operating upper fluid specific gravity : | input data |  | input data
51 |  | Minimum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
52 |  | Minimum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kpag
53 |  | Minimum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
54 |  | Minimum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
55 |  | Minimum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
56 |  | Minimum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
57 |  | Minimum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
58 |  | Minimum operating lower fluid specific gravity : | input data |  | input data
59 |  | Minimum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
60 |  | Maximum operating upper side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
61 |  | Maximum operating upper side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
62 |  | Maximum operating upper fluid phase type : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour
63 |  | Maximum operating upper fluid density : | input data | kg/m³ | input data | kg/m³
64 |  | Maximum operating upper fluid specific gravity : | input data |  | input data
65 |  | Maximum operating upper fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
66 |  | Maximum operating lower side pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
67 |  | Maximum operating lower side temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
68 |  | Maximum operating lower fluid phase type : | select |  | select | [5 empty] | select | T1: gas; T2: liquid; T3: vapour
69 |  | Maximum operating lower fluid density : | input data | kg/m³ | input data | kg/m³
70 |  | Maximum operating lower fluid specific gravity : | input data |  | input data
71 |  | Maximum operating lower fluid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
72 |  | Interface level
73 |  | Upper level / low pressure process fluid : | input data |  | input data
74 |  | Lower level / high pressure process fluid : | input data |  | input data
75 |  | Upper fluid minimum specific gravity : | input data |  | input data
76 |  | Upper fluid maximum specific gravity : | input data |  | input data
77 |  | Lower fluid minimum specific gravity : | input data |  | input data
78 |  | Lower fluid maximum specific gravity : | input data |  | input data
79 |  | Body/element/sensor manufacturer model number : | input data |  | input data
80 | 8.1.6 | Chamber : | supplied with chamber |  | supplied with chamber | [5 empty] | select | T1: supplied with chamber; T2: internals only (no chamber)
81 |  | Body material : | input data |  | input data
82 |  | Flange material : | input data |  | input data
83 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
84 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
85 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
86 |  | Connection orientation : | select |  | select | [5 empty] | select | side-side | side-top | side-bottom | bottom-top
87 |  | Connection centre-to-centre distance : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
88 |  | High measurement : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
89 |  | Low measurement : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
90 |  | Chamber vent : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
91 |  | Chamber drain : | yes |  | yes | [5 empty] | select | T1: yes; T2: no
92 |  | Stilling well : | select |  | select | [5 empty] | select | T1: purchaser's scope; T2: supplier to provide; T3: not applicable
93 |  | Probe installation type : | select |  | select | [5 empty] | select | T1: internal; T2: external chamber
94 |  | Level range : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
95 |  | Chamber required : | no |  | no | [5 empty] | select | T1: yes; T2: no
96 |  | Transmitter
97 | 4.3.1.4 | O-ring material : | input data |  | input data
98 |  | Transmitter enclosure material : | input data |  | input data
99 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
100 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
101 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
102 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
103 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
104 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
105 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
106 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
107 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
108 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
109 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
110 |  | Protocol version : | input data |  | input data
111 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
112 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
113 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
114 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
115 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
116 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
117 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
118 |  | Valves
119 |  | Vent/drain connection size : | ¾ in |  | ¾ in | [5 empty] | select | T1: 20 mm; T2: ¾ in
120 |  | Vent/drain connection rating : | select |  | select | [5 empty] | select | T1: 3000 psi; T2: 6000 psi; T3: 10000 psi
121 |  | Vent/drain connection type : | select |  | select | [5 empty] | select | T1: NPT(F); T2: other
122 |  | Accessories
123 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
124 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
125 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C14: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C15: Specify as per process data.
Note on C16: Specify as per process data.
Note on C17: Select the required project painting durability level.
Note on C18: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C19: Select the ingress protection rating in IP or NEMA.
Note on C20: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C21: Select the code to be followed for the hazardous area classification.
Note on C22: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C23: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C24: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C26: Select the pipe schedule in accordance with the pipe specification.
Note on C27: Specify the size of the connection to the process.
Note on C28: Select the pressure rating of the system connected.
Note on C29: Select the type of the connection to the process.
Note on C30: Specify the orientation of the inlet or insertion point of the instrument (e.g. vertical upwards or angle of orientation).
Note on C31: Specify the material of the process flange.
Note on C32: Specify the diameter of the standpipe/nozzle.
Note on C33: Specify the length of the nozzle/standpipe into which the instrument is to be installed.
Note on C34: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C35: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C36: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C37: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C38: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C40: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C41: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C42: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C43: Specify any corrosive elements in the process stream.
Note on C44: Specify the vapour pressure of the flowing fluid.
Note on C45: Specify the density of the vapour to be declared.
Note on C46: Select whether the process fluid has the potential to plug. If "yes" is selected, specify details in the "Additional notes" column. Default value : no
Note on C47: Specify the specific gravity of the process fluid at the minimum sizing case.
Note on C48: Specify the specific gravity of the process fluid at the maximum sizing case.
Note on C49: Select the phase at the upper location.
Note on C50: Specify the specific gravity of the process fluid in the upper section.
Note on C51: Specify the viscosity of the process fluid in the upper section.
Note on C52: Specify the pressure at the upper location.
Note on C53: Specify the upper location temperature.
Note on C54: Specify the pressure at the lower location.
Note on C55: Specify the lower location temperature.
Note on C56: Select the phase at the upper location.
Note on C57: Specify the lower fluid density.
Note on C58: Specify the specific gravity of the process fluid in the upper section.
Note on C59: Specify the viscosity of the process fluid in the upper section.
Note on C60: Specify the pressure at the upper location.
Note on C61: Specify the upper location temperature.
Note on C62: Select the phase at the upper location.
Note on C63: Specify the upper fluid density.
Note on C64: Specify the specific gravity of the process fluid in the upper section.
Note on C65: Specify the viscosity of the process fluid in the upper section.
Note on C66: Specify the phase at the lower location.
Note on C67: Specify the lower location temperature.
Note on C68: Select the phase at the lower location.
Note on C69: Specify the lower fluid density
Note on C70: Specify the specific gravity of the process fluid in the upper section.
Note on C71: Specify the viscosity of the process fluid in the upper section.
Note on C73: Specify the process fluid that resides in the upper process connection.
Note on C74: Specify the process fluid that resides in the lower process connection.
Note on C75: Specify the minimum specific gravity for the upper fluid.
Note on C76: Specify the maximum specific gravity for the upper fluid.
Note on C77: Specify the minimum specific gravity for the lower fluid.
Note on C78: Specify the maximum specific gravity for the lower fluid.
Note on C79: Specify the model number of the body/element/sensor.
Note on C80: Select whether the instrument is to be supplied as a complete assembly with chamber or not. Default value : supplied with chamber
Note on C81: Specify the material of the main instrument body is a wetted part and should be suitable for the process fluids.
Note on C82: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C83: Specify the size of the connection to the process line or equipment.
Note on C84: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C85: Select the flange rating to match the rating of the system to which it is connected.
Note on C86: Select the location of flanges for the connection of chamber to process.
Note on C87: Specify the separation distance between process connections, either centreline to centreline or centreline to flange face depending on the orientation of the flanges.
Note on C88: Specify the required high level measurement within the separation range.
Note on C89: Specify the required low level measurement within the separation range.
Note on C90: Select to confirm whether the vent is required or leave sealed. Default value : yes
Note on C91: Select to confirm whether the drain is required or leave sealed. Default value : yes
Note on C92: Select whether stilling well is required and so, who supplies.
Note on C93: Select where the probe will be installed to support design selection, e.g. rigid or flexible probe.
Note on C94: Specify the bespoke level range.
Note on C95: Select whether the chamber is required to be supplied with the selected instrument type. When required, a separate document is to support the design. Default value : no
Note on C97: Specify the O-ring material (pressure-containing) to meet the specified process requirements. Consider whether explosive decompression standards are to be complied with.
Note on C98: Specify the material offered to meet the minimum requirements.
Note on C99: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C100: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C101: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C102: Select the required signal type.
Note on C103: Select the type of power supply to the instrument. Default value : hardwired
Note on C104: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C105: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C106: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C107: Select the type of connection for the cable to the transmitter head.
Note on C108: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C109: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C110: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C111: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C112: Specify the bespoke range when supplier non-standard calibration is required.
Note on C113: Specify the lowest measured point for the instrument.
Note on C114: Specify the highest measured point for the instrument.
Note on C115: Select where the functionality is to be located.
Note on C116: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C117: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C119: Specify the connection size to the level gauge valve. Default value : ¾ in
Note on C120: Select the pressure rating of the system connected.
Note on C121: Select the connection type to the process.
Note on C123: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C124: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C125: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelRadarG
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level Radar Gauge | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
23 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
24 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
25 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
26 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
27 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
28 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
29 |  | Installation conditions
30 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
31 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
32 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
33 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
34 |  | Process connection orientation : | input data |  | input data
35 |  | Process connection material type : | input data |  | input data
36 |  | Process connection nozzle/standpipe size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
37 |  | Process connection nozzle/standpipe length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
38 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
39 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
40 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
41 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
42 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
43 |  | Operating conditions
44 |  | Process fluid(s) : | input data |  | input data
45 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
46 |  | Service description : | input data |  | input data
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
49 |  | Process fluid dielectric constant : | input data |  | input data
50 |  | Process vapour operational density : | input data | select | input data | select |  |  |  |  | select | T1: kg/m3; T2: lb/in3
51 |  | Process fluid foam presence : | no |  | no | [5 empty] | select | T1: yes; T2: no
52 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
53 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
54 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
55 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
56 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
57 |  | Minimum operating fluid conductivity : | input data | s/m | input data | s/m
58 |  | Interface level
59 |  | Upper level / low pressure process fluid : | input data |  | input data
60 |  | Lower level / high pressure process fluid : | input data |  | input data
61 |  | Upper fluid minimum dielectric constant : | input data |  | input data
62 |  | Upper fluid maximum dielectric constant : | input data |  | input data
63 |  | Lower fluid minimum dielectric constant : | input data |  | input data
64 |  | Lower fluid maximum dielectric constant : | input data |  | input data
65 |  | Emulsion layer : | select |  | select | [5 empty] | select | T1: yes; T2: no
66 |  | Emulsion layer thickness : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
67 |  | Upper fluid minimum thickness : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
68 |  | Upper fluid maximum thickness : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
69 |  | Body/element/sensor
70 |  | Body/element/sensor manufacturer model number : | input data |  | input data
71 | 8.1.6 | Chamber : | supplied with chamber |  | supplied with chamber | [5 empty] | select | T1: supplied with chamber; T2: internals only (no chamber)
72 |  | Radar gauge antenna / probe material : | input data |  | input data
73 |  | Flange material : | input data |  | input data
74 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
75 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
76 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
77 |  | Stilling well : | select |  | select | [5 empty] | select | T1: purchaser's scope; T2: supplier to provide; T3: not applicable
78 |  | Probe installation type : | select |  | select | [5 empty] | select | T1: internal; T2: external chamber
79 |  | Probe length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
80 |  | Guided wave radar sensor type : | select |  | select | [5 empty] | select | T1: rigid; T2: flexible
81 |  | Interface gasket material : | input data |  | input data
82 |  | Chamber required : | no |  | no | [5 empty] | select | T1: yes; T2: no
83 |  | Dead zone : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
84 |  | Transmitter
85 | 4.3.1.4 | O-ring material : | input data |  | input data
86 |  | Transmitter enclosure material : | input data |  | input data
87 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
88 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
89 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
90 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
91 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
92 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
93 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
94 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
95 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
96 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
97 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
98 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
99 |  | Protocol version : | input data |  | input data
100 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
101 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
102 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
103 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
104 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
105 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
106 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
107 |  | Performance
108 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
109 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
110 |  | Linearity : | input data | % | input data | %
111 |  | Hysteresis : | input data | % | input data | %
112 |  | Long term drift : | input data |  | input data
113 |  | Long term stability : | input data |  | input data
114 |  | Accessories
115 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
116 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
117 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C23: Select the ingress protection rating in IP or NEMA.
Note on C24: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C25: Select the code to be followed for the hazardous area classification.
Note on C26: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C27: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C28: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C30: Select the pipe schedule in accordance with the pipe specification.
Note on C31: Specify the size of the connection to the process.
Note on C32: Select the pressure rating of the system connected.
Note on C33: Select the type of the connection to the process.
Note on C34: Specify the orientation of the inlet or insertion point of the instrument (e.g. vertical upwards or angle of orientation).
Note on C35: Specify the material of the process flange.
Note on C36: Specify the diameter of the standpipe/nozzle.
Note on C37: Specify the length of the nozzle/standpipe into which the instrument is to be installed.
Note on C38: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C39: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C40: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C41: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C42: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C44: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C45: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C46: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C47: Specify any corrosive elements in the process stream.
Note on C48: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C49: Specify the dielectric constant value for the fluid level being measured. Supplier to declare the value to which the instrument can measure down.
Note on C50: Specify the density of the vapour to be declared.
Note on C51: Select whether foam can be formed. When foam is present, additional information is to be provided in the "Supplement" sheet including foam density, expected thickness and stratification of the bubble structure. Default value : no
Note on C52: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C53: Specify the temperature of the process at the minimum sizing case.
Note on C54: Specify the viscosity of the process fluid at the normal sizing case.
Note on C55: Specify the temperature of the process at the maximum sizing case.
Note on C56: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C57: Specify the process condition of the conductivity at the minimum case.
Note on C59: Specify the process fluid that resides in the upper process connection.
Note on C60: Specify the process fluid that resides in the lower process connection.
Note on C61: Specify the dielectric constant value for the fluid level being measured. Supplier to confirm the value to which the instrument can measure down.
Note on C62: Specify the dielectric constant value for the fluid level being measured.
Note on C63: Specify the dielectric constant value for the fluid level being measured.
Note on C64: Specify the dielectric constant value for the fluid level being measured.
Note on C65: Select whether an emulsion layer is possible to form.
Note on C66: Specify the emulsion layer thickness.
Note on C67: Specify the minimum thickness of the upper fluid.
Note on C68: Specify the maximum thickness of the upper fluid.
Note on C70: Specify the model number of the body/element/sensor.
Note on C71: Select whether the instrument is to be supplied as a complete assembly with chamber or not. Default value : supplied with chamber
Note on C72: Specify the material for the probe.
Note on C73: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C74: Specify the size of the connection to the process line or equipment.
Note on C75: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C76: Select the flange rating to match the rating of the system to which it is connected.
Note on C77: Select whether stilling well is required and so, who supplies.
Note on C78: Select where the probe will be installed to support design selection, e.g. rigid or flexible probe.
Note on C79: Specify the design length of the probe, with measurement taken from flange face to end of probe.
Note on C80: Select the guided wave radar flexible cable for the sensor probe is generally used for applications exceeding 1 830 mm (6 ft) in length.
Note on C81: Specify the material of the interface gasket
Note on C82: Select whether the chamber is required to be supplied with the selected instrument type. When required, a separate document is to support the design. Default value : no
Note on C83: Specify the length that the radar level instrument is unable to measure.
Note on C85: Specify the O-ring material (pressure-containing) to meet the specified process requirements. Consider whether explosive decompression standards are to be complied with.
Note on C86: Specify the material offered to meet the minimum requirements.
Note on C87: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C88: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C89: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C90: Select the required signal type.
Note on C91: Select the type of power supply to the instrument. Default value : hardwired
Note on C92: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C93: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C94: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C95: Select the type of connection for the cable to the transmitter head.
Note on C96: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C97: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C98: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C99: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C100: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C101: Specify the bespoke range when supplier non-standard calibration is required.
Note on C102: Specify the lowest measured point for the instrument.
Note on C103: Specify the highest measured point for the instrument.
Note on C104: Select where the functionality is to be located.
Note on C105: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C106: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C108: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C109: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Note on C110: Specify the linearity figure in accordance with IEC 62828 (all parts).
Note on C111: Specify the hysteresis figure in accordance with IEC 62828 (all parts).
Note on C112: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C113: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C115: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C116: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C117: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelNCRadar
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level Non-contact Radar | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Base conditions : | select |  | select | [5 empty] | select | normal | standard
19 |  | Base temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 |  | Base pressure : | input data | select | input data | select |  |  |  |  | select | bara | psia | kPaa | barg | psig | kPag
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
23 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
24 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
25 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
26 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
27 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
28 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
29 |  | Installation conditions
30 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
31 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
32 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
33 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
34 |  | Process connection orientation : | input data |  | input data
35 |  | Process connection material type : | input data |  | input data
36 |  | Process connection nozzle/standpipe size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
37 |  | Process connection nozzle/standpipe length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
38 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
39 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
40 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
41 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
42 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
43 |  | Operating conditions
44 |  | Process fluid(s) : | input data |  | input data
45 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
46 |  | Service description : | input data |  | input data
47 |  | Process fluid corrosive compounds : | input data |  | input data
48 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
49 |  | Process fluid dielectric constant : | input data |  | input data
50 |  | Process vapour operational density : | input data | select | input data | select |  |  |  |  | select | T1: kg/m3; T2: lb/in3
51 |  | Process fluid foam presence : | no |  | no | [5 empty] | select | T1: yes; T2: no
52 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
53 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
54 |  | Minimum operating fluid conductivity : | input data | s/m | input data | s/m
55 |  | Body/element/sensor
56 |  | Body/element/sensor manufacturer model number : | input data |  | input data
57 | 8.1.6 | Chamber : | supplied with chamber |  | supplied with chamber | [5 empty] | select | T1: supplied with chamber; T2: internals only (no chamber)
58 |  | Radar gauge antenna / probe material : | input data |  | input data
59 |  | Flange material : | input data |  | input data
60 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
61 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
62 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
63 |  | Interface gasket material : | input data |  | input data
64 |  | Dead zone : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
65 |  | Radar antenna type : | select |  | select | [5 empty] | select | T1: rod/stick; T2: cone/horn; T3: parabolic
66 |  | Radar frequency : | input data | Hz | input data | Hz
67 |  | Transmitter
68 |  | Transmitter enclosure material : | input data |  | input data
69 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
70 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
71 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
72 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
73 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
74 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
75 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
76 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
77 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
78 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
79 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
80 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
81 |  | Protocol version : | input data |  | input data
82 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
83 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
84 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
85 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
86 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
87 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
88 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
89 |  | Performance
90 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
91 |  | Long term drift : | input data |  | input data
92 |  | Long term stability : | input data |  | input data
93 |  | Accessories
94 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
95 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
96 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the units to be used, either "normal" or "standard".
Note on C19: Specify the temperature to be used for base units.
Note on C20: Specify the pressure to be used to support the base units.
Note on C21: Select the required project painting durability level.
Note on C22: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C23: Select the ingress protection rating in IP or NEMA.
Note on C24: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C25: Select the code to be followed for the hazardous area classification.
Note on C26: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C27: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C28: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C30: Select the pipe schedule in accordance with the pipe specification.
Note on C31: Specify the size of the connection to the process.
Note on C32: Select the pressure rating of the system connected.
Note on C33: Select the type of the connection to the process.
Note on C34: Specify the orientation of the inlet or insertion point of the instrument (e.g. vertical upwards or angle of orientation).
Note on C35: Specify the material of the process flange.
Note on C36: Specify the diameter of the standpipe/nozzle.
Note on C37: Specify the length of the nozzle/standpipe into which the instrument is to be installed.
Note on C38: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C39: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C40: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C41: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C42: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C44: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C45: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C46: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C47: Specify any corrosive elements in the process stream.
Note on C48: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C49: Specify the dielectric constant value for the fluid level being measured. Supplier to declare the value to which the instrument can measure down.
Note on C50: Specify the density of the vapour to be declared.
Note on C51: Select whether foam can be formed. When foam is present, additional information is to be provided in the "Supplement" sheet including foam density, expected thickness and stratification of the bubble structure. Default value : no
Note on C52: Specify the temperature of the process at the minimum sizing case.
Note on C53: Specify the temperature of the process at the maximum sizing case.
Note on C54: Specify the process condition of the conductivity at the minimum case.
Note on C56: Specify the model number of the body/element/sensor.
Note on C57: Select whether the instrument is to be supplied as a complete assembly with chamber or not. Default value : supplied with chamber
Note on C58: Specify the material for the probe.
Note on C59: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C60: Specify the size of the connection to the process line or equipment.
Note on C61: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C62: Select the flange rating to match the rating of the system to which it is connected.
Note on C63: Specify the material of the interface gasket
Note on C64: Specify the length that the radar level instrument is unable to measure.
Note on C65: Select the type of technology used for the antenna.
Note on C66: Specify the frequency of the selected instrument.
Note on C68: Specify the material offered to meet the minimum requirements.
Note on C69: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C70: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C71: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C72: Select the required signal type.
Note on C73: Select the type of power supply to the instrument. Default value : hardwired
Note on C74: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C75: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C76: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C77: Select the type of connection for the cable to the transmitter head.
Note on C78: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C79: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C80: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C81: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C82: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C83: Specify the bespoke range when supplier non-standard calibration is required.
Note on C84: Specify the lowest measured point for the instrument.
Note on C85: Specify the highest measured point for the instrument.
Note on C86: Select where the functionality is to be located.
Note on C87: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C88: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C90: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C91: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C92: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C94: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C95: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C96: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelUltSon
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level Ultrasonic | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 |  | P&ID number : | input data |  | input data
14 |  | Line or equipment number : | input data |  | input data
15 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
16 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
18 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
19 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
20 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
21 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
22 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
23 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
24 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
25 |  | Installation conditions
26 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
27 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
28 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
29 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
30 |  | Process connection orientation : | input data |  | input data
31 |  | Process connection material type : | input data |  | input data
32 |  | Process connection nozzle/standpipe size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
33 |  | Process connection nozzle/standpipe length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
34 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
35 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
36 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
37 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
38 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
39 |  | Operating conditions
40 |  | Process fluid(s) : | input data |  | input data
41 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
42 |  | Service description : | input data |  | input data
43 |  | Process fluid corrosive compounds : | input data |  | input data
44 |  | Process fluid dielectric constant : | input data |  | input data
45 |  | Process vapour operational density : | input data | select | input data | select |  |  |  |  | select | T1: kg/m3; T2: lb/in3
46 |  | Process fluid foam presence : | no |  | no | [5 empty] | select | T1: yes; T2: no
47 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
48 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
49 |  | Minimum operating fluid conductivity : | input data | s/m | input data | s/m
50 |  | Body/element/sensor manufacturer model number : | input data |  | input data
51 | 8.1.6 | Chamber : | supplied with chamber |  | supplied with chamber | [5 empty] | select | T1: supplied with chamber; T2: internals only (no chamber)
52 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
53 |  | Blocking distance : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
54 |  | Flange material : | input data |  | input data
55 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
56 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
57 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
58 |  | Stilling well : | select |  | select | [5 empty] | select | T1: purchaser's scope; T2: supplier to provide; T3: not applicable
59 |  | Probe length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
60 |  | Interface gasket material : | input data |  | input data
61 |  | Chamber required : | no |  | no | [5 empty] | select | T1: yes; T2: no
62 |  | Dead zone : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
63 |  | Transmitter
64 |  | Transmitter enclosure material : | input data |  | input data
65 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
66 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
67 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
68 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
69 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
70 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
71 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
72 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
73 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
74 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
75 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
76 |  | Protocol version : | input data |  | input data
77 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
78 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
79 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
80 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
81 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
82 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
83 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
84 |  | Performance
85 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
86 |  | Long term drift : | input data |  | input data
87 |  | Long term stability : | input data |  | input data
88 |  | Accessories
89 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
90 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
91 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C14: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C15: Specify as per process data.
Note on C16: Specify as per process data.
Note on C17: Select the required project painting durability level.
Note on C18: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C19: Select the ingress protection rating in IP or NEMA.
Note on C20: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C21: Select the code to be followed for the hazardous area classification.
Note on C22: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C23: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C24: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C26: Select the pipe schedule in accordance with the pipe specification.
Note on C27: Specify the size of the connection to the process.
Note on C28: Select the pressure rating of the system connected.
Note on C29: Select the type of the connection to the process.
Note on C30: Specify the orientation of the inlet or insertion point of the instrument (e.g. vertical upwards or angle of orientation).
Note on C31: Specify the material of the process flange.
Note on C32: Specify the diameter of the standpipe/nozzle.
Note on C33: Specify the length of the nozzle/standpipe into which the instrument is to be installed.
Note on C34: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C35: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C36: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C37: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C38: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C40: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C41: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C42: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C43: Specify any corrosive elements in the process stream.
Note on C44: Specify the dielectric constant value for the fluid level being measured. Supplier to declare the value to which the instrument can measure down.
Note on C45: Specify the density of the vapour to be declared.
Note on C46: Select whether foam can be formed. When foam is present, additional information is to be provided in the "Supplement" sheet including foam density, expected thickness and stratification of the bubble structure. Default value : no
Note on C47: Specify the temperature of the process at the minimum sizing case.
Note on C48: Specify the temperature of the process at the maximum sizing case.
Note on C49: Specify the process condition of the conductivity at the minimum case.
Note on C50: Specify the model number of the body/element/sensor.
Note on C51: Select whether the instrument is to be supplied as a complete assembly with chamber or not. Default value : supplied with chamber
Note on C52: Select the material to be selected for the sensor.
Note on C53: Specify the distance from the end of the sensor that is not able to provide a measurement.
Note on C54: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C55: Specify the size of the connection to the process line or equipment.
Note on C56: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C57: Select the flange rating to match the rating of the system to which it is connected.
Note on C58: Select whether stilling well is required and so, who supplies.
Note on C59: Specify the design length of the probe, with measurement taken from flange face to end of probe.
Note on C60: Specify the material of the interface gasket
Note on C61: Select whether the chamber is required to be supplied with the selected instrument type. When required, a separate document is to support the design. Default value : no
Note on C62: Specify the length that the radar level instrument is unable to measure.
Note on C64: Specify the material offered to meet the minimum requirements.
Note on C65: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C66: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C67: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C68: Select the required signal type.
Note on C69: Select the type of power supply to the instrument. Default value : hardwired
Note on C70: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C71: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C72: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C73: Select the type of connection for the cable to the transmitter head.
Note on C74: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C75: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C76: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C77: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C78: Specify the bespoke range when supplier non-standard calibration is required.
Note on C79: Specify the lowest measured point for the instrument.
Note on C80: Specify the highest measured point for the instrument.
Note on C81: Select where the functionality is to be located.
Note on C82: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C83: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C85: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C86: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C87: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C89: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C90: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C91: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelRFCapac
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level RF Capacitance | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
19 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
20 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
21 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
22 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
23 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
24 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
25 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
26 |  | Installation conditions
27 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
28 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
29 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
30 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
31 |  | Process connection orientation : | input data |  | input data
32 |  | Process connection material type : | input data |  | input data
33 |  | Process connection nozzle/standpipe size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
34 |  | Process connection nozzle/standpipe length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
35 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
36 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
37 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
38 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
39 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
40 |  | Operating conditions
41 |  | Process fluid(s) : | input data |  | input data
42 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
43 |  | Service description : | input data |  | input data
44 |  | Process fluid corrosive compounds : | input data |  | input data
45 |  | Process fluid dielectric constant : | input data |  | input data
46 |  | Process vapour operational density : | input data | select | input data | select |  |  |  |  | select | T1: kg/m3; T2: lb/in3
47 |  | Process fluid foam presence : | no |  | no | [5 empty] | select | T1: yes; T2: no
48 |  | Minimum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
49 |  | Normal operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
50 |  | Normal operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
51 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
52 |  | Maximum operating liquid viscosity : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
53 |  | Minimum operating fluid conductivity : | input data | s/m | input data | s/m
54 |  | Body/element/sensor manufacturer model number : | input data |  | input data
55 | 8.1.6 | Chamber : | supplied with chamber |  | supplied with chamber | [5 empty] | select | T1: supplied with chamber; T2: internals only (no chamber)
56 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
57 |  | Sensor insulation/sheath material : | input data |  | input data
58 |  | Flange material : | input data |  | input data
59 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
60 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
61 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
62 |  | Probe length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
63 |  | Interface gasket material : | input data |  | input data
64 |  | Probe type : | select |  | select | [5 empty] | select | T1: ​​​​​​​bare metal; T2: metal insulated with sheath
65 |  | Probe insulation material : | select |  | select | [5 empty] | select | T1: PVDF; T2: TFE; T3: ceramic
66 |  | Dead zone : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
67 |  | Transmitter
68 | 4.3.1.4 | O-ring material : | input data |  | input data
69 |  | Transmitter enclosure material : | input data |  | input data
70 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
71 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
72 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
73 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
74 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
75 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
76 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
77 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
78 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
79 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
80 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
81 |  | Protocol version : | input data |  | input data
82 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
83 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
84 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
85 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
86 |  | Span and zero adjustment : | select |  | select | [5 empty] | select | T1: local; T2: remote; T3: both
87 |  | Lower range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
88 |  | Upper range limit : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | in | °C | °F | barg | psig | kPag | bar | psi | kPa | %
89 |  | Performance
90 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
91 |  | Linearity : | input data | % | input data | %
92 |  | Long term drift : | input data |  | input data
93 |  | Long term stability : | input data |  | input data
94 |  | Accessories
95 |  | Weather enclosure : | select |  | select | [5 empty] | select | T1: yes; T2: no
96 |  | Electrical surge protector : | no |  | no | [5 empty] | select | T1: yes; T2: no
97 |  | Sunshade : | no |  | no | [5 empty] | select | T1: yes; T2: no
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the required project painting durability level.
Note on C19: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C20: Select the ingress protection rating in IP or NEMA.
Note on C21: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C22: Select the code to be followed for the hazardous area classification.
Note on C23: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C24: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C25: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C27: Select the pipe schedule in accordance with the pipe specification.
Note on C28: Specify the size of the connection to the process.
Note on C29: Select the pressure rating of the system connected.
Note on C30: Select the type of the connection to the process.
Note on C31: Specify the orientation of the inlet or insertion point of the instrument (e.g. vertical upwards or angle of orientation).
Note on C32: Specify the material of the process flange.
Note on C33: Specify the diameter of the standpipe/nozzle.
Note on C34: Specify the length of the nozzle/standpipe into which the instrument is to be installed.
Note on C35: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C36: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C37: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C38: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C39: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C41: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C42: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C43: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C44: Specify any corrosive elements in the process stream.
Note on C45: Specify the dielectric constant value for the fluid level being measured. Supplier to declare the value to which the instrument can measure down.
Note on C46: Specify the density of the vapour to be declared.
Note on C47: Select whether foam can be formed. When foam is present, additional information is to be provided in the "Supplement" sheet including foam density, expected thickness and stratification of the bubble structure. Default value : no
Note on C48: Specify the viscosity of the process fluid at minimum sizing conditions.
Note on C49: Specify the temperature of the process at the minimum sizing case.
Note on C50: Specify the viscosity of the process fluid at the normal sizing case.
Note on C51: Specify the temperature of the process at the maximum sizing case.
Note on C52: Specify the viscosity of the process fluid at the maximum sizing conditions.
Note on C53: Specify the process condition of the conductivity at the minimum case.
Note on C54: Specify the model number of the body/element/sensor.
Note on C55: Select whether the instrument is to be supplied as a complete assembly with chamber or not. Default value : supplied with chamber
Note on C56: Select the material to be selected for the sensor.
Note on C57: Specify the sensor insulation/sheath material if the process fluid dielectric value does not allow the capacitive effect to form.
Note on C58: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C59: Specify the size of the connection to the process line or equipment.
Note on C60: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C61: Select the flange rating to match the rating of the system to which it is connected.
Note on C62: Specify the design length of the probe, with measurement taken from flange face to end of probe.
Note on C63: Specify the material of the interface gasket
Note on C64: Select the probe type dependent on whether fluid is conductive or not. Sheath required when fluid is conductive.
Note on C65: Select the insulation material required.
Note on C66: Specify the length that the radar level instrument is unable to measure.
Note on C68: Specify the O-ring material (pressure-containing) to meet the specified process requirements. Consider whether explosive decompression standards are to be complied with.
Note on C69: Specify the material offered to meet the minimum requirements.
Note on C70: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C71: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C72: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C73: Select the required signal type.
Note on C74: Select the type of power supply to the instrument. Default value : hardwired
Note on C75: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C76: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C77: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C78: Select the type of connection for the cable to the transmitter head.
Note on C79: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C80: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C81: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C82: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C83: Specify the bespoke range when supplier non-standard calibration is required.
Note on C84: Specify the lowest measured point for the instrument.
Note on C85: Specify the highest measured point for the instrument.
Note on C86: Select where the functionality is to be located.
Note on C87: Specify the lowest value of the measured variable that a device can be adjusted to measure.
Note on C88: Specify the highest value of the measured variable that a device can be adjusted to measure.
Note on C90: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Note on C91: Specify the linearity figure in accordance with IEC 62828 (all parts).
Note on C92: Specify the long term drift figure in accordance with IEC 62828 (all parts).
Note on C93: Specify the long term stability figure in accordance with IEC 62828 (all parts) over 5 years.
Note on C95: Select whether enclosure is required. When "yes" add to "additional notes" column if enclosure includes other tags.
Note on C96: Select whether the transmitter has protection against high current on the signal cable due to power supply irregularity or lightning surge. Default value : no
Note on C97: Select whether add protection of the transmitter against direct exposure to sun is required. Default value : no
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelTunFork
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level Tuning Fork | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
19 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
20 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
21 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
22 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
23 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
24 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
25 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
26 |  | Installation conditions
27 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
28 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
29 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
30 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
31 |  | Process connection orientation : | input data |  | input data
32 |  | Process connection material type : | input data |  | input data
33 |  | Process connection nozzle/standpipe size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
34 |  | Process connection nozzle/standpipe length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
35 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
36 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
37 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
38 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
39 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
40 |  | Operating conditions
41 |  | Process fluid(s) : | input data |  | input data
42 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
43 |  | Service description : | input data |  | input data
44 |  | Process fluid corrosive compounds : | input data |  | input data
45 |  | Process vapour operational density : | input data | select | input data | select |  |  |  |  | select | T1: kg/m3; T2: lb/in3
46 |  | Process fluid foam presence : | no |  | no | [5 empty] | select | T1: yes; T2: no
47 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
48 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
49 |  | Body/element/sensor manufacturer model number : | input data |  | input data
50 | 8.1.6 | Chamber : | supplied with chamber |  | supplied with chamber | [5 empty] | select | T1: supplied with chamber; T2: internals only (no chamber)
51 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
52 |  | Blocking distance : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
53 |  | Flange material : | input data |  | input data
54 |  | End connection size : | input data | select | input data | select |  |  |  |  | select | T1: mm; T2: in; T3: not applicable
55 |  | End connection flange type : | ASME B16.5 RF |  | ASME B16.5 RF | [5 empty] | select | ASME B16.5 RTJ | ASME B16.5 RF | ASME B16.5 FF | not applicable
56 |  | End connection flange rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500 | not applicable
57 |  | Fork insertion length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
58 |  | Transmitter
59 | 4.3.1.4 | O-ring material : | input data |  | input data
60 |  | Transmitter enclosure material : | input data |  | input data
61 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
62 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
63 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
64 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
65 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
66 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
67 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
68 |  | Reset : | select |  | select | [5 empty] | select | T1: automatic; T2: manual
69 |  | Contact configuration : | select |  | select | [5 empty] | select | T1: contact open on level detected; T2: contact close on level detected
70 |  | Contact material : | input data |  | input data
71 |  | Contact rating : | input data |  | input data
72 |  | Deadband : | select |  | select | [5 empty] | select | T1: fixed; T2: variable
73 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
74 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
75 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
76 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
77 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
78 |  | Protocol version : | input data |  | input data
79 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
80 |  | Performance
81 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
82 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the required project painting durability level.
Note on C19: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C20: Select the ingress protection rating in IP or NEMA.
Note on C21: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C22: Select the code to be followed for the hazardous area classification.
Note on C23: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C24: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C25: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C27: Select the pipe schedule in accordance with the pipe specification.
Note on C28: Specify the size of the connection to the process.
Note on C29: Select the pressure rating of the system connected.
Note on C30: Select the type of the connection to the process.
Note on C31: Specify the orientation of the inlet or insertion point of the instrument (e.g. vertical upwards or angle of orientation).
Note on C32: Specify the material of the process flange.
Note on C33: Specify the diameter of the standpipe/nozzle.
Note on C34: Specify the length of the nozzle/standpipe into which the instrument is to be installed.
Note on C35: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C36: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C37: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C38: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C39: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C41: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C42: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C43: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C44: Specify any corrosive elements in the process stream.
Note on C45: Specify the density of the vapour to be declared.
Note on C46: Select whether foam can be formed. When foam is present, additional information is to be provided in the "Supplement" sheet including foam density, expected thickness and stratification of the bubble structure. Default value : no
Note on C47: Specify the temperature of the process at the minimum sizing case.
Note on C48: Specify the temperature of the process at the maximum sizing case.
Note on C49: Specify the model number of the body/element/sensor.
Note on C50: Select whether the instrument is to be supplied as a complete assembly with chamber or not. Default value : supplied with chamber
Note on C51: Select the material to be selected for the sensor.
Note on C52: Specify the distance from the end of the sensor that is not able to provide a measurement.
Note on C53: Specify the flange material to be compatible with the process conditions, fluid and process connection. For instruments such as clamp on types where there is no flange, specify "not applicable".
Note on C54: Specify the size of the connection to the process line or equipment.
Note on C55: Select the flange type for the selected instrument to be declared. Default value : ASME B16.5 RF
Note on C56: Select the flange rating to match the rating of the system to which it is connected.
Note on C57: Specify the length from the flange face to the switching point on the tuning fork.
Note on C59: Specify the O-ring material (pressure-containing) to meet the specified process requirements. Consider whether explosive decompression standards are to be complied with.
Note on C60: Specify the material offered to meet the minimum requirements.
Note on C61: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C62: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C63: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C64: Select the required signal type.
Note on C65: Select the type of power supply to the instrument. Default value : hardwired
Note on C66: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C67: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C68: Select whether the tuning fork reset configuration is automatic or manual.
Note on C69: Select whether the contact opens or closes on the tuning fork detecting level.
Note on C70: Specify the material for the contact.
Note on C71: Specify the voltage/current that the switch can repeatedly connect and interrupt without degrading its design life.
Note on C72: Typically, fixed deadbands are used for alarms and adjustable deadbands for control . If “variable” is selected, specify the band in “Additional notes”. If “fixed” is selected, specify the value beyond the set point to revert back to normal state.
Note on C73: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C74: Select the type of connection for the cable to the transmitter head.
Note on C75: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C76: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C77: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C78: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C79: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C81: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C82: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Public Review Draft
Public Review Draft
Public Review Draft

## PDS LevelNucl
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Level Nucleonic | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Level application type : | select |  | select | [5 empty] | select | point | continuous | interface
5 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
6 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
7 | 4.1.2.1 | Tag number : | input data |  | input data
8 |  | Service description : | input data |  | input data
9 |  | Manufacturer : | input data |  | input data
10 | 8.3.4.1 | Model number : | input data |  | input data
11 |  | Equipment manufacturer serial number : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
13 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
14 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
15 |  | P&ID number : | input data |  | input data
16 |  | Line or equipment number : | input data |  | input data
17 |  | Vessel diameter (ID) : | input data | select | input data | select |  |  |  |  | select | mm | in
18 |  | Vessel wall thickness : | input data | select | input data | select |  |  |  |  | select | mm | in
19 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
20 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
21 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
22 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
23 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
24 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
25 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
26 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
27 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
28 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
29 |  | Operating conditions
30 |  | Process fluid(s) : | input data |  | input data
31 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
32 |  | Service description : | input data |  | input data
33 |  | Process fluid corrosive compounds : | input data |  | input data
34 |  | Process vapour operational density : | input data | select | input data | select |  |  |  |  | select | T1: kg/m3; T2: lb/in3
35 |  | Process fluid foam presence : | no |  | no | [5 empty] | select | T1: yes; T2: no
36 |  | Minimum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
37 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
38 |  | Source/container
39 |  | Manufacturer model number : | input data |  | input data
40 |  | Source holder type : | select |  | select | [5 empty] | select | lead-filled carbon steel | lead filled 316L stainless steel | solid 316L | other
41 |  | Source type/strength : | input data |  | input data
42 |  | Number of sources : | 1 |  | 1 | [5 empty] | select | T1: 1; T2: 2; T3: 3
43 |  | Dose rate at housing surface : | input data |  | input data
44 |  | Location/orientation : | input data |  | input data
45 |  | Process connection size/type : | input data |  | input data
46 |  | Source shipment container : | select |  | select | [5 empty] | select | T1: integrated; T2: separate
47 |  | Pressure rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
48 |  | Detector
49 |  | Manufacturer model number : | input data |  | input data
50 |  | Type : | select |  | select | [5 empty] | select | T1: point; T2: continuous; T3: continuous flexible
51 |  | Sensor type : | select |  | select | [5 empty] | select | T1: scintillation crystals; T2: plastic scintillator; T3: Geiger Muller
52 |  | Number of detectors : | select |  | select | [5 empty] | select | T1: 1; T2: 2; T3: 3
53 |  | Active/total length : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
54 |  | Transmitter
55 | 4.3.1.4 | O-ring material : | input data |  | input data
56 |  | Transmitter enclosure material : | input data |  | input data
57 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
58 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
59 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
60 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
61 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
62 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
63 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
64 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
65 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
66 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
67 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
68 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
69 |  | Protocol version : | input data |  | input data
70 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
71 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
72 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
73 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
74 |  | Performance
75 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
76 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
Note on C4: Select the type of nucleonic level instrument to be supplied.
Note on C5: Select the code compliance for the region where the instrument is to be installed.
Note on C6: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C7: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C8: Specify a functional description of the tag.
Note on C9: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C10: Specify the model number of the offered instrument assembly/unit.
Note on C11: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C12: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C13: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C14: Select the location of the facility where the equipment is to be permanently installed.
Note on C15: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C16: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C17: Specify the internal diameter of the equipment that the instrumentation is designed to measure.
Note on C18: Specify the equipment wall thickness through which the signal is required to pass.
Note on C19: Specify as per process data.
Note on C20: Specify as per process data.
Note on C21: Select the required project painting durability level.
Note on C22: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C23: Select the ingress protection rating in IP or NEMA.
Note on C24: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C25: Select the code to be followed for the hazardous area classification.
Note on C26: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C27: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C28: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C30: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C31: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C32: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C33: Specify any corrosive elements in the process stream.
Note on C34: Specify the density of the vapour to be declared.
Note on C35: Select whether foam can be formed. When foam is present, additional information is to be provided in the "Supplement" sheet including foam density, expected thickness and stratification of the bubble structure. Default value : no
Note on C36: Specify the temperature of the process at the minimum sizing case.
Note on C37: Specify the temperature of the process at the maximum sizing case.
Note on C39: Specify the model number of the source/container.
Note on C40: Select the source holder type (e.g. lead-filled carbon steel, lead filled 316L stainless steel, solid 316L, other)
Note on C41: Specify the type and strength of radiation (e.g. Cs-137 from 1.85 MBq (0.5 mCi) to 111 GBq (3 Ci) and Co-60 around 9.25 Gbq (250 mCi)).
Note on C42: Select the number of sources supplied as part of this tagged item. The longer the range the potential need for more sources. Default value : 1
Note on C43: Specify the max exposure at the housing. Tends to be country specific e.g. 500uSv/h at 30cm/1m for Sweden, 7.5 uSv/h for UK, 200uSv/h for France, ≤50µSv/h at 3’ for US and Canada etc..
Note on C44: Specify how the source/container are to be mounted and oriented.
Note on C45: Specify the connection required for the source/container to the equipment. Only required to be populated when internal source.
Note on C46: Select whether the sources are to be shipped 'integrated' or 'separate' to the housing.
Note on C47: Select the correct rating compatible with the system connected. Applicable to internal mounted designs only.
Note on C49: Specify the model number of the detector.
Note on C50: Select the type of detector (e.g. point, continuous, continuous flexible).
Note on C51: Select the sensor technology. It is typically scintillation crystals, plastic scintillator or Geiger Muller.
Note on C52: Select the number of detectors required for the application.
Note on C53: Specify the length of the detector required for the selected service.
Note on C55: Specify the O-ring material (pressure-containing) to meet the specified process requirements. Consider whether explosive decompression standards are to be complied with.
Note on C56: Specify the material offered to meet the minimum requirements.
Note on C57: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C58: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C59: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C60: Select the required signal type.
Note on C61: Select the type of power supply to the instrument. Default value : hardwired
Note on C62: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C63: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C64: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C65: Select the type of connection for the cable to the transmitter head.
Note on C66: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C67: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C68: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C69: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C70: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C71: Specify the bespoke range when supplier non-standard calibration is required.
Note on C72: Specify the lowest measured point for the instrument.
Note on C73: Specify the highest measured point for the instrument.
Note on C75: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C76: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Public Review Draft
Public Review Draft
Public Review Draft

## PDS Sand
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Sand | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
5 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
6 | 4.1.2.1 | Tag number : | input data |  | input data
7 |  | Service description : | input data |  | input data
8 |  | Manufacturer : | input data |  | input data
9 | 8.3.4.1 | Model number : | input data |  | input data
10 |  | Equipment manufacturer serial number : | input data |  | input data
11 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
13 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
14 |  | P&ID number : | input data |  | input data
15 |  | Line or equipment number : | input data |  | input data
16 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
17 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
19 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
20 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
21 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
22 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
23 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
24 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
25 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
26 |  | Installation conditions
27 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
28 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
29 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
30 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
31 |  | Process connection material type : | input data |  | input data
32 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
33 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
34 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
35 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
36 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
37 |  | Operating conditions
38 |  | Process fluid(s) : | input data |  | input data
39 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
40 |  | Service description : | input data |  | input data
41 |  | Process fluid corrosive compounds : | input data |  | input data
42 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
43 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
44 |  | Pipe clamp material : | input data |  | input data
45 |  | Transmitter
46 |  | Transmitter enclosure material : | input data |  | input data
47 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
48 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
49 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
50 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
51 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
52 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
53 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
54 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
55 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
56 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
57 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
58 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
59 |  | Protocol version : | input data |  | input data
60 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
61 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
62 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
63 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
64 |  | Performance
65 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
66 |  | Repeatability : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
Note on C4: Select the code compliance for the region where the instrument is to be installed.
Note on C5: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C6: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C7: Specify a functional description of the tag.
Note on C8: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C9: Specify the model number of the offered instrument assembly/unit.
Note on C10: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C11: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C12: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C13: Select the location of the facility where the equipment is to be permanently installed.
Note on C14: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C15: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C16: Specify as per process data.
Note on C17: Specify as per process data.
Note on C18: Select the required project painting durability level.
Note on C19: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C20: Select the ingress protection rating in IP or NEMA.
Note on C21: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C22: Select the code to be followed for the hazardous area classification.
Note on C23: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C24: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C25: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C27: Select the pipe schedule in accordance with the pipe specification.
Note on C28: Specify the size of the connection to the process.
Note on C29: Select the pressure rating of the system connected.
Note on C30: Select the type of the connection to the process.
Note on C31: Specify the material of the process flange.
Note on C32: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C33: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C34: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C35: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C36: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C38: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C39: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C40: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C41: Specify any corrosive elements in the process stream.
Note on C42: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C43: Specify the temperature of the process at the maximum sizing case.
Note on C44: Specify the pipe clamp material.
Note on C46: Specify the material offered to meet the minimum requirements.
Note on C47: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C48: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C49: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C50: Select the required signal type.
Note on C51: Select the type of power supply to the instrument. Default value : hardwired
Note on C52: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C53: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C54: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C55: Select the type of connection for the cable to the transmitter head.
Note on C56: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C57: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C58: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C59: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C60: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C61: Specify the bespoke range when supplier non-standard calibration is required.
Note on C62: Specify the lowest measured point for the instrument.
Note on C63: Specify the highest measured point for the instrument.
Note on C65: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Note on C66: Specify the repeatability of the instrument selected in accordance with the guidelines set out in IEC 62828 (all parts).
Public Review Draft
Public Review Draft
Public Review Draft

## PDS CorrEro
Row | IOGP S-718D (1.011) Procurement Data Sheet for Basic Process Measurement Instruments Corrosion and Erosion | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | Instrumentation type : | select |  | select | [5 empty] | select | erosion - insertion | erosion - clamp on | corrosion - insertion | corrosion - clamp on
5 | 5.1.2, 5.1.3, 6.1.2, 6.1.3, 7.1.2, 7.1.3, 8.1.2, 8.1.3, 9.1.2, 9.1.3, Table 2, Table 3, Table 5, Table 6, Table 8, Table 9, Table 11, Table 12, Table 14, Table 15 | Code requirement : | select |  | select | [5 empty] | select | US | non-US
6 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
7 | 4.1.2.1 | Tag number : | input data |  | input data
8 |  | Service description : | input data |  | input data
9 |  | Manufacturer : | input data |  | input data
10 | 8.3.4.1 | Model number : | input data |  | input data
11 |  | Equipment manufacturer serial number : | input data |  | input data
12 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project country : | input data |  | input data
13 | 4.1.1, 5.1.1 - 5.1.3, 6.1.1 - 6.1.3, 7.1.1 - 7.1.3, 8.1.1 - 8.1.3, 9.1, Tables 1 - 10 | Project region : | input data |  | input data
14 | 4.3.1.3.1 | Plant environmental location : | select |  | select | [5 empty] | select | marine | onshore
15 |  | P&ID number : | input data |  | input data
16 |  | Line or equipment number : | input data |  | input data
17 | 4.1.7.2 | Minimum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
18 | 4.1.7.2 | Maximum ambient temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
19 |  | Coating durability : | select |  | select | [5 empty] | select | low | medium | high | very high | not applicable
20 | 4.1.4 | SIL rating : | select |  | select | [5 empty] | select | 1 | 2 | 3 | not applicable
21 | 4.1.6, 6.2.1 | Ingress protection : | select |  | select | [5 empty] | select | IP66 | NEMA 4X
22 | 4.3.3.1 | Ex protection : | Exia |  | Exia | [5 empty] | select | Exia | Exib | Exic | Exd | Exe | Exma | Exmb | Exmc
23 | 4.3.3.1 | Hazardous area classification standard : | select |  | select | [5 empty] | select | IEC 60079 | NFPA 70 Article 500 | NFPA 70 Article 505
24 | 4.3.3.1 | Explosion hazard classification : | select |  | select | [5 empty] | select | non-hazardous | zone 2 | zone 1 | zone 0 | division 2 | division 1
25 | 4.3.3.1 | Explosion group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | Class I Group A | Class I Group B | Class I Group C | Class I Group D
26 | 4.3.3.1 | Temperature class : | select |  | select | [5 empty] | select | T1 | T2 | T3 | T4 | T5 | T6
27 |  | Installation conditions
28 |  | Process connection schedule : | select |  | select | [5 empty] | select | STD | XS | XXS | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 5S | 10S | 40S | 80S
29 |  | Process connection size : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
30 |  | Process connection rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
31 |  | Process connection type : | select |  | select | [5 empty] | select | T1: RF; T2: RTJ; T3: FF
32 |  | Process connection material type : | input data |  | input data
33 |  | Maximum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
34 |  | Minimum design pressure : | input data | select | input data | select |  |  |  |  | select | T1: barg; T2: psig; T3: kPag
35 |  | Maximum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
36 |  | Minimum design temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
37 |  | Sour service specification : | select |  | select | [5 empty] | select | T1: NACE MR0175/ISO 15156; T2: NACE MR0103/ISO 17945; T3: not applicable
38 |  | Operating conditions
39 |  | Process fluid(s) : | input data |  | input data
40 | 5.2.3 | Process fluid state : | select |  | select | [5 empty] | select | T1: liquid; T2: vapour; T3: gas
41 |  | Service description : | input data |  | input data
42 |  | Process fluid corrosive compounds : | input data |  | input data
43 |  | Process fluid erosion possibility : | select |  | select | [5 empty] | select | T1: yes; T2: no
44 |  | Maximum operating temperature : | input data | select | input data | select |  |  |  |  | select | bar: T1 to T2
45 |  | Body/element/sensor manufacturer model number : | input data |  | input data
46 | 7.2.3.1, 8.3.3.3 | Sensor material : | select |  | select | [5 empty] | select | 316 / 316L stainless steel | 22 % Cr duplex stainless steel | 25 % Cr super duplex stainless steel | 6 % Mo SS | alloy 20 (UNS N08020) | alloy 400 (UNS N04400) | alloy 625 (UNS N06625) | alloy C-276 (UNS N010276) | 90/10 CuNi (UNS C70600) | titanium grade 2 | other
47 |  | Sensor insertion length : | input data |  | input data
48 |  | Pipe clamp material : | input data |  | input data
49 |  | Insertion assembly
50 |  | Insertion type : | select |  | select | [5 empty] | select | T1: manual; T2: hydraulic
51 |  | Process connection nominal size : | input data |  | input data
52 |  | Process connection nominal rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
53 |  | Process connection termination type : | input data |  | input data
54 |  | Isolation valve style : | input data |  | input data
55 |  | Valve nominal pressure rating : | select |  | select | [5 empty] | select | Cl-150 | Cl-300 | Cl-600 | Cl-900 | Cl-1500 | Cl-2500
56 |  | Valve body material : | input data |  | input data
57 |  | Valve seat material : | input data |  | input data
58 |  | Packing material : | input data |  | input data
59 |  | Transmitter
60 |  | Transmitter enclosure material : | input data |  | input data
61 |  | Transmitter mounting : | integrated |  | integrated | [5 empty] | select | T1: integrated; T2: remote
62 |  | Transmitter display : | integral LCD display |  | integral LCD display | [5 empty] | select | T1: integral LCD display; T2: remote indicator; T3: not applicable
63 |  | Supply voltage : | 24 V DC loop power |  | 24 V DC loop power | [5 empty] | select | T1: 24 V DC loop power; T2: external
64 |  | Signal type : | select |  | select | [5 empty] | select | T1: ​​​​​​​24 Vdc; T2: 4-20 mA; T3: mV
65 |  | Power supply type : | hardwired |  | hardwired | [5 empty] | select | hardwired | battery | power over ethernet | solar
66 |  | External power voltage : | input data | select | input data | select |  |  |  |  | select | T1: V AC; T2: V DC
67 |  | Isolated outputs : | not applicable |  | not applicable | [5 empty] | select | T1: yes; T2: no; T3: not applicable
68 |  | Cable entry : | M20 x 1.5 |  | M20 x 1.5 | [5 empty] | select | T1: ½-14 NPTF; T2: M20 x 1.5
69 |  | Cable termination : | select |  | select | [5 empty] | select | T1: screwed; T2: spring loaded
70 | 4.1.2.2 | Communication protocol : | 4-20mA HART |  | 4-20mA HART | [5 empty] | select | 4-20mA HART | Foundation Fieldbus | Wireless HART | ISA 100.11a | Profibus PA | other
71 |  | Wireless antenna type : | internal antenna |  | internal antenna | [5 empty] | select | external antenna | external antenna - extended range | remote antenna | remote antenna - high gain | internal antenna | not applicable
72 | 4.1.7.2 | Wireless update rate : | input data | select | input data | select |  |  |  |  | select | s | min | hrs | days
73 |  | Protocol version : | input data |  | input data
74 | 4.1.2.1 | Fail safe direction : | fail low (NAMUR) |  | fail low (NAMUR) | [5 empty] | select | T1: fail high (NAMUR); T2: fail low (NAMUR)
75 |  | Calibration bespoke : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
76 |  | Minimum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
77 |  | Maximum measurement range : | input data | select | input data | select |  |  |  |  | select | m³/h | ft³/h | kg/h | lb/h | m | mm | in | °C | °F | barg | psig | kPag | bar | psi | kPa | % | g/s
78 |  | Performance
79 | 7.3.1, 7.3.2.2, 7.3.3.2, 7.3.3.3, 8.1.4 | Accuracy : | input data | % of span | input data | % of span
Note on C4: Select the instrument type (technology) to be purchased.
Note on C5: Select the code compliance for the region where the instrument is to be installed.
Note on C6: Select the CAS level to be applied in IOGP S-718Q, Annex A. Default value : D
Note on C7: Specify the unique tag number for the equipment to follow the operator's philosophy for tagging globally.
Note on C8: Specify a functional description of the tag.
Note on C9: Specify the manufacturer's name after the package evaluation, but prior to the purchase order.
Note on C10: Specify the model number of the offered instrument assembly/unit.
Note on C11: Specify the unique identification number for the equipment as prescribed by the supplier.
Note on C12: Specify the name assigned by ISO to the country in ISO 3166-1.
Note on C13: Specify the geographic location of the project within a country which determines the applicability of local regulatory requirements.
Note on C14: Select the location of the facility where the equipment is to be permanently installed.
Note on C15: Specify the P&ID number where the orifice plate assembly is indicated.
Note on C16: Specify the line, vessel or equipment where the instrument assembly is installed for measurement purpose.
Note on C17: Specify as per process data.
Note on C18: Specify as per process data.
Note on C19: Select the required project painting durability level.
Note on C20: Select the relevant SIL level required. For instrumentation not used in a safety loop, select "not applicable".
Note on C21: Select the ingress protection rating in IP or NEMA.
Note on C22: Select the electrical protection for the specified hazardous area (e.g. Exia, Exd). Default value : Exia
Note on C23: Select the code to be followed for the hazardous area classification.
Note on C24: Select the hazardous zone or division in which the functional or physical object is expected to operate.
Note on C25: Select the gas group classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C26: Select the temperature classification of the physical object in accordance with the zone classification (IEC 60079, NFPA 70, Article 505) or division classification (NFPA 70, Article 500).
Note on C28: Select the pipe schedule in accordance with the pipe specification.
Note on C29: Specify the size of the connection to the process.
Note on C30: Select the pressure rating of the system connected.
Note on C31: Select the type of the connection to the process.
Note on C32: Specify the material of the process flange.
Note on C33: Specify the maximum design pressure that should be below the maximum allowable working pressure (MAWP) of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating pressure.
Note on C34: Specify the figure that should be the minimum design pressure of the system into which the instrument is installed.
Note on C35: Specify the temperature that should be below the maximum temperature of the system into which the instrument is installed. Depending on company standards, it can be 10 - 25 % above the maximum operating temperature.
Note on C36: Specify the temperature that should be the minimum design temperature of the system into which the instrument is installed.
Note on C37: Select the code that is not only dependent on the H2S concentration. Other factors include pressure, temperature, pH, and concentration of other contaminants such as chlorides and cyanide.
Note on C39: Specify the process fluid(s) in accordance with the process data sheet to ensure wetted parts compatibility. For interface level, both fluids are to be specified.
Note on C40: Select whether the process fluid state is a liquid, vapour or gas phase.
Note on C41: Specify what service the instrument is required for to assist the supplier in selecting the correct instrument.
Note on C42: Specify any corrosive elements in the process stream.
Note on C43: Select whether the process has erosive particles contained within. If "yes" is selected, provide further details in the "Supplement" sheet.
Note on C44: Specify the temperature of the process at the maximum sizing case.
Note on C45: Specify the model number of the body/element/sensor.
Note on C46: Select the material to be selected for the sensor.
Note on C47: Specify the length that the sensor passes into the system past the internal wall.
Note on C48: Specify the pipe clamp material.
Note on C50: If insertion type is specified, select whether manual or hydraulic extraction is required.
Note on C51: Specify the process connection nominal size for the insertion assembly.
Note on C52: Select the rating of the insertion assembly.
Note on C53: Specify the type of connection between the insertion assembly and the body.
Note on C54: Specify the design of isolation supplied.
Note on C55: Select the nominal pressure rating of the valve.
Note on C56: Specify the valve body material.
Note on C57: Specify the seat material.
Note on C58: Specify the details of the material used in the valve packing.
Note on C60: Specify the material offered to meet the minimum requirements.
Note on C61: Select whether a single integrated assembly or remote mounting of the transmitter is required. Default value : integrated
Note on C62: Select whether add "integral LCD display" or "remote indicator". Default value : integral LCD display
Note on C63: Select the power supply to the instrument, generally 24V DC loop power. Default value : 24 V DC loop power
Note on C64: Select the required signal type.
Note on C65: Select the type of power supply to the instrument. Default value : hardwired
Note on C66: Specify the external power supply to the flow transmitter to be stated. When loop powered then input "not applicable" in Additional notes field.
Note on C67: Select "yes" when isolated from power supply; "no" when not isolated from power supply; "not applicable" if the unit is loop powered. Default value : not applicable
Note on C68: Select the size of the cable gland connection to the transmitter. The transmitter cable entry size should be ½-14 NPTF or M20 x 1.5. Default value : M20 x 1.5
Note on C69: Select the type of connection for the cable to the transmitter head.
Note on C70: Select the communication protocol for the transmitter. Wireless HART is IEC 62591 and ISA 100.11a is IEC 62734. Default value : 4-20mA HART
Note on C71: Select the antenna type most suitable for the application. Default value : internal antenna
Note on C72: Specify the time window allowed for the exchange of data for the instrument. The typical rate is between 1 s and 60 min.
Note on C73: Specify the required version of supplied protocol. The default version of HART is 7. Earlier versions on HART® 5 and HART® 6 do not support the wireless.
Note on C74: Select the the fail direction for transmitters when the status is faulty. Default value : fail low (NAMUR)
Note on C75: Specify the bespoke range when supplier non-standard calibration is required.
Note on C76: Specify the lowest measured point for the instrument.
Note on C77: Specify the highest measured point for the instrument.
Note on C79: Specify the required accuracy for the complete supplied assembly in accordance with IEC 62828 (all parts).
Public Review Draft
Public Review Draft
Public Review Draft

## Supplement
Row |  | IOGP S-718D (1.011) Procurement Data Sheets for Basic Process Measurement Instruments | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
Public Review Draft

## Guidance
IOGP S-718D (1.011) Procurement Data Sheets for
Basic Process Measurement Instruments
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-718 Specification for Basic Process Measurement Instruments.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
Public Review Draft
Public Review Draft

## Back Cover
Public Review Draft