## Front & Preliminaries
|  |  |  | SPECIFICATION | JANUARY
|  |  |  | S-615L | 2019
Information Requirements for Centrifugal Pumps
Revision history
| VERSION | DATE | AMENDMENTS
| 1.0 | January 2019 | Issued for Publication
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Project 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
Information requirements for
Centrifugal Pumps
Foreword
This specification was prepared under a Joint Industry Project 33 (JIP33) “Standardization of Equipment Specifications for Procurement” organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Ten key oil and gas companies from the IOGP membership participated in developing this specification under JIP33 Phase 2 with the objective to leverage and improve industry level standardization for projects globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, based on the ten participating members’ company specifications, resulting in a common and jointly approved specification, and building on recognized industry and/or international standards.
This specification has been developed in consultation with a broad user and supplier base to promote the opportunity to realize benefits from standardization and achieve significant cost reductions for upstream project costs. The JIP33 work groups performed their activities in accordance with IOGP’s Competition Law Guidelines (November 2014).
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The vision from the CPC industry is to standardize specifications for global procurement for equipment and packages, facilitating improved standardization of major projects across the globe. While individual oil and gas companies have been improving standardization within their own businesses, this has limited value potential and the industry lags behind other industries and has eroded value by creating bespoke components in projects.
This specification aims to significantly reduce this waste, decrease project costs and improve schedule through pre-competitive collaboration on standardization.
Following agreement of the relevant JIP33 work group and approval by the JIP33 Steering Committee, the IOGP Management Committee has agreed to the publication of this specification by IOGP. Where adopted by the individual operating companies, this specification and associated documentation aims to supersede existing company documentation for the purpose of industry-harmonized standardization.
IOGP S-615L Version 1.0
Information requirements for
Centrifugal Pumps
Introduction
The purpose of this information requirements specification (IRS) is to define information requirements for the supply of Centrifugal Pumps for Petroleum and Natural Gas Industries in accordance with ANSI/API Std 610 for application in the petroleum and natural gas industries. This document defines the information requirements, including format, timing and purpose, for information to be provided by the vendor. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the supplementary requirements specification (IOGP S-615), quality requirements specification (IOGP S-615Q) and equipment datasheets (IOGP S-615D) which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification
IOGP S-615L Version 1.0

## IRS Cover
Insert Buyer Logo Here |  |  | Information Requirements for |  |  | Insert Project Logo Here
Centrifugal Pumps
| CLIENT : |  |  | Insert Client_name
| PROJECT TITLE : |  |  | Insert Project Title
| PROJECT LOCATION : |  |  | Insert Project_location
| JOB/PROJECT NUMBER : |  |  | Insert Job/Project number here
| TAG No. : |  |  | Insert Tag_No
| SERVICE : |  |  | Insert Service Description
| DOCUMENT NUMBER : |  |  | Insert Project Document Number
| REVISION : |  |  | Insert Project Document Revision
Issue | Date | Issue Description |  |  | By |  | Checked | Approved
IOGP S-615L Version 1.0 | [8 empty] | Sheet 1 of | 1
Note on N17: Optional Text : Intended for service description such as "Water Treatment Area 400V Switchboard"
Note on N21: Author: Project Specific document number and format
Note on N23: Author: Project specification Revision number and format

## Deliverables
Information requirements for Centrifugal Pumps
Deliverables
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Deliverable, referencing the Parent Standard, IOGP Supplement or Industry Standard where the Information is requested. e.g. API610#01, S-615#01
B | Requirement - a short description of the Information Deliverable that would typically provide the Information required, based on the description in the Parent Standard, IOGP Supplement or an Industry Standard Title.
C | Condition Invoking Requirement - describes special condition(s) under which the Information Deliverable is required; e.g.. service offshore and weight greater than 1 tonne means information is required. NB: if blank, always required
D | Typical Deliverable - Purchaser to advise the short description of the Information Deliverable that would typically include this Information Requirement
E | Submit With Proposal - Yes or No, where ‘Yes' means the Information Deliverable is required to be submitted with Suppliers Proposal or 'No' is not required
F, G & H | First Issue Post Purchase Order - issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the Information Deliverable and Period defined after Purchase Order placement
I | Required As Built - Yes or No, where ‘Yes' means the Information Deliverable is required to be 'As Built' on completion or delivery of equipment or 'No' is not required 'As Built'
J | Fulfilled by Information Deliverable Number(s) – identifies which Information Deliverable(s) listed in the Supplier Master Information Schedule (SMIS) addresses the Purchasers requirements. NB; it should be noted that one Information Deliverable can fulfil more than one Information Requirement.
K | Translation Required -Yes or No, where 'Yes' means the Information Deliverable should be translated into a language(s) (to be advised) other than English and 'No' means to be provided in English
L | Remarks - may include bid clarification questions & decisions (specify author & date)
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
MD#01 | Supplier master information schedule |  | Information Deliverables List | No | For Acceptance |  | WAO | Yes
MD#02 | Delivery schedule |  | Delivery/Production Schedule | Yes | For Information |  | WAO | No
MD#03 | Progress report |  | Progress Report | No | For Information |  | WAO (Monthly) | No
MD#04 | Quality plan | Required for CAS A, B, C | Quality Plan
MD#06 | Sub-vendor delivery schedule |  | Sub-Supplier List | Yes | For Information |  | WAO (Monthly) | No
MD#07 | Inspection and test plan for complete package |  | Inspection and Test Plan (ITP) | No | For Acceptance |  | WAO | No
MD#08 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No
MD#09 | Non-conformance records |  | Nonconformance History | No | For Acceptance |  | WAO | Yes
MD#10 | Concession requests |  | Concession request | No | For Acceptance |  | WAO | Yes
Technical Information Deliverables
API 610#01 | Pump performance curves |  | Performance Curves | Yes | For Acceptance |  | WAO | Yes
API 610#02 | Noise data sheets |  | Noise Data Sheets | Yes | For Information |  | WAO | Yes
API 610#03 | Installation, operation and maintenance instructions index |  | Installation, Operation and Maintenance Manual Index | No | For Information |  | WAO | No
API 610#04 | Installation, operation and maintenance instructions |  | Installation, Operation and Maintenance Manual | No | For Information |  | WPTD | No
API 610#05 | Shaft and rotor total indicator (TIR) reading certificates | Required for CAS A, B, C | Shaft and rotor TIR certificates
API 610#06 | Wear part running clearance certificates | Required for CAS A, B, C | Wear part running clearance certificates
API 610#07 | Torsional critical speed analysis | Needed if specified on the data sheet | Speed Analysis | No | For Acceptance |  | WAO | No
API 610#08 | Performance test data |  | Performance Test Data | No | For Acceptance |  | WAT | No |  |  | Submit within 24 h after test
API 610#09 | Rotating component balancing certificates | required for CAS A, B | Impeller balancing certificates
API 610#10 | Non-destructive examination records | Non-pressure casing components NDE certificates needed if specified on the data sheet. Required if CAS A, B, C | NDE certificates
API 610#11 | Material certificates |  | Material certificates | No | For Acceptance |  | WPTF | Yes
API 610#12 | Weld procedures, procedure qualification records and weld maps | Required for CAS A, B, C | Weld Procedures
API 610#13 | Surface preparation and painting inspection certificates | Required for CAS A, B, C | Surface preparation and inspection certificates
API 610#14 | Major weld repair certificates | Needed if major weld repair performed | Major weld repair certificates | No | For Acceptance |  | WAT | Yes
API 610#15 | Welders qualifications | Required for CAS A, B, C | Welders qualifications
API 610#16 | Heat treatment certificates | Required for CAS A, B, C | Heat treatment certificates
API 610#17 | Nameplate Drawing |  | Nameplate Drawings | No | For Acceptance |  | WPTD | No
API 610#18 | Baseplate flatness and coplanarity certificates | Required for CAS A, B, C | Baseplate flatness and coplanarity certificates
API 610#19 | Nozzle forces and moments testing certificates | Needed if specified on the data sheet. | Nozzle forces and moments testing certificates | No | For Acceptance |  | WAT | Yes
API 610#20 | Special tools list | Needed if special tools are specified | Special Tools List | Yes | For Information |  | WAO | No
API 610#21 | Positive material identification certificates | Non-pressure casing components PMI certificates needed if specified on the data sheet. Required if CAS A, B, C | PMI certificates
API 610#22 | Performance and mechanical run test procedures | Test procedure for vertical pumps that cannot be tested as a complete assembly is also be submitted with proposal | Test Procedures | Yes | For Information |  | WPTT | No
API 610#23 | Optional test procedures | Needed if specified on the data sheet. | Test procedures | Yes | For Information |  | WPTT | No |  |  | Outline of the procedures are also be submitted with proposal
API 610#24 | Certified hydrostatic test data |  | Test Data | No | For Acceptance |  | WAT | No |  |  | Where ANSI/API Std 610, 8.3.2.10 and 8.2.2.3 apply, test report is to be submitted as quickly as possible to minimise delay in post hydrotest machining
API 610#25 | Disassembly after testing certificates | Needed if specified on the data sheet. | Disassembly after testing certificates | No | For Acceptance |  | WAT | Yes
API 610#26 | Optional test data and reports | Needed if optional test are specified on the data sheet | Test Reports | No | For Acceptance |  | WAT | No
API 610#27 | Structural resonance test certificates | Needed if specified on the data sheet. | Structural resonance test certificates | No | For Acceptance |  | WAT | Yes
API 610#28 | Certified dimensional outline drawings |  | Dimensional Data | Yes | For Acceptance |  | WAO | Yes
API 610#29 | Cross-sectional drawings and bills of materials |  | Drawings | Yes | For Information |  | WAO | Yes
API 610#30 | Overall package piping and instrument diagram |  | Piping and Instrument Diagrams | Yes | For Acceptance |  | WAO | Yes
API 610#31 | Data sheets |  | Data Sheets | Yes | For Acceptance |  | WAO | Yes
API 610#32 | Recommended spare parts |  | List of recommended spare parts and SPIR forms for complete package | Yes | For Information |  | WPTD | Yes
API 610#33 | Utility requirements |  | Utlity Schedule | Yes | For Information |  | WAO | No
API 610#34 | Lubrication schedule |  | Lubrication Schedule | No | For Information |  | WAO | No
API 610#35 | Inspection and test equipment calibration certificates | Required for CAS A, B, C | Inspection and test equipment calibration certificates
API 610#36 | Lateral critical speed analysis | Needed if specified on the data sheet | Speed Analysis | No | For Acceptance |  | WAO | No
API 610#37 | Damped unbalanced response analysis | Needed if specified on the data sheet |  | No | For Acceptance |  | WAO | No
API 610#38 | Material safety data sheets | Needed if any fluids are included in the Vendor's scope | 'Material Safety Data Sheets | Yes | For Information |  | WAO | No
API 610#39 | Electrical and instrumentation wiring diagrams | Needed for pumps with condition monitoring, (dual) seal systems and pressurised lube systems | Electrical Diagrams | No | For Acceptance |  | WAO | Yes
API 610#40 | Motor performance data |  | Motor Perfomance Data | No | For Acceptance |  | WAO | No
API 610#41 | Shaft coupling assembly drawing and bill of materials |  | Assembly Drawings | No | For Acceptance |  | WAO | Yes
API 610#42 | Shaft seal drawing and bills of materials |  | Assembly Drawings | Yes | For Acceptance |  | WAO | Yes
API 610#43 | Overall package piping systems schematics and bills of materials |  | Piping systems schematics and bills of materials | No | For Acceptance |  | WAO | Yes
API 610#44 | Pump speed-torque curve superimposed on motor driver speed-torque curves |  | Performance Curves | No | For Acceptance |  | WAO | No
S-615#01 | Warm-up (or Cool-down) procedure | If required by the Vendor | Procedures | No | For Information |  | WAO | No
S-615#02 | Instrument data Ssheets | Needed if instruments are included in the Vendor's scope | Instrument Data Sheets | No | For Acceptance |  | WAO | Yes
S-615#03 | Instrument list | Needed if instruments are included in the Vendor's scope | Instrument List | No | For Information |  | WAO | No
S-615#04 | Non-destructive examination procedures | Required for CAS A, B, C | Non-Destructive Examination Procedure
S-615#05 | Non-destructive examination operators qualifications | Required for CAS A, B, C | NDE operators qualifications
S-615#06 | Certified hydrostatic test procedure |  | Test Procedures | No | For Information |  | WPTT | No
S-615#07 | Impeller as-built drawing | Needed if impeller was modified after test (with Purchaser's approval) by underfiling, overfilling, V-cutting or any other such technique to correct hydraulic performance | Impeller Drawings | No | For Information |  | WAT | Yes
S-615#08 | Painting procedure |  | Painting Procedure | Yes | For Information |  | WPTD | No
S-615#09 | Manufacturing record book index |  | Manufacturer Record Book Index | No | For Acceptance |  | WAO | No
S-615#10 | Manufacturing record book |  | Manufacturer Record Book | No | For Acceptance |  | WPTD | Yes
S-615#11 | Declaration of conformity |  | Declaration of Conformity | No | For Acceptance |  | WPTD | No

## Definitions
Information requirements for Centrifugal Pumps
Definitions
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Deliverable, referencing the Parent Standard, IOGP Supplement or Industry Standard where the Information is requested. e.g. API610#01, S-614#01
B | Requirement - a short description of the Information Deliverable that would typically provide the Information required, based on the description in the Parent Standard, IOGP Supplement or an Industry Standard Title.
C | Description - an excerpt from the Parent Standard, IOGP Supplement or Industry Standard.
D | Reference - reference to the Parent Standard, IOGP Supplement or Industry Standard that the Information Deliverable is identified in.
E | Format - defines the required format of the relevant Information Deliverable to be submitted by Vendor for Purchaser/Contractor for information and acceptance as shown in Table 9.1 of Instructions Tab and selected from pick list.
F | CFIHOS Discipline Document Type Code - the CFIHOS discipline document type that could be used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Deliverables
MD#01 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a) information deliverable type, title/description b) unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c) planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. | ANSI/API Std 610 10.3.1.1 | Native
MD#02 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by [vendor/sub-vendors] Schedule details typically** include;. a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and sub-vendor) e) Information deliverable submission dates identifying any execution activity dependencies Once agreed , changes to planned dates are subject to agreement by [purchaser]. Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [vendor's] standard practice unless otherwise agreed in the contract. | ANSI/API Std 610 10.2.3.d | PDF
MD#03 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. | ANSI/API Std 610 10.3.3, Annex L | PDF
MD#04 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] | Contract Requirement | PDF
MD#06 | Sub-vendor delivery schedule | Definition of processes, products or services that will be externally provided and the controls to be applied by the [vendor] to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . Note: ISO 9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. | Contract Requirement | Native
MD#07 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. | Contract Requirement | PDF
MD#08 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a) Packaging requirements; contents, identification, size, weight and number of packages/container (s), b) special packing/unpacking/handling requirements c) storage location and requirements, d) preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. | ANSI/API Std 610 8.4, Annex L S-615 8.4 | PDF
MD#09 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. | Contract Requirement | PDF
MD#10 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout | Contract Requirement | PDF
Technical Information Deliverables
API 610#01 | Pump performance curves | As per the requirements of 10.2.4, 10.3.2.2 of ANSI/API Std 610, with the addition, as applicable, of the following: - all duty points, including the guarantee point; - for viscous duties, the viscous duty performance curves including maximum expected powers based on worst case cold start and normal viscous conditions. Performance curves based on water performance are also be provided; - the curves to be based on the internal clearances proposed by Vendor after making allowances for any added clearance based on temperature, viscosity, particulates and wear component galling tendencies; - for pumps with discharge orifices proposed, pump performance curves are to be provided to reflect predicted performance with and without the orifice installed. | ANSI/API Std 610 6.1, 9.3.1.1, 10.2.4, Annex L S-615, 6.1, 6.7.4.d | PDF
API 610#02 | Noise data sheets | For Proposal : Predicted overall package noise data including any noise attenuation devices (if included in the Vendor's scope). For Acceptance: noise data sheets including individual pump, driver, gear (if any) and auxiliary equipment octave band centre frequency sound power and sound pressure level plus guaranteed overall sound power and sound pressure levels including any noise attenuation devices (if included in the Vendor's scope). | ANSI/API Std 610, 6.1.14, 10.2.3.b, Annex L, | PDF
API 610#03 | Installation, operation and maintenance instructions index | Installation, Operation and Maintenance Instructions Index is to be agreed prior to submission of the manual. Each manual and sub-vendor manual is to include the below listed sections as a minimum. Index to also include full sub-indices details. Note that the Installation, Operation and Maintenance Manual is not to contain any SMIR documents that have been formally submitted to the Purchaser during the contract but listed and referenced. Section 1 - Installation: as per the requirements of ANSI/API Std 610, L.2.1 cc) 1) with the following change: delete vii). Section 2 - Commissioning, start-up and operation procedures and acceptance criteria: i) lubrication recommendations; ii) pre-commissioning/pre-start-up checks and tests; iv) operation and shutdown procedures; iii) acceptance checks and tests. Section 3 - Disassembly and reassembly: as per the requirements of ANSI/API Std 610, L.2.1 cc) 3) with the following change: add viii) fastener torques. Section 4 - Any start-up, shutdown or operating restrictions required to protect the integrity of the equipment Section 5 - Operating procedures for special tools, if any Section 6 - Driver Installation, Operation and Maintenance Manuals: Section 7 - Mechanical Seal Installation, Operation and Maintenance Manuals Section 8 - All auxiliary equipment (add sections as appropriate), Installation, Operation and Maintenance Manuals Section 9 - Troubleshooting | ANSI/API Std 610 6.4.3.14, 6.11.2, 10.3.5, Annex L S-615, 7.6.3 | PDF
API 610#04 | Installation, operation and maintenance instructions | Provides sufficient information to install, operate and maintain the equipment, as well as sufficient information for troubleshooting. Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package vendor. 'Description of methods of operating a piece of equipment or process unit, including but not limited to instructions, procedures, drawings, tables, etc. for the operation -stop, start, and emergency shutdown. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. NOTE: Unless otherwise agreed, can be delivered in manufacturer's standard manual or as one or several documents clearly marked which part they cover (I, O, M) | ANSI/API Std 610 6.4.3.14 6.11.2, 10.3.5, Annex L S-615, 7.6.3 | PDF
API 610#05 | Shaft and rotor total indicator (TIR) reading certificates | Certificates detailing all shaft run-out checks, including phase relation for each displacement probe location on pumps, motors, steam turbines and gear units. | ANSI/API Std 610 6.6, 9.3.3.1, 9.3.12.2.d, Table 17, Table 19 | PDF
API 610#06 | Wear part running clearance certificates | Certificates detailing all as-built close clearances and those specified at Purchase. | ANSI/API Std 610 Table 6; S-615 6.7.4 | PDF
API 610#07 | Torsional critical speed analysis | As per the requirements of 6.9.2.10 of ANSI/API Std 610. | ANSI/API Std 610 6.9.2.10, Annex L S-615, 6.9.2.10 | PDF
API 610#08 | Performance test data | As per the requirements of L.2.1 u) of ANSI/API Std 610, with the following change: - performance test data is to include Fast Fourier Transform spectra for each test point. | ANSI/API Std 610 6.9.3, 8.3.3, 10.3.2.2, Annex L S-615, 6.9.3, 8.3.3. | PDF
API 610#09 | Rotating component balancing certificates | The certificate to be provided by the manufacturer recording the results of the balancing of all rotating elements to the specified grade in accordance with the Purchaser accepted balancing procedure. To include residual unbalance check. | ANSI/API Std 610 6.9.4, 9.1.3.7, 9.2.4; S-615 6.9.4, 9.1.3.7, 9.2.4; S-615D | PDF
API 610#10 | Non-destructive examination records | Detailed non-destructive examination reports describing procedure used, results obtained and action for visual, radiographic, ultrasonic, magnetic particle, and dye-penetrant examinations. Reports shall be signed and dated by an authorized operator and identify components tested, location, heat-treated condition, and other requirements per Project specifications. | ANSI/API Std 610 6.12.1.5, 8.2.1.3 | PDF
API 610#11 | Material certificates | Certificate type shall be as required by the QRS/Project requirements. Material test certificates shall include as a minimum chemical analysis, mechanical test results and heat treatment condition. Additional data to satisfy Project requirements. | ANSI/API Std 610 6.12.1.8, 6.12.4.3, 8.2.2.7, Annex H Tables H.2 and H.4; S-615 6.12.1.8, 8.2.2.7; S-615D | PDF
API 610#12 | Weld procedures, procedure qualification records and weld maps | WPSs and PQRs proposed for each different weld and materials type including weld maps to clearly show the location and type of the proposed weld. For proposed major weld repairs, weld repair maps showing location and major dimensions of weld repair cavities, qualification records, drawings, photographs, heat treatment detail, NDE requirements and other specified documents are also be submitted. | ANSI/API Std 610 6.12.2, 6.12.3, 6.12.4, Annex L S-615, 6.12.2 | PDF
API 610#13 | Surface preparation and painting inspection certificates | Certification confirming that the unpainted equipment meets the visual requirements of MSS SP-55. Certificate to include Purchaser's PO number; item or tag number, and shall verify that painting and/or insulation is in accordance with the Purchaser's specifications or the Purchaser accepted specifications, as applicable. To include intermediate coat number/checks, temperature, humidity, DFT, coverage/opacity, colour etc. and signed by the painting/insulation contractor. | ANSI/API Std 610 6.12.2.1, 7.3.12, 8.4.2.4; S-615 6.1.37.3, 8.4.2.4, 9.3.8.3.3 | PDF
API 610#14 | Major weld repair certificates | Certification that major weld repairs have been satisfactorily completed and inspected according to the same quality standard used to inspect the casting. | ANSI/API Std 610 6.12.2.3; S-615 6.12.2.3, 6.12.2.5 | PDF
API 610#15 | Welders qualifications | Qualification of all welders or welding operators using approved weld procedures and by weld position in accordance with project specifications. Welders name, identification and positions to be recorded to code requirements with approval by third party inspection authority when applicable. | ANSI/API Std 610 Table 11; S-615D | PDF
API 610#16 | Heat treatment certificates | Scanned Original or wet stamped verified copies of pyrometric charts or certificates confirming the heat treatment cycles have been conducted to the Purchaser's/Material specification's requirements. To include charts for any heat treatment conducted such as, during forming, normalising, quenching, post-weld heat treatment, rotor heat stability testing. Certificates to state PO number, item number, and identification to permit traceability to the heat-treated component or materials. | ANSI/API Std 610 Table 11; S-615D | PDF
API 610#17 | Nameplate Drawing | Nameplate data content is to be as per API 610 clause 6.13.2/S-615 clause 6.13.2. Font size minimum 5mm. Nameplate language per PO. | ANSI/API Std 610 6.13.2; S-615, 6.13.2 | PDF
API 610#18 | Baseplate flatness and coplanarity certificates | Certification confirming that all the machinery mounting pads of the baseplate have been fully machined flat and that their surfaces are in the same plane within 150 μm/m (0,002 in/ft) of distance between the pads. | ANSI/API Std 610 7.3; S-615 7.3 | PDF
API 610#19 | Nozzle forces and moments testing certificates | Certification confirming that when subjected to moments MYc and MZc applied to either nozzle, the shaft displacement the drive end or at the register fit of the coupling hub are within the values shown in ANSI/API Std 610 11th ed., Table 13. | ANSI/API Std 610 7.3.21 | PDF
API 610#20 | Special tools list | As per the requirements of L.2.1 g) of ANSI/API Std 610. | ANSI/API Std 610 7.6, 10.2.3.g | PDF
API 610#21 | Positive material identification certificates | Certification that the alloying element percentages of materials subject to verification are in accordance with the proposed recognised material specification. | ANSI/API Std 610 8.2.2.8; S-615 8.2.2.8; S-615D | PDF
API 610#22 | Performance and mechanical run test procedures | As per the requirements of 8.3.1.1, 8.3.1.2, 8.3.3.3 of ANSI/API Std 610 with the following change: - add description of the test setup and instrumentation. | ANSI/API Std 610 8.3.1, 8.3.3, 8.3.4; S-615, 8.3.1, 8.3.3, 8.3.4, 9.3.9.1, 10.2.3.q | PDF
API 610#23 | Optional test procedures | Procedures for all optional tests (when specified in the data sheet) to determine that equipment is satisfactory for the specified service and meets all Purchaser requirements | ANSI/API Std 610 8.3.1, 8.3.4, 10.2.3 j), 10.2.5 S-615, 8.3.1, 10.2.5 | PDF
API 610#24 | Certified hydrostatic test data | Certified Hydrostatic Test Data at a minimum of 1.5 times the maximum allowable working pressure including full details of any areas machined post hydrotest. | ANSI/API Std 610 8.3.2, Annex L; S-615L 8.3.2. | PDF
API 610#25 | Disassembly after testing certificates | Certification that the condition of the pump internals after all running testing has not been adversely affected to the extent that they are outside the acceptance criteria of their 'as new' condition. | ANSI/API Std 610 8.3.3.8 | PDF
API 610#26 | Optional test data and reports | As per the requirements of L.2.1 v) of ANSI/API Std 610, where such testing is specified in the data sheet, with the following change: - add minimum submergence testing (vertically submerged pumps). | ANSI/API Std 610 8.3.4, Annex L; S-615, 8.3.4. | PDF
API 610#27 | Structural resonance test certificates | Certificate detailing the pump structure/driver stand natural frequency which shall have at least 10 % separation from the minimum and maximum continuous operating speeds. | ANSI/API Std 610 9.3.9.2 | PDF
API 610#28 | Certified dimensional outline drawings | For Proposal: Outline dimensioned drawings for each pump skid, driver and auxiliary systems where applicable including: size and location of major Purchaser connections; overall dimensions; maintenance clearance dimensions; overall masses; erection masses; maximum maintenance masses (indicated for each piece), lifting points and methods of lifting the assembled skid package and, if applicable, the standard baseplate number. For Acceptance: Certified dimensional outline drawing for each pump major skid, driver and auxiliary systems, where applicable, are to be provided as per the requirements of 10.3.2.1, L.2.1 a) of ANSI/API Std 610, with the following changes: - 1) add connection finish; include electrical and instrument connections, where applicable - 5) add foundation loads; anchor bolt size; - 7) add forces and moments for other purchaser connections; - 8) add rigging and lifting plan where applicable. Drawings are to include full detail of sole plates and anti-vibration mounts (AVMs) where applicable. | ANSI/API Std 610 10.2.2.1.a, 10.2.2.2, 10.3.2.1, Annex L | Native
API 610#29 | Cross-sectional drawings and bills of materials | For Proposal: Cross-sectional drawings showing the details of the proposed pump and driver. For Acceptance Cross-Sectional drawings showing details of all furnished equipment parts, including drivers and auxiliary systems and instrumentation where applicable. Drawings to include: reference part numbers; OEM and sub-vendor actual part numbers; actual manufacturers materials; material codes. Also include as applicable: axial and radial fits; clearances; pre-loads; axial rotor floats. | ANSI/API Std 610 10.2.2.1.b, 10.2.2.2, 10.3.4.1, Annex L | PDF
API 610#30 | Overall package piping and instrument diagram | For proposal: Overall pump, driver and systems (where applicable) package P&ID showing all piping and instrumentation included in the Vendor's scope. For acceptance: Overall pump, driver and systems (where applicable) package P&ID including: summary of the key equipment featured and brief key data (flows, pressures, temperatures); valve, orifice and line sizes and specs.; instrumentation and safety devices and set points; seal system alarm and shutdown limits; vibration alarm and shutdown settings; bearing temperature alarm and shutdown settings; lubricating oil system control, alarm and shutdown settings (pressure and temperature); casing/driver windings temperature alarm and shutdown settings. | ANSI/API Std 610 10.2.2.1 c), 10.2.2, Annex L | PDF
API 610#31 | Data sheets | In all cases the pump performance data is, where applicable, be based on the specified viscous duty, the clearances proposed by Vendor after making allowances for any added clearance based on temperature, viscosity and wear component galling tendencies and any discharge orifice proposed by Vendor. For Proposal: As per the requirements of 10.2.3 a) of ANSI/API Std 610, with the following changes: - applies to pump, driver and mechanical seal data sheets. For Acceptance: Pump, driver and mechanical seal data sheets, fully completed for the purchased equipment. | ANSI/API Std 610 10.2.3.a), Annex L; S-615, 6.8.1 | PDF
API 610#32 | Recommended spare parts | For Proposal: As per the requirements of 10.2.3 f) of ANSI/API Std 610, with the following changes: - applies to parts for all equipment furnished by Vendor. For Acceptance: As per the requirements of 10.3.4 of ANSI/API Std 610, with the following changes: - Applies to parts for all equipment furnished by Vendor. - List is to indicate all spare parts recommended by Vendor/Sub Vendor for commissioning, start-up, 2 years of operation and capital or insurance spares. - For each part listed, the original manufacturer's name and part number is to be shown. - For antifriction bearings, full bearing designation numbers with appropriate suffixes that clearly indicate bearing type, size, cage type, and the selected internal clearance or pre-load is to be shown. | ANSI/API Std 610 10.2.3.f, 10.3.4, Annex L; S-615, 10.3.4 | Native
API 610#33 | Utility requirements | For Proposal: As per the requirements of 10.2.3 i) of ANSI/API Std 610, with the following changes: - remove all references to lubricating oil. For Acceptance: As per the requirements of L.2.1 g) 4) of ANSI/API Std 610. | ANSI/API Std 610 10.2.3i, Annex L | PDF
API 610#34 | Lubrication schedule | The lubricant table is to indicate, for each complete unit and for each device or point to be lubricated, the following data: - Make and tag of the lubricant to be utilized and of other makes, if required in the Project specifications; - Physical and chemical characteristics sufficient to define the equivalency with others (viscosity at 50°C, specific gravity, index of viscosity, etc.) - The quantity of lubricant required - The required pressure of the lubricant (if applicable) - The heat load being removed by the lubricant (if applicable) - Expected yearly consumption according to the experience of the Vendor. | ANSI/API Std 610 10.2.3i, Annex L | PDF
API 610#35 | Inspection and test equipment calibration certificates | Current calibration certificates for all shop instrumentation to be used during inspection and testing activities. | ANSI/API Std 610 10.3.2.2; S-615 10.3.2.2 | PDF
API 610#36 | Lateral critical speed analysis | As per the requirements of I.3 of ANSI/API Std 610. | ANSI/API Std 610 Annex I, Annex L | PDF
API 610#37 | Damped unbalanced response analysis | As per the requirements of I.1.4 of ANSI/API Std 610. | ANSI/API Std 610 Annex I, Annex L | PDF
API 610#38 | Material safety data sheets | Material safety data sheets are to be in accordance with local standards for the specific paints, preservatives, coatings, lubricants, cooling media and chemicals supplied with, or applied to the supplied machinery or equipment. E.g. OSHA Form 174. | ANSI/API Std 610 Annex L | PDF
API 610#39 | Electrical and instrumentation wiring diagrams | The Vendor standard drawings are to be submitted. The diagrams are also to show the connections, terminal/pin/socket and cable detail between different items within the package, including earthing and spare terminals. The diagram is also identify all connections to Purchaser's power supply and instrumented systems. | ANSI/API Std 610 Annex L | PDF
API 610#40 | Motor performance data | As per the requirements of L.2.2 e) of ANSI/API Std 610. | ANSI/API Std 610 Annex L | PDF
API 610#41 | Shaft coupling assembly drawing and bill of materials | Shaft coupling assembly drawing and bill of materials, including coupling specification, fit, full dimensions, allowable misalignment tolerances, balance grade, service factor, weights, machining/mounting details, keys detail and maintenance details. The coupling drawing is to include coupling thermal growth data in millimetres per 100°C temperature rise as applicable. | ANSI/API Std 610 Annex L | PDF
API 610#42 | Shaft seal drawing and bills of materials | For Proposal: Shaft seal preliminary drawing and materials of construction. For Acceptance: Shaft seal drawing showing details of equipment including direction of rotation, seal harness connection details, seal harness pressures and flowrates, maximum and minimum dynamic and static design pressures and temperatures. Bill of materials to include actual OEM part numbers, materials and material codes. | ANSI/API Std 610 Annex L | PDF
API 610#43 | Overall package piping systems schematics and bills of materials | Overall pump and driver package piping systems schematics and bills of material including as applicable for all systems: applicable WPS (fabrications); parts list; quantities; sizes; dimensions; specifications; materials of construction. | ANSI/API Std 610 Annex L; | PDF
API 610#44 | Pump speed-torque curve superimposed on motor driver speed-torque curves | Pump speed-torque curve superimposed on the motor driver speed-torque curves | ANSI/API Std 610 Annex L; S-615 7.1.6 | PDF
S-615#01 | Warm-up (or Cool-down) procedure | Detailed procedure to be followed to achieve instantaneous start-up of the pump with the pumping temperatures indicated on the data sheet. | S-615 6.1.36 | PDF
S-615#02 | Instrument data Ssheets | Purchaser's format instrument data sheets, fully completed. | S-615 7.4.2.5 | PDF
S-615#03 | Instrument list | Instrument list with tag nos., service descriptions, ranges, alarm and trip set points (if any) | S-615 7.4.2.5 | PDF
S-615#04 | Non-destructive examination procedures | Written description of all essential parameters and precautions to be applied when non-destructively testing products in accordance with standard(s), code(s) or specification(s) | S-615 8.2.2.1 | PDF
S-615#05 | Non-destructive examination operators qualifications | Qualification certificates for the technicians and operators signing certificates are required. NDE Operators are required to be qualified by an authorized qualification body such as to PCN, CSWIP, SNT-TC-1A, or other Purchaser approved standard according to EN ISO 9712/ISO 9712 for radiographic, ultrasonic, magnetic particle and dye penetrant examination. An index is required for all NDE Operators providing Name, Identification, Qualifications, Start and Expiry Dates of Qualifications | ASME BPVC, Article 1, Section V | PDF
S-615#06 | Certified hydrostatic test procedure | Procedure to determine that equipment pressure envelope strength and integrity complies fully with the Purchaser requirements | S-615 8.3.2.1 | PDF
S-615#07 | Impeller as-built drawing | Impeller as-built drawing. Drawing showing the details of any modifications (under filling, over filling, V-cutting or any other such technique) made to the impeller after the performance test to correct hydraulic performance. | ANSI/API Std 610 8.3.3.7 a); S-615 8.3.3.7.a) | PDF
S-615#08 | Painting procedure | Detailed procedure for surface preparation and painting covering all items in Vendor's scope of supply. To include systems for the materials of construction, the operating temperatures, the site environment, any items under insulation. | S-615 8.4.2.4 | PDF
S-615#09 | Manufacturing record book index | Each manufacturing record book (MRB) is to include all of the manufacturing records and certification referenced in the Purchaser accepted Inspection and Test Plans and all documentation required to demonstrate full compliance with, and/or as specified in the Purchase Order and its attachments. As a minimum, the MRB shall contain the below listed documentation. Note that the Manufacturing Record Book is not contain any documents that have been submitted to the Purchaser during the contract. All ITP verifying documents All as-built data Some examples of these are: material certificates, NDE certificates, welding detail, manufacturing and test personnel qualifications, balance certificates, as-built dimensions, as-built clearances, declarations of conformity. | S-615 10.3.5.4 | PDF
S-615#10 | Manufacturing record book | Manufacturing record book is to contain all required quality related documents relating to the complete package. The Vendor's proposed index is to be agreed prior to submission of the manual and the MRB shall be compiled in strict accordance with the Purchaser accepted MRB index. | S-615 10.3.5.4 | PDF
S-615#11 | Declaration of conformity | The manufacture’s or other party’s confirmation that the product is designed, manufactured and tested as specified. To be delivered according to applicable authorities requirements. | Contract Requirement | PDF

## Instructions
Information requirements for
Centrifugal Pumps
Instructions & Guidance
Sheets with Green coloured tabs are those which are to be issued to suppliers
Sheets with Red tabs are for user / buyer information only
This workbook contains a hidden sheet ('Pick Lists') which is used for drop down menu selection within the main part of this workbook.
1 | Front & Preliminaries Tab
The 'Front & Preliminaries ' tab includes an IOGP Front sheet for the IRS followed by Acknowledgements, a Disclaimer, Copyright Notice, Foreword and Introduction
2 | 'IRS Cover' Tab
The 'IRS Cover' tab has been included for Company and/or Contractor Buyers to update and include as a Cover Sheet for the issue of the IRS to Suppliers, but Users may replace this sheet with an alternative User or Project format.
3 | 'Deliverables' Tab
The 'Deliverables' tab includes columns A to L, including Column A for the relevant requirement code and Column B for the Requirement for the different Information Deliverables (Data, Documents and/or Models) to be provided by suppliers, based on the parent standard, IOGP Supplement or the specified parent industry Standard. Condition Invoking Revoking Requirement Column C is included to allow any specific conditions to be identified that may require a additional deliverable(s). Typical Deliverable Column D is provided for Buyer to identify the deliverable type that the information would typically appear within; this also allows the buyer's Requisitioning Engineers to group the various Information Requirements by Deliverable Type. Column E includes Submission Requirements (Yes or No) at Proposal, while columns F, G & H identify Issue Purpose (For Information or For Acceptance) and Durations (Period or Weeks/Months) for First Issue of the particular deliverable Post Purchase Order. [Note for Buyer - default values in the downloadable IRS are set to the equivalent of CAS level D, as defined in the QRS. Buyer is to adjust the values in these columns to match the actual CAS level for the specific application]. Required As Built, Fulfilled by Document Number(s), Translation Required and Remarks columns I, J, K & L are also included. Definitions for each column are contained in the rows above the columns: Abbreviations used for various submission requirements in Column H are shown in table 3.1 below:
Table 3.1 - Information Submission Abbreviations
4 | 'Definitions' Tab
The 'Definitions' tab includes several columns A to F, including Column A for the relevant Code & Column B for the Requirement for the different Information (Data, Documents and/or Models) Deliverables to be provided by Suppliers, all copied from the 'Deliverable's tab. Column C includes a full description of the Information Deliverable based on the Parent Standard, IOGP Supplement or an Industry Standard. Column D gives a reference to the Parent Standard, IOGP Supplement or an Industry Standard that the Information deliverable is identified in. Column E identifies the Deliverable format as listed in Table 9.1 below. Column F relates the CFIHOS discipline document type that could be used to classify the document having this IRS content. Definitions for each column are contained in the rows above the columns:
5 | 'Instructions' Tab
This 'Instructions' tab is provided to instruction & guidance to Company, Contractor, Buyer and/or Suppliers in the use of this IRS.
6 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various tabs of this workbook.
Buyer |  | Organisation placing a Contract or Purchase Order with Supplier for equipment or services on project; may be alternatively referred to as 'User' or 'Purchaser'
CFIHOS |  | Capital Facilities Information Hand Over Specification
Company |  | Project Operating Entity or the organisation Contractor is under contract to
Contractor |  | Project Contractor responsible for procuring equipment.
Information |  | Data, Documents and/or Models
IRS |  | Information Requirements Specification
PO |  | Purchase Order
QRS |  | Quality Requirements Specification
SMIS |  | Supplier Master Information Schedule
Supplier |  | Organisation supplying equipment or services to Company and/or Contractor on project; may alternatively be referred to as "Vendor", "Seller" or “Manufacturer”.
7 | CFIHOS
The Information Requirements and Deliverables described in this IRS are also published within the CFIHOS (Capital Facilities Information Hand Over Specification) Industry Standard. The objective of CFIHOS is to create a common information standard across the Oil and Gas industry to facilitate efficient information exchange on projects. Further information on CFIHOS can be found at http://uspi-global.org/index.php/projects/frameworks-methodologies/136-cfihos
8 | Document Metadata
Typical Metadata for Information Deliverables to be provided by Suppliers is shown in Table 8.1 below
Table 8.1 - Supplier Deliverable Metadata
9 | Deliverable Formats
The format of the relevant Information Deliverable to be submitted by Supplier for Buyer/Contractor is to be as described in table 9.1 below. Where required to be ‘As Built’ deliverables are be updated and handed over in the native format.
Table 9.1 – Deliverable Formats

## Supplementary Sheet
Row | Information requirements for Centrifugal Pumps |  |  |  | Issue
2 | Tag No. : | Insert Tag_No
3 | Service : | Insert Service Description
4 | USER SUPPLEMENTARY REQUIREMENTS
5 | Delete this sheet if not required.
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
IOGP S-615L Version 1.0 |  |  | Sheet 1 of | 1

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col K
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
WAO
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code |  | Previous Template
Deliverables Tab Pick Lists Col E: Hard Copy; Deliverables Tab Pick Lists Col H: Hard Copy | Intelligent vector drawing Like CAD
Deliverables Tab Pick Lists Col E: Native; Deliverables Tab Pick Lists Col H: Native | Multi media Like Film, Micro fiche, Video, Sound
Deliverables Tab Pick Lists Col E: PDF; Deliverables Tab Pick Lists Col H: PDF | Raster Image like a bitmap
Deliverables Tab Pick Lists Col E: Intelligent Vector (CAD); Deliverables Tab Pick Lists Col H: S/D | Structured Data Like CSV file, MS-access, MS-Excel, Application Database
Deliverables Tab Pick Lists Col E: Multi media (Film) | Technical publication or Text
Raster Image (Bitmap)
Structured Data (MS Apps)
Technical Publication (Text)
|  | WAD | - | Weeks After Delivery
|  | WAI | - | Weeks After Inspection
|  | WAO | - | Weeks After Order
|  | WAO (Monthly) | - | Weeks After Order Monthly
|  | WAT | - | Weeks After Test
|  | WPTD | - | Weeks Prior To Delivery
|  | WPTF | - | Weeks Prior to Fabrication
|  | WPTT | - | Weeks Prior To Test
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: