## Front & Preliminaries
|  |  |  | SPECIFICATION | OCTOBER
|  |  |  | S-620L | 2018
Information Requirements for High-voltage switchgear and controlgear
Revision history
| VERSION | DATE | AMENDMENTS
| 1.0 | October 2018 | Issued for Publication
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Project 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
Information Requirements for
High-voltage switchgear and controlgear
Foreword
This specification package was prepared under a Joint Industry Project 33 (JIP33) “Standardization of Equipment Specifications for Procurement” organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Ten key oil and gas companies from the IOGP membership participated in developing this specification under JIP33 Phase 2 with the objective to leverage and improve industry level standardization for projects globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, based on the ten participating members’ company specifications, resulting in a common and jointly approved specification, and building on recognized industry and/or international standards.
The specification package has been developed in consultation with a broad user and supplier base to promote the opportunity to realize benefits from standardization and achieve significant cost reductions for upstream project costs. The JIP33 work groups performed their activities in accordance with IOGP’s Competition Law Guidelines (November 2014).
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The vision from the CPC industry is to standardize specifications for global procurement for equipment and packages, facilitating improved standardization of major projects across the globe. While individual oil and gas companies have been improving standardization within their own businesses, this has limited value potential and the industry lags behind other industries and has eroded value by creating bespoke components in projects.
The specification package aims to significantly reduce this waste, decrease project costs and improve schedule through pre-competitive collaboration on standardization.
Following agreement of the relevant JIP33 work group and approval by the JIP33 Steering Committee, the IOGP Management Committee has agreed to the publication of this specification package by IOGP. Where adopted by the individual operating companies, the specification package aims to supersede existing company documentation for the purpose of industry-harmonized standardization.
IOGP S-620L Version 1.0
Information Requirements specification for
High-voltage switchgear and controlgear
Introduction
The purpose of this information requirements specification (IRS) is to define Information requirements for the supply of high-voltage switchgear and controlgear in accordance with IEC 62271-200:2011 for application in the petroleum and natural gas industries. This document defines the information requirements, including format, timing and purpose, for information to be provided by the manufacturer. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS is to be used in conjunction with the supplementary specification (IOGP S-620), quality requirements specification (IOGP S-620Q) and datasheets (IOGP S-620D) which together comprise the full set of specification documents. The Introduction section in the supplementary specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification
IOGP S-620L Version 1.0

## IRS Cover
Insert Buyer Logo Here |  |  | Information Requirements for |  |  | Insert Project Logo Here
High-voltage switchgear and controlgear
| CLIENT : |  |  | Insert Client_name
| PROJECT TITLE : |  |  | Insert Project Title
| PROJECT LOCATION : |  |  | Insert Project_location
| JOB/PROJECT NUMBER : |  |  | Insert Job/Project number here
| TAG No. : |  |  | Insert Tag_No
| SERVICE : |  |  | Insert Service Description
| DOCUMENT NUMBER : |  |  | Insert Project Document Number
| REVISION : |  |  | Insert Project Document Revision
Issue | Date | Issue Description |  |  | By |  | Checked | Approved
IOGP S-620L Version 1.0 | [8 empty] | Sheet 1 of | 1
Note on N17: Optional Text : Intended for service description such as "Water Treatment Area 400V Switchboard"
Note on N21: Author: Project Specific document number and format
Note on N23: Author: Project specification Revision number and format

## Deliverables
Information Requirements for High-voltage switchgear and controlgear
Deliverables
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Deliverable, referencing the Parent Standard, IOGP Supplement or Industry Standard where the Information is requested . e.g. API672#01, S-620#01
B | Requirement - a short description of the Information Deliverable that would typically provide the Information required, based on the description in the Parent Standard, IOGP Supplement or an Industry Standard Title.
C | Condition Invoking Requirement - describes special condition(s) under which the Information Deliverable is required; e.g.. service offshore and weight greater than 1 tonne means information is required. NB: if blank, always required
D | Typical Deliverable - User to advise the short description of the Information Deliverable that would typically include this Information Requirement
E | Submit With Proposal - Yes or No, where ‘Yes' means the Information Deliverable is required to be submitted with Manufacturers Proposal or 'No' is not required
F, G & H | First Issue Post Purchase Order - issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the Information Deliverable and Period defined after Purchase Order placement
I | Required As Built - Yes or No, where ‘Yes' means the Information Deliverable is required to be 'As Built' on completion or delivery of equipment or 'No' is not required 'As Built'
J | Fulfilled by Information Deliverable Number(s) – identifies which Information Deliverable(s) listed in the Supplier Master Information Register (SMIR) addresses the Users requirements. NB; it should be noted that one Information Deliverable can fulfil more than one Information Requirement.
K | Translation Required -Yes or No, where 'Yes' means the Information Deliverable should be translated into a language(s) (as defined in the data sheets) other than English and 'No' means to be provided in English
L | Remarks - may include bid clarification questions & decisions (specify author & date)
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Requirements
MD#01 | Supplier Master Information Schedule |  | Information Deliverables List | No | For Information |  | WAO | Yes
MD#02 | Delivery schedule |  | Delivery/Production Schedule | Yes | For Information |  | WAO | No |  |  | Preliminary with proposal
MD#03 | Progress Report |  | Progress Report | No | For Information |  | WAO (Monthly) | No
MD#04 | Quality Plan | CAS A & B as per S-620Q | Quality Plan | Yes | For Acceptance |  | WAO | No |  |  | Preliminary with proposal
MD#05 | Design and Development Plan | NOT RELEVANT FOR HVSG
MD#06 | Sub-Supplier Delivery Schedule |  | Sub-Supplier List | Yes | For Information |  | WAO (Monthly) | No |  |  | Preliminary with proposal
MD#07 | Inspection and Test Plan (ITP) |  | Inspection and Test Plan (ITP) | Yes | For Acceptance |  | WAO | No |  |  | Preliminary with proposal
MD#08 | Handling, shipping and storage procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No
MD#09 | Non-conformance records | CAS A & B as per S-620Q | Non-conformance History | No | For Information |  | WPTD | Yes
MD#10 | Concession requests |  | Concession request | No | For Acceptance |  | WAO (Monthly) | Yes
MD#11 | Obsolescence management plan |  | Management plan | Yes | For Information |  | WAO | No |  |  | Preliminary with proposal
S-620#M01 | IED Configuration Responsibilities | Where IEDs are included in scope | Responsibility matrix | Yes | For Information |  | WAO | No |  |  | Preliminary with proposal
Technical Information Requirements
IEC62271-200#01 | Functional design specification |  | Functional Design Specification | Yes | For Information |  | WAO | No
IEC62271-1#01 | General Arrangement details |  | General Arrangement Drawing | Yes | For Acceptance |  | WAO | Yes |  |  | Preliminary with proposal
IEC62271-1#02 | Foundation and Installation details |  | Installation Drawing | No | For Information |  | WAO | Yes
S-620#02 | CT sizing calculations |  | Calculation | No | For Information |  | WAO | Yes
S-620#03 | Current transformer characteristics |  | Characteristics | No | For Information |  | WAO | Yes
S-620#04 | High-voltage protective devices characteristics and ratings |  | Characteristics | No | For Information |  | WAO | Yes
S-620#05 | Utility load calculation |  | Calculation | No | For Information |  | WAO | Yes
IEC62271-200#02 | Heat Dissipation Calculation & Loads |  | Calculation | No | For Information |  | WAO | Yes
S-620#06 | Connection Diagram |  | Connection Diagram | No | For Information |  | WAO | Yes
S-620#07 | Switchgear I/O schedule | Where IEDs included in scope | Schedule | No | For Information |  | WAO | Yes
S-620#08 | Functional logic diagram |  | Logic Diagram | No | For Acceptance |  | WAO | Yes
S-620#09 | Switchgear single line diagram |  | Single Line Diagram | No | For Acceptance |  | WAO | Yes
S-620#10 | Circuit and wiring diagram |  | Circuit and wiring diagram | No | For Acceptance |  | WAO | Yes
S-620#11 | Inter-panel diagram |  | Connection diagram | No | For Information |  | WAO | Yes
S-620#12 | Probability of failure on demand reliability data | Where SIL performance requirements are included in scope | Reliability data | No | For Information |  | WAO | Yes
S-620#13 | IED Interrogation and Programming Software | Where IEDs included in scope | Software | No | For Information |  | WAO | Yes
S-620#14 | Relay IED configuration files | Where IEDs included in scope | Software configuration file | No | For Information |  | WPTT | Yes
S-620#15 | IEC 61850 configuration files | Where IEDs included in scope with IEC 61850 interface to remote systems | Software configuration file | No | For Information |  | WPTT | Yes
IEC62271-1#03 | Installation, Operation and Maintenance (IOM) Manual |  | Installation , Operation and Maintenance (IOM) Manual | No | For Information |  | WPTD | No
IEC62271-1#04 | Recommended Spare Part List (RSPL) |  | Spare Part List (RSPL) | No | For Information |  | WPTD | Yes
IEC62271-200#03 | Chemical Inventory and Material Safety Data Sheets |  | Material Safety Data Sheets | No | For Information |  | WPTD | No
S-620#16 | Bill of materials |  | Bill of materials | No | For Information |  | WPTD | Yes
S-620#17 | Type test report |  | Test certificate | No | For Information |  | WPTD | No
IEC62271-1#05 | Lifting Equipment Test Certificate | If lifting equipment included in scope | Test certificate | No | For Information |  | WPTD | No
IEC62271-1#06 | Weight Data Sheet |  | Weight report | No | For Information |  | WAO | Yes
S-620#18 | ECMS simulation test procedure | If ECMS Simulation included in scope | Test procedure |  | For Acceptance |  | WPTT | No
S-620#19 | ECMS simulation test report | Where IEDs included in scope | Test report |  | For Information |  | WAT | Yes
S-620#20 | Routine Verification Test (FAT) Procedure |  | Test procedure | No | For Information |  | WPTT | No
IEC62271-1#07 | Routine Verification Test (FAT) Results |  | Test report |  | For Information |  | WAT | Yes
S-620#21 | Certificate of conformity | Where class or regional certification is included in scope | Certificate of conformance (CoC) | No | For Information |  | WPTD | Yes |  |  | marine class approval from an independent verification body
S-620#22 | Site acceptance test (SAT) procedure | If SAT included in scope | Tes procedure | No | For Acceptance |  | WPTT | No |  |  | To incorporate site interfaces
S-620#23 | Site acceptance test report | If SAT included in scope | Test report | No | For Acceptance |  | WAT | Yes

## Definitions
Information Requirements for High-voltage switchgear and controlgear
Definitions
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Deliverable, referencing the Parent Standard, IOGP Supplement or Industry Standard where the Information is requested. e.g. API672#01, S-620#01
B | Requirement - a short description of the Information Deliverable that would typically provide the Information required, based on the description in the Parent Standard, IOGP Supplement or an Industry Standard Title.
C | Description - an excerpt from the Parent Standard, IOGP Supplement or Industry Standard.
D | Reference - reference to the Parent Standard, IOGP Supplement or Industry Standard that the Information Deliverable is identified in.
E | Format - defines the required format of the relevant Information Deliverable to be submitted by Manufacturer for User for information and acceptance as shown in Table 9.1 of Instructions Tab and selected from pick list.
F | CFIHOS Discipline Document Type Code - the CFIHOS discipline document type that could be used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Requirements
MD#01 | Supplier Master Information Schedule | Schedule of specific information deliverables developed by the manufacturer and accepted by the user to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a) information deliverable type, title/description b) unique identification (code/number) in the manufacturer's format unless agreed otherwise in the contract. c) planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. | Contract Requirement | Native
MD#02 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by manufacturer/suppliers. Schedule details typically** include;. a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Once agreed , changes to planned dates are subject to agreement by user. Progress against planned dates is measured and the schedule updated and reported to the user in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the manufacturer's standard practice unless otherwise agreed in the contract. | Contract Requirement | Native
MD#03 | Progress Report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. | Contract Requirement | PDF
MD#04 | Quality Plan | Plan specifying the actions, responsibilities and associated resources to be applied by the manufacturer, and when applicable sub-suppliers, to deliver the services or procured item(s) in conformance with the agreed requirements. ISO9001 Clause 8.1 and ISO10005 may be used to inform the development of quality plans for specific applications, processes or products.. | Contract Requirement | Native
MD#05 | Design and Development Plan | NOT RELEVANT FOR HVSG | Contract Requirement
MD#06 | Sub-Supplier Delivery Schedule | Definition of processes, products or services that will be externally provided and the controls to be applied by the [supplier] to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . Note: ISO9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. | Contract Requirement | PDF
MD#07 | Inspection and Test Plan (ITP) | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria, records and associated manufacturer, user and independent conformity assessment activities. ISO9001 Clause 8.1 and ISO10005 may be used to inform the development of inspection and test plans for specific processes and products. | Contract Requirement | Native
MD#08 | Handling, shipping and storage procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a) Packaging requirements; contents, identification, size, weight and number of packages/container (s), b) special packing/unpacking/handling requirements c)) storage location and requirements, d) preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. | Contract Requirement | PDF
MD#09 | Non-conformance records | Details of non-conformances raised by or to the manufacturer/sub suppliers against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the manufacturer in accordance with ISO9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a nonconforming condition are subject to agreement by the user in accordance with the concession management protocols defined in the Contract. | Contract Requirement | PDF
MD#10 | Concession requests | Formal submission seeking user agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, user directions, agreed action status provided with progress reports and at contract closeout | Contract Requirement | Native
MD#11 | Obsolescence management plan | Plan defining the manufacturer's co-ordinated activities to direct and control the strategies for the identification and mitigation of the effects of obsolescence to the user, through all stages of the life of all components within the high-voltage switchgear and controlgear assembly. An example of the principles of this plan is defined within IEC 62402, Obsolescence management – Application guide. | S-620 Clause 5.0.103 | PDF
S-620#M01 | IED Configuration Responsibilities | Responsibility matrix or flow chart detailing device configuration and set-point responsibilities including protection relay, IED generic configuration and IED functional logic files for the purpose of interface control between user and manufacturer during the development of the switchgear and controlgear assembly. | S-620 Clause 5.115.3 | PDF
Technical Information Requirements
IEC62271-200#01 | Functional design specification | A document containing specific design data and performance requirements for the equipment. This document covers the design, available functionality and the hardware included in the scope. This document can also include images of hardware, topology sketches and extracts from general arrangement drawings in addition to text to provide a common understanding of the assemblies. | S-620 Clause 5.108.4, IEC 62271-200 Clause 9.2
IEC62271-1#01 | General Arrangement details | The manufacturer's standard general arrangement drawing showing overall dimensions and critical interface dimensions. The drawing contains references to main specifications and standards. For equipment / components the drawing may include cross sectional views. | IEC62271-200 Clause 9.2
IEC62271-1#02 | Foundation and Installation details | The manufacturer's standard installation drawing showing; • Critical interface dimensions • Interface connections • Weight of assemblies, equipment and components • Centre of gravity • Withdrawal/installation and maintenance space. • Installation and mounting details • Lifting arrangement The drawing to reference to main specifications and standards. | IEC62271-200 Clause 9.2
S-620#02 | CT sizing calculations | Calculations to size the CT's, e.g. burden and accuracy class. | S-620 Clause 9.2
S-620#03 | Current transformer characteristics | The magnetization and transient characteristics of the current transformers. | S-620 Clause 9.2
S-620#04 | High-voltage protective devices characteristics and ratings | Time-current characteristics of high-voltage protection devices provided with the switchgear and controlgear assembly, e.g. motor-starter fuse and protection relay curves. | S-620 Clause 9.2
S-620#05 | Utility load calculation | Summarises the normal and transient DC and AC utility loads of the switchgear for the purpose of sizing external power provision. | IEC 62271-1 Clause 10.3
IEC62271-200#02 | Heat Dissipation Calculation & Loads | This document contains the calculation by the manufacturer to arrive at the heat load produced by the switchgear to enable HVAC sizing and includes load factors and type of load provided to the manufacturer to produce accurate calculation | S-620 Clause 9.2
S-620#06 | Connection Diagram | Drawing providing information about the external physical connections per functional unit including hydraulic, pneumatic and electrical connections. | IEC 62271-1 Clause 11.3.5
S-620#07 | Switchgear I/O schedule | Schedule of tags identifying IED programmable addresses and hardwired signal interfaces for all functional units within the switchgear and control gear assembly. | S-620 Clause 5.4.1.1
S-620#08 | Functional logic diagram | Control logic embedded in IEDs (e.g. protection relays) that is developed by the manufacturer to implement the requirements of the user diagrams and associated protection relay settings. | S-620 Clause 5.115.3
S-620#09 | Switchgear single line diagram | Drawing detailing major items of equipment, including protection devices per functional unit using IEC 60617 standard symbols and/or ANSI C37.2 device function numbers per switchgear and controlgear assembly. | S-620 Clause 9.2
S-620#10 | Circuit and wiring diagram | Drawing detailing in schematic form the functional unit in respect of electrical and instrument circuit connections based on the principles in IEC 61082-1, Preparation of documents used in electrotechnology – Part 1: Rules. The circuit(s) to be shown to the extent necessary for the understanding of the circuit(s) functions and how the components are interconnected. The drawing includes details of all device hardwired connections within the functional unit and external interfaces to terminal blocks. Hardwired connections internal to the functional unit, devices and external interface terminal blocks are to be identified as per manufacturers standard. | S-620 Clause 9.2
S-620#11 | Inter-panel diagram | Wiring diagram detailing the control and auxiliary interfaces between functional units within the switchgear and controlgear assembly. The wiring diagram identifies functional unit inter-connection and field run connections to be made during assembly of transport units. | S-620 Clause 9.2
S-620#12 | Probability of failure on demand reliability data | Identifies reliability input data for functional unit and protection relay probability of failure on demand (PFD) to enable user to perform functional safety requirements assessments to IEC 61511. | S-620 Clause 5.115.2
S-620#13 | IED Interrogation and Programming Software | Software required to access and program the relays and programmable devices in the HV switchgear | S-620 Clause 5.115.3
S-620#14 | Relay IED configuration files | Relay and programmable configuration devices files (native files and PDF) | S-620 Clause 5.113.3
S-620#15 | IEC 61850 configuration files | Substation Configuration Description (SCD) or Configured IED Description (CID) files | S-620 Clause 5.115.4
IEC62271-1#03 | Installation, Operation and Maintenance (IOM) Manual | The manufacturer's standard IOM manual. This document includes sufficient information to install, operate and maintain the equipment. This document includes sufficient information for troubleshooting. If required a supplementary sheet can be added identifying components that are not suitable for 5 years continuous operation without inspection or replacement under the user specified service conditions. | IEC62271-1 Clause 11.4
IEC62271-1#04 | Recommended Spare Part List (RSPL) | Identified products which may require replacement are listed in a spare parts list identified and described so that the necessary spare, the whole item or parts can be obtained. The spare parts list includes: - reference to project documentation (e.g. drawing number and position number); - the manufacturer’s catalogue/unique and unambiguous parts number; - for standardized parts: the real manufacturer’s name and catalogue/unique and unambiguous parts number. - reference to tag (where applicable) The list includes equipment manufacturer's recommendation for commissioning and two years operational spares. | S-620 Clause 5.0.104, IEC 62271-1 Clause 11.4
IEC62271-200#03 | Chemical Inventory and Material Safety Data Sheets | A structured form containing information on the safety, health and environmental protection aspects of the chemical, including protective measures and emergency actions. Safety Data Sheets (SDS) to be in accordance with local/national regulations and in the official operating language of the plant, or in English if accepted by local authorities. A collection of SDS to be delivered to User for chemicals delivered as part of equipment, as first fill or used for preservation before operation. Exceptions are • grease • fat • surface preservatives • coatings • oils in volume per equipment below 10 litres. The report includes one SDS per unique chemical trade name. The report to include a cross reference table with each unique chemical trade name, equipment tag number(s) and SDS file name. | IEC62271-1 Clause 13
S-620#16 | Bill of materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and references to specifications including sub-suppliers and associated purchase orders. | IEC62271-200 Clause 9.2
S-620#17 | Type test report | A document that provides a summary of type tests, including the specific year and edition of the IEC used to perform the type test for all discrete functional units provided | IEC 62271-200 Clause 6.1
IEC62271-1#05 | Lifting Equipment Test Certificate | Lifting equipment test certificate in relation switchgear load certified hoist | S620 Clause 10.1.2
IEC62271-1#06 | Weight Data Sheet | Document with weight of individual shipping sections | IEC62271-200 Clause 9.2
S-620#18 | ECMS simulation test procedure | User-agreed functional test procedure of the ECMS or its parts using the parameter set for the planned application including communication interfaces with integrated control and safety systems. | S-620 Clause 7.107, S-620Q Annex A
S-620#19 | ECMS simulation test report | Results from the execution of ECMS simulation test procedure including communication interfaces with integrated control and safety systems. | S-620 Clause 7.107 S-620Q Annex A
S-620#20 | Routine Verification Test (FAT) Procedure | Procedure documenting the manufacturers recommended testing activities and acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Procedure to define test set-up and test equipment. | IEC 62271-200 Clause 7, S-620Q Annex A
IEC62271-1#07 | Routine Verification Test (FAT) Results | This document records and documents all results from the activities performed in accordance with the FAT procedure. Include any observation rework retesting. | IEC 62271-1 Clause 8
S-620#21 | Certificate of conformity | The manufacture’s or other party’s confirmation that the product is designed, manufactured and tested as specified. To be delivered according to applicable authorities requirements. An example is marine class approval of the switchgear | S-620 Clause 9.2
S-620#22 | Site acceptance test (SAT) procedure | Procedure documenting the manufacturers recommended site tests including discrete functional unit and overall assembly, electrical, mechanical, protection relay and IEDs. | IEC62271-1 Clause 11.3.7
S-620#23 | Site acceptance test report | Site acceptance test report including discrete functional unit and overall assembly, electrical, mechanical, protection relay and IED tests. | S-620 Clause 7

## Instructions
Information Requirements for
High-voltage switchgear and controlgear
Instructions and Guidance
Sheets with Green coloured tabs are those which shall be issued to suppliers
Sheets with Red tabs are for user / buyer information only
This workbook contains a hidden sheet ('Pick Lists') which is used for drop down menu selection within the main part of this workbook.
1 | Front & Preliminaries Tab
The 'Front & Preliminaries ' tab includes an IOGP Front sheet for the IRS followed by Acknowledgements, a Disclaimer, Copyright Notice, Foreword and Introduction
2 | 'IRS Cover' Tab
The 'IRS Cover' tab has been included for Company and/or Contractor Buyers to update and include as a Cover Sheet for the issue of the IRS to Suppliers/ Manufacturers, but Users may replace this sheet with an alternative User or Project format.
3 | 'Deliverables' Tab
The 'Deliverables' tab includes columns A to L, including Column A for the relevant requirement code and Column B for the Requirement for the different Information Deliverables (Data, Documents and/or Models) to be provided by suppliers, based on the parent standard, IOGP Supplement or the specified parent industry Standard. Condition Invoking Revoking Requirement Column C is included to allow any specific conditions to be identified that may require a additional deliverable(s). Typical Deliverable Column D is provided for users to identify the deliverable type that the information would typically appear within. This also allows the buyer's Requisitioning Engineers to group the various Information Requirements by Deliverable Type. Column E includes Submission Requirements (Yes or No) at Proposal, while columns F, G & H identify Issue Purpose (For Information or For Acceptance) and Durations (Period or Weeks/Months) for First Issue of the particular deliverable Post Purchase Order. [Note for Buyer - default values in the downloadable IRS are set to the equivalent of CAS level D, as defined in the QRS. Buyer shall adjust the values in these columns to match the actual CAS level for the specific application]. Required As Built, Fulfilled by Document Number(s), Translation Required and Remarks columns I, J, K & L are also included. Definitions for each column are contained in the rows above the columns: Abbreviations used for various submission requirements in Column H are shown in table 3.1 below:
Table 3.1 - Information Submission Abbreviations
4 | 'Definitions' Tab
The 'Definitions' tab includes several columns A to F, including Column A for the relevant Code & Column B for the Requirement for the different Information (Data, Documents and/or Models) Deliverables to be provided by Suppliers, all copied from the 'Deliverable's tab. Column C includes a full description of the Information Deliverable based on the Parent Standard, IOGP Supplement or an Industry Standard. Column D gives a reference to the Parent Standard, IOGP Supplement or an Industry Standard that the Information deliverable is identified in. Column E identifies the Deliverable format as listed in Table 9.1 below. Column F relates the CFIHOS discipline document type that could be used to classify the document having this IRS content. Definitions for each column are contained in the rows above the columns:
5 | 'Instructions' Tab
This 'Instructions' tab is provided to instruction & guidance to Company, Contractor, Buyer and/or User in the use of this IRS.
6 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various tabs of this workbook.
User |  | Organisation placing a Contract or Purchase Order with Supplier for equipment or services on project. To align with the definitions used in IEC 62271 1 and IEC 62271 200, the term “User” is used in place of “Customer”, "Buyer and/ or "Purchaser".
CFIHOS |  | Capital Facilities Information Hand Over Specification
Company |  | Project Operating Entity or the organisation Contractor is under contract to
Contractor |  | Project Contractor responsible for procuring equipment.
Information |  | Data, Documents and/or Models
IRS |  | Information Requirements Specification
PO |  | Purchase Order
QRS |  | Quality Requirements Specification
SMIR |  | Supplier Master Information Register
Manufacturer |  | Organisation supplying equipment or services to Company and/or Contractor on project. To align with the definitions used in IEC 62271 1 and IEC 62271 200, the term “Manufacturer” is used in place of “Supplier", "Vendor" and/ or "Seller".
7 | CFIHOS
The Information Requirements and Deliverables described in this IRS are also published within the CFIHOS (Capital Facilities Information Hand Over Specification) Industry Standard. The objective of CFIHOS is to create a common information standard across the Oil and Gas industry to facilitate efficient information exchange on projects. Further information on CFIHOS can be found at http://uspi-global.org/index.php/projects/frameworks-methodologies/136-cfihos
8 | Document Metadata
Typical Metadata for Information Deliverables to be provided by Suppliers is shown in Table 8.1 below
Table 8.1 - Supplier Deliverable Metadata
9 | Deliverable Formats
The format of the relevant Information Deliverable to be submitted by Supplier for Buyer/Contractor shall be as described in table 9.1 below. Where required to be ‘As Built’, deliverables shall be updated and handed over in the native format.
Table 9.1 – Deliverable Formats

## Supplementary Sheet
Row | Note | Information Requirements for |  |  |  |  | Issue
High-voltage switchgear and controlgear
|  | Tag No. : |  | Insert Tag_No
|  | Service : |  | Insert Service Description
USER SUPPLEMENTARY REQUIREMENTS
1 |  |  | Delete this sheet if not required.
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
IOGP S-620L Version 1 |  |  |  |  | Sheet 1 of | 1

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col K
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
WAO
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code |  | Previous Template
Deliverables Tab Pick Lists Col E: Hard Copy; Deliverables Tab Pick Lists Col H: Hard Copy | Intelligent vector drawing Like CAD
Deliverables Tab Pick Lists Col E: Native; Deliverables Tab Pick Lists Col H: Native | Multi media Like Film, Micro fiche, Video, Sound
Deliverables Tab Pick Lists Col E: PDF; Deliverables Tab Pick Lists Col H: PDF | Raster Image like a bitmap
Deliverables Tab Pick Lists Col E: Intelligent Vector (CAD); Deliverables Tab Pick Lists Col H: S/D | Structured Data Like CSV file, MS-access, MS-Excel, Application Database
Deliverables Tab Pick Lists Col E: Multi media (Film) | Technical publication or Text
Raster Image (Bitmap)
Structured Data (MS Apps)
Technical Publication (Text)
|  | WAD | - | Weeks After Delivery
|  | WAI | - | Weeks After Inspection
|  | WAO | - | Weeks After Order
|  | WAO (Monthly) | - | Weeks After Order Monthly
|  | WAT | - | Weeks After Test
|  | WPTD | - | Weeks Prior To Delivery
|  | WPTF | - | Weeks Prior to Fabrication
|  | WPTT | - | Weeks Prior To Test
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: