## Front & Preliminaries
|  |  |  | SPECIFICATION | June
|  |  |  | S-710L | 2020
Information Requirements for
Air-cooled Heat Exchangers
Revision history
| VERSION | DATE | PURPOSE
| 1 | June 2020 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-710L Information Requirements for
Air-cooled Heat Exchanger
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
S-710L Information Requirements for
Air-cooled Heat Exchanger
Introduction
The purpose of this information requirements specification (IRS) is to define Information requirements for the supply of air-cooled heat exchangers for application in the petroleum and natural gas industries. This document defines the information requirements, including format, timing and purpose, for information to be provided by the manufacturer. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS it to be used in conjunction with the supplementary requirements specification (IOGP S-710), quality requirements specification (IOGP S-710Q) and equipment data sheet (IOGP S-710D) which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification

## Supplier Instructions
S-710L Information Requirements for
Air-cooled Heat Exchangers
Supplier Instructions
In response to Invitation To Tender (ITT)
Tenderers to submit information as defined in column E - 'Submit At Proposal' in 'Requirements' sheet, in accordance with ITT instructions
On award of contract
Specified Information requirements shall be submitted in accordance with contract information submission instructions. Suppliers to prepare and submit 'Supplier Master Information Schedule' (SMIS) incorporating information requirements in accordance with columns F - 'First Issue Post Purchase Order' in 'Requirements' sheet. Supplier to demonstrate compliance with each information requirement either by providing document number cross reference to the Requirement in 'Supplier Master Information Schedule' (SMIS) and, if specified in the Contract, using column J 'Fulfilled by Document Number(s)' in the IRS Requirements Sheet.
On completion of scope
Supplier to validate that the information delivered meets the IRS requirements either through cross reference to the deliverable type in a as-built version of the 'Supplier Master Information Schedule' SMIS and, if specified in the Contract, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in Requirement sheet populated with the specific document numbers issued to the Purchaser.
IRS Structure Contents
1 |  | 'Front & Preliminaries' Tab
The 'Front & Preliminaries ' tab includes an IOGP Front sheet for the IRS followed by Acknowledgements, a Disclaimer, Copyright Notice, Foreword and Introduction
2 |  | 'Supplier Instructions' Tab
This 'Supplier Instructions' tab provides instructions that Suppliers are to follow in response to this IRS.
3 |  | 'Requirements' Tab
The 'Requirements' tab lists the suite of information requirements that are to be supplied during tendering and following award of the purchase order to deliver the purchase order scope. The information requirements are grouped under three broad categories; Management information requirements: Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. Technical information requirements: Technical information developed by the supplier or their sub suppliers, during the design and development, acquisition, manufacture, assembly and testing of the contracted scope. Purchase Order Specific Information Requirements: Information requirements specified by individual owners-operators in addition to those specified by IOGP-JIP33 to meet specific operational, project or legislative requirements. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. "The 'Requirements' tab includes columns A to L, including Column A for the relevant requirement code and Column B for the Requirement for the different Information Requirements (Data, Documents and/or Models) to be provided by suppliers, based on the parent standard, IOGP Specification or the specified parent industry Standard. Condition Invoking Revoking Requirement Column C is included to allow any specific conditions to be identified that may require a additional deliverable(s). Typical Deliverable Column D is provided for Purchaser to identify the deliverable type that the information would typically appear within; this also allows the Purchaser's Requisitioning Engineers to group the various Information Requirements by Deliverable Type. Column E includes Submission Requirements (Yes or No) at Proposal, while columns F, G & H identify Issue Purpose (For Information or For Acceptance) and Durations (Period or Weeks/Months) for First Issue of the particular deliverable Post Purchase Order. Required As Built, Fulfilled by Document Number(s), Translation Required and Remarks columns I, J, K & L are also included. Definitions for each column are contained in the rows above the columns: Abbreviations used for various submission requirements in Column H are shown in table 3.1 below:
Table 3.1 - Information Submission Abbreviations
4 |  | 'Definitions' Tab
The 'Definitions' tab includes several columns A to F, including Column A for the relevant Code & Column B for the Requirement for the different Information (Data, Documents and/or Models) Requirements to be provided by Suppliers, all copied from the 'Requirements' tab. Column C includes a full description of the Information Requirement based on the Parent Standard, IOGP Specification or an Industry Standard. Column D gives a reference to the Parent Standard, IOGP Specification or an Industry Standard that the Information requirement is identified in. Column E identifies the Requirement format as listed in Table 9.1 below. Column F relates the CFIHOS discipline document type that could be used to classify the document having this IRS content. Definitions for each column are contained in the rows above the columns:
5 |  | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various tabs of this workbook.
Buyer |  |  | Organisation placing a Contract or Purchase Order with Supplier for equipment or services on project; may be alternatively referred to as 'User' or 'Purchaser'
CFIHOS |  |  | Capital Facilities Information Hand Over Specification
Company |  |  | Project Operating Entity or the organisation Contractor is under contract to
Contractor |  |  | Project Contractor responsible for procuring equipment.
Information |  |  | Data, Documents and/or Models
IRS |  |  | Information Requirements Specification
PO |  |  | Purchase Order
QRS |  |  | Quality Requirements Specification
SMIS |  |  | Supplier Master Information Schedule
Supplier |  |  | Organisation supplying equipment or services to Company and/or Contractor on project; may alternatively be referred to as "Vendor", "Seller" or “Manufacturer”.
6 |  | CFIHOS
The Information Requirements are also classified according to document classification published in v1.4 of Capital Facilities Information Hand Over Specification (CFIHOS). The objective of CFIHOS is to create a common information standards across the process industries. Further information on CFIHOS can be found at:
https://uspi.nl/index.php/projects/frameworks-methodologies/136-cfihos
7 |  | Document Metadata
Typical Metadata for Information Deliverables to be provided by Suppliers is shown in Table 7.1 below
Table 7.1 - Supplier Deliverable Metadata
8 |  | Deliverable Formats
The format of the relevant Information Deliverable to be submitted by Supplier for Buyer/Contractor is to be as described in table 8.1 below. Where required to be ‘As Built’, deliverables are to be updated and handed over in the native format.
Table 8.1 – Deliverable Formats

## Requirements
S-710L Information Requirements for Air-cooled Heat Exchangers
Requirements
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement based on the description in the Parent Standard, IOGP Specification or an Industry Standard Information Requirement Title.
C | Condition Invoking Requirement - describes special condition(s) under which the Information Requirement is required; e.g.. service offshore and weight greater than 1 tonne means information is required. NB: if blank, always required
D | Typical Deliverable - Purchaser to advise the short description of the Information Deliverable that would typically include this Information Requirement
E | Submit With Proposal - Yes or No, where 'Yes' means the Information Requirement is required to be submitted with Vendors Proposal or 'No' is not required
F, G & H | First Issue Post Purchase Order - issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the Information Requirement and Period defined after Purchase Order placement.
I | Required As Built - Yes or No, where 'Yes' means the Information Requirement is required to be 'As Built' on completion or delivery of equipment or 'No' is not required 'As Built'
J | Fulfilled by Information Deliverable Number(s) - identifies which Information Requirement(s) listed in the Supplier Master Information Schedule (SMIS) addresses the Purchasers requirements. NB; it should be noted that one Information Deliverable can fulfil more than one Information Requirement.
K | Translation Required -Yes or No, where 'Yes' means the Information Requirement should be translated into a language(s) (to be advised) other than English and 'No' means to be provided in English
L | Remarks - may include bid clarification questions & decisions (specify author & date)
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S710-IR-1 | Supplier master information schedule |  | Information Deliverables List | No | For Acceptance |  | WAO | Yes |  | -
S710-IR-2 | Delivery schedule |  | Delivery/Production Schedule | Yes | For Information |  | WAO | No |  | -
S710-IR-3 | Progress report |  | Progress Report | No | For Information |  | WAO (Monthly) | No |  | -
S710-IR-4 | Quality plan | Required for CAS A, B, C | Quality Plan | No | - |  | - | - |  | -
S710-IR-5 | Sub-vendor delivery schedule |  | Sub-Vendor List | Yes | For Information |  | WAO (Monthly) | No |  | -
S710-IR-6 | Inspection and test plan for complete package |  | Inspection and Test Plan (ITP) | No | For Information |  | WAO | No |  | -
S710-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No |  | -
S710-IR-8 | Non-conformance records |  | Nonconformance History | No | For Acceptance |  | WAO | Yes |  | -
S710-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | WAO | Yes |  | -
Technical Information Deliverables
S710-IR-19 | Completed data sheet |  | Manufacturer Datasheet | Yes | For Acceptance |  | WAO | No |  | -
S710-IR-20 | Preliminary plan and elevation |  | Proposal Drawing | Yes | - |  | - | No |  | - | To be submitted with proposal only
S710-IR-22 | Thermal and hydraulic design calculations | Needed when thermal and hydraulic design is in the scope of the vendor | Thermal data sheet | Yes | For Information |  | WAO | Yes
S710-IR-23 | General Assembly |  | General Arrangement Diagram | No | For Acceptance |  | WAO | Yes |  | -
S710-IR-24 | Bundle and auxiliary structure detail drawing |  | Detailed Drawing | No | For Acceptance |  | WAO | Yes |  | -
S710-IR-47 | Component details and assembly drawings |  | Detailed Drawing | No | For Information |  | WAO | Yes |  | -
S710-IR-25 | Noise data sheet |  | Noise data sheet | Yes | For Information |  | WAO | Yes |  | -
S710-IR-26 | Fan characteristic curves |  | Manufacturer Datasheet | Yes | For Information |  | WAO | Yes |  | -
S710-IR-27 | Mechanical design calculations |  | Design Calculation | No | For Acceptance |  | WAO | Yes |  | -
S710-IR-43 | Structural design calculation | When supporting structure is in ACHE vendor scope | Design Calculation | No | For Information |  | WAO | No
S710-IR-28 | Non-destructive examination procedure |  | Non Destructive Test Procedure | No | For Acceptance |  | WAO | No |  | -
S710-IR-29 | Alloy verification | Needed when material of construction is alloy steel | Positive Material Identification (PMI) procedure | No | For Information |  | WAO | No |  |  | This is typically carried out for pressure parts and major load bearing parts.
S710-IR-30 | Pickling and passivation | Needed when material of construction is stainless steel | Pickling and passivation procedure | No | For Information |  | WAO | No
S710-IR-31 | Post weld heat treatment | Needed when heat treatment is required | Heat Treatment procedure | No | For Information |  | WAO | No
S710-IR-32 | Test Pressure |  | Pressure test procedure | No | For Acceptance |  | WAO | No |  | -
S710-IR-33 | Tube expansion | Needed when tubes are expanded through tubesheet | Tube expansion procedure | No | For Information |  | WAO | No
S710-IR-48 | Tube-to-tubesheet weld joint preparation | For strength welded tube-to-tubesheet joint | Tube-to-tubesheet fabrication plan | No | For Information
S710-IR-34 | Surface preparation and coating | Needed when coating or painting is specified by Purchaser | Painting and Coating Procedure | No | For Information |  | WAO | No
S710-IR-35 | Heat treatment record | Needed when heat treatment is required | Heat Treatment Records | No | For Information |  | WAO | Yes
S710-IR-36 | Non-Destructive Examination record | Required for CAS A and B only | Non-Destructive Examination (NDE) Report | - | - |  | - | - |  | -
S710-IR-37 | Welding procedure specification | Required for CAS A, B and C only | Welding procedure specification | - | - |  | - | - |  | -
S710-IR-49 | Procedure qualification record | Required for CAS A, B and C only | Welding Procedure qualification record | - | - |  | - | - |  | -
S710-IR-50 | Weld map |  | Welding Traceability Records | No | For Information |  | WAO | Yes |  | -
S710-IR-51 | Weld repair |  | Welding Repair Procedure | No | For Information |  | WAO | Yes |  | -
S710-IR-38 | Assembly lifting plan |  | Lifting, Hoisting, And Rigging Plan | No | For Information |  | WAO | No |  | -
S710-IR-39 | Material test report (2.2) | Required for CAS A and B only | Material test report (2.2) | - | - |  | - | - |  | -
S710-IR-54 | Materials Inspection Certificate (3.1) |  | Materials Inspection Certificate (3.1) | No | - |  | WAO | No |  | -
S710-IR-40 | Manufacturer Record Book (MRB) |  | Manufacturer Record Book (MRB) | No | For Acceptance |  | WAD | Yes |  | - | Manufacturer Record Book index, if required, shall be provided in first revision of the document. When index agreed, Manufacturer Record Book content shall be provided in subsequent revision of the document.
S710-IR-41 | Installation manual |  | Installation manual | No | For Information |  | WAO | Yes |  | - | 1. Installation manual can be delivered as part of Installation, operation and maintenance (IOM) manual or as a stand alone document 2. IOM Manual index, if required, shall be provided in first revision of the document.
S710-IR-53 | Maintenance manual |  | Maintenance manual | No | For Information |  | WAO | No |  | - | 1. Maintenance manual can be delivered as part of Installation, operation and maintenance (IOM) manual or as a stand alone document 2. IOM Manual index, if required, shall be provided in first revision of the document.
S710-IR-52 | Operations manual |  | Operations manual | No | For Information |  | WPTD | No |  | - | 1. Maintenance manual can be delivered as part of Installation, operation and maintenance (IOM) manual or as a stand alone document 2. IOM Manual index, if required, shall be provided in first revision of the doc
S710-IR-42 | Spare parts |  | Spare Part List | Yes | For Information |  | WAO | Yes |  | -
S710-IR-45 | Shop Run in test report | When specified by purchaser | Shop Run in test report | No | For Information |  | WPTD | Yes
Purchase Order Specific Information Requirements

## Definitions
S-710L Information Requirements for Air-cooled Heat Exchanger
Definitions
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement that would typically provide the Information required, based on the description in the Parent Standard, IOGP Specification or an Industry Standard Title.
C | Description - an excerpt from the Parent Standard, IOGP Specification or Industry Standard.
D | Reference - reference to the Parent Standard, IOGP Specification or Industry Standard that the Information Deliverable is identified in.
E | Format - defines the required format of the relevant Information Requirement to be submitted by Vendor for Purchaser/Contractor for information and acceptance as shown in Table 9.1 of Instructions Tab and selected from pick list.
F | CFIHOS Discipline Document Type Code - the CFIHOS discipline document type that could be used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Deliverables
S710-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the Vendor and accepted by the Purchaser to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. | Contract Requirement | Native | CFIHOS-70000099
S710-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by Vendor/sub-vendors. Schedule details typically** include; a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and Vendor) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the Purchaser in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the Vendor's standard practice unless otherwise agreed in the contract. | Contract Requirement | PDF | CFIHOS-70000298
S710-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. | Contract Requirement | PDF | CFIHOS-70000300
S710-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] | Contract Requirement | PDF
S710-IR-5 | Sub-vendor delivery schedule | Definition of processes, products or services that will be externally provided and the controls to be applied by the Vendor to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed vendors of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . Note: ISO 9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. | Contract Requirement | Native
S710-IR-6 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. | Contract Requirement | PDF | CFIHOS-70000180
S710-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. | Contract Requirement | PDF | CFIHOS-70000154
S710-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. | Contract Requirement | PDF | CFIHOS-70000226
S710-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout | Contract Requirement | PDF | CFIHOS-70000389
Technical Information Deliverables
S710-IR-19 | Completed data sheet | S-710D (IOGP data sheet for Air-cooled heat exchangers) with vendor filled-in data. Extent of data to be filled-in by vendor or purchaser shall be as identified on data sheet. | 5.1, 7.1.11.16, 7.2.3.17, 7.2.8.2.2, 7.2.8.3.2 | PDF | CFIHOS-70000416
S710-IR-20 | Preliminary plan and elevation | Preliminary sketch or drawing indicating major (e.g. overall bank length, width, supporting structure height) dimensions in plan and elevation, extent of access platforms,walkways and ladder and the nozzle sizes. | 5.10, 5.2 | PDF
S710-IR-22 | Thermal and hydraulic design calculations | Calculations to support the thermal and hydraulic design. | 6.1.3 | PDF
S710-IR-23 | General Assembly | Drawing is to include but not limited to information such as: • General arrangement of air cooled heat exchanger bay assembly; • Major dimensions in plan and elevation (each bay length/width, total bank length/width, supporting structure height etc.); • Extent and platforms,walkways, ladder; • Dimensions and locations of supports and sizes of hold-down bolts; • Nozzle size, rating, facing, location, projection beyond header surface, allowable loading (forces and moments) and direction of flow; • Purchaser data (Item number, service, project name and location, order number); • Design data (Design code, design pressure, maximum allowable working pressure, test pressure, maximum and minimum design temperature, corrosion allowance); • Material specifications and grades for all pressure parts including gasket; • Weight of the tube bundle, the exchanger empty and full of water, and the mass of the heaviest component (or combination of components) intended by the Vendor for handling in a single lift; • Column reactions for each load type; • Radiographic and other non-destructive examination requirements; • Surface preparation and painting requirements; • Maximum and minimum plug torque values with recommended thread lubrication. | 6.1.1 | PDF | CFIHOS-70000153
S710-IR-24 | Bundle and auxiliary structure detail drawing | Drawing is to include detailed information for: • Gaskets; • Tube bundle including sectional views, welding, and construction details for all pressure parts​; • Structure, walkways, platforms, ladders and stairways, if applicable; • Fan ring including support. | 6.1.1, 6.1.2, 6.1.5 | PDF | CFIHOS-70000116
S710-IR-47 | Component details and assembly drawings | Drawing is to include detailed information for: • Tube bundle frame; • Field assembly; • All auxiliary equipment and controls including cable trays and junction box; • Electrical and control connections including those of motive and signal air for any pneumatically actuated louvers or fans; • Motor suspension assembly including fans, bearings, pulleys, belts etc. as applicable; • Plenum chamber including plenum beams; • Fan screens and guards; • Header guard. | 6.1.1, 6.1.2, 6.1.5 | PDF | CFIHOS-70000116
S710-IR-25 | Noise data sheet | Include actual sound-power and sound-pressure levels of the equipment at designated location, taking into account relevant information, e.g. inlet shape (type and dimension of bell or cone), obstructions, etc. Reference to fan includes driver, speed reducer, etc. | 6.1.1, 5.6, 5.7, 7.2.2.1, 7.2.2.2 | PDF
S710-IR-26 | Fan characteristic curves | Curves to relate static or total pressure, rate of air flow, blade pitch, and fan input shaft power, for dry-air standard conditions. The operating point and shaft power for the specified design conditions,including fan critical speeds for use with variable-frequency drives. | 5.8, 7.2.3.13 | PDF | CFIHOS-70000416
S710-IR-27 | Mechanical design calculations | • Calculations required by the pressure design code for design of pressure components, including header boxes, tubes, tube to tubesheet joints, inlet and outlet process nozzles including swage connections and other non-standard pressure boundary components; • Restraint relief calculations; • Local load analysis due to external forces and moments on nozzles. • Thickness calculations for lifting devices; | 6.1.3 | PDF | CFIHOS-70000086
S710-IR-43 | Structural design calculation | Structural calculations to evaluate column reactions and structural sections strength for each applicable design load and design load combination. | 6.1.3, 7.3.3.1 | PDF | CFIHOS-70000086
S710-IR-28 | Non-destructive examination procedure | Detailed procedure for all the non-destructive examinations carried out including acceptance criteria. Include non-destructive examination procedure carried out on tube-tubesheet weld joint, if applicable, | 6.1.1 | PDF | CFIHOS-70000227
S710-IR-29 | Alloy verification | Detailed procedure for alloy verification of material. | 6.1.1 | PDF
S710-IR-30 | Pickling and passivation | Procedure describing cleaning of stainless steel surfaces and welds to restore their passive oxide film | 6.1.1 | PDF
S710-IR-31 | Post weld heat treatment | A procedure detailing: • material and item type; • holding temperature ranges and soaking times; • heating and cooling rates; • methods of heating and cooling. (e.g., gas, electrical resistance, induction, furnace); • location and number of thermocouples used to control and record the PWHT; • precautions taken to prevent distortion, collapse or other damage as appropriate; • extent of heating and insulation for local or partial PWHT, including sketch. | 6.1.1 | PDF
S710-IR-32 | Test Pressure | Hydrotest procedure for complete (header boxes, nozzles,tubes etc.) bundle assembly including leak testing (if any) carried out. | 10.2.2 | PDF | CFIHOS-70000286
S710-IR-33 | Tube expansion | Procedure for expansion of tubes into tubesheet including expansion dimensional check records to verify expansion. | 6.1.1 | PDF
S710-IR-48 | Tube-to-tubesheet weld joint preparation | Procedure for tube-to-tubesheet welding detailing the sequence of steps for joint preparation, assembly, cleaning,rolling and testing.​ | 9.3.4.3 | PDF
S710-IR-34 | Surface preparation and coating | Vendor's procedures for surface preparation, painting and coating in line with Purchaser requirements such as : a. Environmental requirements b. Color scheme | 10.2.4, 6.1.1 | PDF | CFIHOS-70000384
S710-IR-35 | Heat treatment record | Records of all heat treatment performed on the pressure components and welds are to be attached including chart recording of the measured temperatures. In case of re-heat treatment due to repair, an additional sheet for the re-heat treatment is to be completed. | 6.2.2 | PDF | CFIHOS-70000423
S710-IR-36 | Non-Destructive Examination record | Report of NDE performed on pressure components and welds such as radiography, ultrasonic testing, magnetic particle and liquid penetrant testing. The report includes location, type of NDE and the indications obtained.When repairs are required, the report includes the areas repaired, the nature of defects repaired and the repair procedures used. When ultrasonic examination type of NDE is performed, the following information to be provided: a) pulse-echo unit manufacturer, model, and damping control setting; b) search unit manufacturer, model, dimensions, and the substance (such as oil or water) that is used to couple the transducer with the material being inspected; c) frequency used and the test angle on the component’s surface; and d) wedge medium for angle-beam examination. | 6.1.1 , 6.2.2 | PDF
S710-IR-37 | Welding procedure specification | A specification that describes the welding procedure and process of a specific set of essential variables. | 6.1.4, 9.1.1.1, 9.1.1.5 | PDF | CFIHOS-70000408
S710-IR-49 | Procedure qualification record | Records documenting welding and associated testing of welding processes to a defined set of essential variables. Typically includes all testing procedure references and both destructive and non-destructive testing results. | 6.1.4, 9.1.1.1, 9.1.1.5 | PDF | CFIHOS-70000362
S710-IR-50 | Weld map | a weld map that shall identify each weld joint and the applicable welding procedure specification with information to evaluate qualification of welding procedure specification for respective weld joint, e.g weld joint location, joint type, thickness, diameter (if applicable) and material grade. | 6.1.4 | PDF | CFIHOS-70000360
S710-IR-51 | Weld repair | a procedure to describe a set of logically sequenced instructions to execute a weld repair | 6.1.4 | PDF | CFIHOS-70000363
S710-IR-38 | Assembly lifting plan | Lifting and installation instructions, capturing what particular activities and requirements will be executed and delivered for lifting, hoisting, and rigging. Should cover scope regardless of timing in asset lifecycle. | 6.1.1 | PDF | CFIHOS-70000200
S710-IR-39 | Material test report (2.2) | A document in which the material supplier declares that the products supplied are in compliance with the requirements of the Purchase Order , and in which test results are supplied based on non-specific inspection and testing NOTE: see ISO/IEC 17000, clause 5.5 and ISO 10474 / EN 10204. | 6.1.1 , 6.2.2 | PDF | CFIHOS-70000412
S710-IR-54 | Materials Inspection Certificate (3.1) | A document with test results based on specific inspection and testing, issued by the Vendor and validated by the Vendor's authorised inspection representative independent of the manufacturing department. NOTE: see ISO/IEC 17000, clause 5.5 and ISO 10474 / EN 10204 | 6.1.1, 6.2.2 | PDF
S710-IR-40 | Manufacturer Record Book (MRB) | Detailed information/description for the documents to be included in MRB as agreed between Purchaser and Vendor: Shall include but not be limited to documents Recording Compliance With Statutory and/or Local Regulations, and inspection and testing results / reports for all the testing (e.g. Mill tests on Material, production test coupon results, NDE, NDE personnel qualification, impact test, Heat treatment, leak testing, ferrite testing, hardness testing, shop-run in test etc.) carried out at Vendor/Sub-Vendor shop and at mill. | 6.2.1 | PDF
S710-IR-41 | Installation manual | Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. | 6.1.6 | PDF
S710-IR-53 | Maintenance manual | Description of methods of maintaining a specific piece of equipment when in operation. | 6.1.6 | PDF
S710-IR-52 | Operations manual | Description of methods of operating a piece of equipment or process unit, including but not limited to instructions, procedures, drawings, tables, etc. for the operation -stop, start, and emergency shutdown. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. | 6.1.6 | PDF
S710-IR-42 | Spare parts | List is to indicate spare parts recommended by Vendor. Each item is to be referenced by its original manufacturers name and part number. | 6.1.1, 6.2.2 | PDF | CFIHOS-70000374
S710-IR-45 | Shop Run in test report | The report shall include recorded values for : • Fan tip clearances; • Fan blade pitches as per design blade angle (± 0.5° blade angle); • Fan speeds; • Vibration levels (see 7.3.2.1); • Noise levels (see 7.2.2); • Motor voltage, motor amperage; • Air flow measurements for each fan. | 10.3 | PDF
Purchase Order Specific Information Requirements

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
Intelligent Vector (CAD)
Multi media (Film)
Raster Image (Bitmap)
Structured Data (MS Apps)
Technical Publication (Text)
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: