## Front & Preliminaries
|  |  |  | SPECIFICATION | August
|  |  |  | S-702D | 2020
Data Sheet for
DC Uninterruptible Power Systems
(UPS) (IEC 62040-5-3)
Revision history
| VERSION | DATE | PURPOSE
| 1 | August 2020 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
Data Sheet for
DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
Data Sheet for
DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3)
Introduction
The purpose of this equipment data sheet is to define buyer specific requirements for the procurement of DC uninterruptible power systems (UPS) in accordance with IOGP S-702, for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-702, information requirements specification IOGP S-702L and quality requirements specification IOGP S-702Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet

## Data Sheet
Row | S-702D Data Sheet for DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3) | [5 empty] | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description | [5 empty] | Default
4 | Ref. Clause | Description | Purchaser Identified Values | Manufacturer Declared Values |  | Additional notes
5 |  | GENERAL
6 | 5.1.2 | Vendor : | Input Data
7 | 5.1.2 | Order status : | Select |  |  |  |  | Select | for enquiry | for purchase
8 | 5.1.2 | Purchase order number, date : | Input Data
9 | 5.1.2 | Manufacturer : | Input Data
10 | 5.1.2 | Model number : | Input Data
11 | 5.1.2 | Serial number : | Input Data
12 | 5.2.3 | Application : | Input Data
13 | 5.3.2 | Purchaser specified rated output current : | Input Data |  | A
14 | 5.1.1 | Quantity : | Input Data
15 |  | Conformity assessment system (CAS) level : | D |  |  |  |  | Select | A | B | C | D
16 |  | CONFIGURATION
17 | 5.1.1, A.1, Figure A.1, Figure A.3, Figure A.5 | DC UPS configuration : | Select |  |  |  |  | Select | simplified single DC UPS with blocking diode -Figure A.1 | simplified dual DC UPS with independent output bus -Figure A.5A | simplified dual DC UPS with common output bus -Figure A.5B | other
18 | A.2.2 | Blocking diode required at output of single DC UPS : | Select |  |  |  |  | Select | N/A | No | Yes
19 | A.2.3 | Scalability : | Select |  |  |  |  | Select | N/A | modular | manufacturer standard
20 | 5.1.1 | DC UPS topology : | Select |  |  |  |  | Select | direct energy storage connect | series converter connect | shunt converter connect
21 | B.2.3 | Series converter connect option : | Select |  |  |  |  | Select | N/A | with DC-DC converter | with dropper diode
22 | 5.4.2.3 | Battery configuration : | Select |  |  |  |  | Select | 1 x 100% | 2 x 100% | 2 x 50% | 2 x 50% (with interconnector) | other
23 | 5.3.2, 5.3.4 | Performance classification : | Select | Select |  |  |  | Select | WW | NW | NN
24 | 8.1.1.3 | Bi-directional rectifier : | Select |  |  |  |  | Select | Yes | No
25 | 8.2.2.11 | Remote access required : | No |  |  |  |  | Select | No | Yes (read/write) | Yes (read only)
26 | 8.2.2.11 | Hardware (adapters, connectors, cables, etc.) required for remote monitor : | No |  |  |  |  | Select | No | Yes
27 | 8.1.1.5, 8.1.1.6 | On-line battery monitoring facility required : | No |  |  |  |  | Select | No | string monitoring | cell monitoring
28 | 8.1.1.4 | On-line battery testing feature required : | Select |  |  |  |  | Select | Yes | No
29 | 8.1.1.4 | Battery test load interface : | No |  |  |  |  | Select | No | Yes
30 | 5.4.2.3 | DC earth leakage monitoring required : | No |  |  |  |  | Select | No | Yes
31 | 7.4.14 | Single line diagram and status display : | Select |  |  |  |  | Select | on mimic | on HMI | on both mimic and HMI
32 | 8.1.2.11 | Black Start feature required : | Select |  |  |  |  | Select | Yes | No
33 | 8.1.1.1 | Earth screen required for isolation transformer : | Select |  |  |  |  | Select | Yes | No | manufacturer to advise
34 |  | PHYSICAL ASPECTS
35 | 7.2.1 | Mounting : | Select |  |  |  |  | Select | floor mounting | wall mounting
36 | 7.2.1 | Overall cabinet dimensions - length : | Input Data | Input Data | mm
37 | 7.2.1 | Overall cabinet dimensions - depth : | Input Data | Input Data | mm
38 | 7.2.1 | Overall cabinet dimensions - height : | Input Data | Input Data | mm
39 | 7.2.1 | Reference Outline Drawing number : | Input Data
40 | 7.2.1 | Total DC UPS cabinet mass : | Input Data |  | kg
41 | 7.2.1 | Total DC UPS mass with batteries (if integrated) : | Input Data |  | kg
42 | 7.2.4, 7.2.5 | Cable entry location : | Select |  |  |  |  | Select | bottom | top | both bottom and top
43 | 7.2.4, 7.2.5 | Cable entry type : | Select |  |  |  |  | Select | removable - undrilled plate | multi cable transit (MCT)
44 | 7.2.4, 7.2.5 | Gland plate material : | Select |  |  |  |  | Select | manufacturer standard | non-magnetic plate
45 | 7.2.1 | Paint colour : | Select |  |  |  |  | Select | supplier standard | other
46 | 7.2.1 | Canopy for cabinet required : | No |  |  |  |  | Select | No | Yes
47 | 7.3.5 | Document holder : | Yes |  |  |  |  | Select | Yes | No
48 |  | INSTALLATION
49 | 4.1 | Site : | Select |  |  |  |  | Select | onshore - coastal | onshore - desert | onshore - inland | offshore - fixed | offshore - floating | marine (ship)
50 | 4.1 | Location of DC UPS cabinet installation : | Select |  |  |  |  | Select | indoor | outdoor
51 | 7.3.1, 7.3.2 | Front access clearance dimensions for operation and maintenance : | Input Data |  | mm
52 | 7.3.2 | Side clearance for ventilation (if required) : | Input Data |  | mm
53 | 7.3.2 | Rear clearance for ventilation (if required) : | Input Data |  | mm
54 | 7.2.3, 7.9.3 | Installed location of battery : | Select |  |  |  |  | Select | battery room | inside DC UPS room | inside DC UPS enclosure | separate indoor battery cabinet | outdoor (battery enclosure) | outdoor (hazardous area battery enclosure)
55 | 7.2.3 | Maximum battery assembly dimensions (L x D x H) : | Input Data |  | mm
56 |  | SAFETY
57 | 5.1.1 | Accessibility : | Select |  |  |  |  | Select | operator access area | service access area | restricted access location
58 | 5.1.1 | Key required for cabinet : | Select |  |  |  |  | Select | Yes | No
59 | 7.2.2 | Degree of protection (with closed doors) : | IP31 | IP31 |  |  |  | Select | IP31 | IP32 | IP42 | IP44 | IP55 | manufacturer standard
60 | 7.2.2 | Degree of protection (with open doors) : | IP2X | IP2X |  |  |  | Select | IP2X | IP3X
61 | 4.3.2 | Area classification : | Select |  |  |  |  | Select | safe | hazardous
62 | 4.3.2 | Hazardous area certification required : | Select |  |  |  |  | Select | none | ATEX | IECEx
63 | 4.3.2 | Level of protection : | Select |  |  |  |  | Select | N/A | Ex-db | Ex-db eb
64 | 4.3.2 | Gas group : | Select |  |  |  |  | Select | IIA | IIB | IIB + H2 | IIC
65 | 4.3.2 | Temperature class : | Select |  |  |  |  | Select | T3 | T4 | T5 | T6 | T1 | T2
66 | 4.3.2 | Equipment protection level : | Select |  |  |  |  | Select | Ga | Gb | Gc
67 | 7.7.5 | Cooling fan replacement while DC UPS in service : | No |  |  |  |  | Select | No | Yes
68 | 5.1.2 | Local language for caution/danger/warning labels : | Input Data
69 |  | ELECTROMAGNETIC COMPATIBLITY
70 | 5.1.4 | Emission : | UPS Cat C3 |  |  |  |  | Select | UPS Cat C3 | UPS Cat C2 | UPS Cat C1 | UPS Cat C4
71 | 5.1.4 | Immunity : | UPS Cat C3 |  |  |  |  | Select | UPS Cat C3 | UPS Cat C2 | UPS Cat C1 | UPS Cat C4
72 |  | ENVIRONMENTAL CONDITIONS
73 | 4.2.1.1 | Minimum ambient temperature (operation) : | Input Data |  | °C
74 | 4.2.1.1 | Maximum ambient temperature (operation) : | Input Data |  | °C
75 | 4.2.1.1 | Maximum relative humidity (operation) : | Input Data |  | %
76 | 4.2.1.1 | Temperature at which relative humidity is specified (operation) : | Input Data |  | °C
77 | 4.2.1.2 | Maximum altitude (operation) : | Input Data |  | m
78 | 4.2.2 | Minimum ambient temperature (storage and transportation) : | Input Data |  | °C
79 | 4.2.2 | Maximum ambient temperature (storage and transportation) : | Input Data |  | °C
80 | 4.2.2 | Maximum relative humidity (storage and transportation) : | Input Data |  | %
81 | 4.2.2 | Temperature at which relative humidity is specified (storage and transportation) : | Input Data |  | °C
82 | 4.3.2 | Seismic requirement data : | Input Data
83 | 4.2.2 | Storage site of DC UPS : | Select |  |  |  |  | Select | indoor – climate controlled (humidity and temperature) | indoor – temperature controlled only | indoor – natural ventilation | outdoor | refer abnormal or unusual conditions below
84 | 4.3.2 | Additional or unusual conditions (operation) : | Input Data
85 | 4.3.3 | Additional or unusual conditions (storage and transportation) : | Input Data
86 | 5.1.5 | Acoustic noise at 1 m - normal mode : | Select |  | dBA |  |  | Select | 70 | other
87 | 5.1.5 | Acoustic noise at 1 m - stored energy mode : | Select |  | dBA |  |  | Select | 70 | other
88 |  | COMMUNICATION INTERFACE(S)
89 | 5.6 | (1) Interface media for SCADA (ICSS / DCS) : | Select |  |  |  |  | Select | none | hardwired discrete | serial | ethernet (Cu) | ethernet (fiber) | wireless | other
90 | 5.6 | (1) Maximum allowable length of communication cable (for copper) : | Input Data |  | m
91 | 5.6 | (1) Interface protocol for SCADA (ICSS / DCS) : | Select |  |  |  |  | Select | N/A | potential free contact | RS485 | Modbus | Profinet | other
92 | 5.6 | (2) Interface media for Electrical Management / Control System : | Select |  |  |  |  | Select | none | hardwired discrete | serial | ethernet (Cu) | ethernet (fiber) | wireless
93 | 5.6 | (2) Maximum allowable length of communication cable (for copper) : | Input Data |  | m
94 | 5.6 | (2) Interface protocol for Electrical Management / Control System : | Select |  |  |  |  | Select | N/A | potential free contact | RS485 | Modbus | Profinet | other
95 | 5.6 | (3) Remote access / monitoring software required : | Select |  |  |  |  | Select | Yes | No
96 | 5.6 | (3) Interface media for Remote access / monitoring : | Select |  |  |  |  | Select | none | ethernet (Cu) | ethernet (fiber) | wireless
97 | 5.6 | (3) Maximum allowable length of communication cable (for copper) : | Input Data |  | m
98 | 5.6 | (3) Interface protocol for Remote access / monitoring : | Select |  |  |  |  | Select | N/A | SNMP | HTTPS | RDP | SFTP | Modbus | Profinet | other / supplier standard
99 |  | AC INPUT SPECIFICATIONS
100 | 5.2.1 | Voltage (steady state, R.M.S) - rated : | Input Data |  | V
101 | 5.2.1 | Voltage (steady state, R.M.S - tolerance : | Input Data |  | %
102 | 5.2.1 | Frequency - rated : | Select |  |  |  |  | Select | 50 Hz | 60 Hz
103 | 5.2.1 | Frequency - tolerance : | Input Data |  | %
104 | 5.2.2 | Phases required : | Select | Select |  |  |  | Select | 1 | 2 | 3
105 | 5.2.2 | Neutral required : | Select | Select |  |  |  | Select | Yes | No
106 | 5.2.2 | Current (R.M.S) - rated (with the energy storage device charged) : | Input Data |  | A
107 | 5.2.2 | Power factor : | Input Data | Input Data
108 | 5.2.2 | In-rush (% of rated current) : | Input Data | Input Data | %
109 | 5.2.2 | In-rush (time) : | Input Data | Input Data | s
110 | 5.2.2 | Maximum current (with low input volt and energy storage device charging) : | Input Data |  | A
111 | 5.2.2 | Time for overload (125 % of rated current) : | Input Data | Input Data | s
112 | 5.2.2 | Time for overload (150 % of rated current) : | Input Data | Input Data | s
113 | 5.2.2 | Total harmonic distortion (THD p.u.) : | Input Data |  | %
114 | 5.2.3 | Short circuit current of the input supply : | Input Data |  | kA
115 | 5.2.2 | Minimum prospective short circuit current : | Input Data |  | kA
116 | 5.2.2 | Earth leakage current : | Input Data |  | mA
117 | 5.2.2 | AC power distribution system - compatibility : | Select |  |  |  |  | Select | TN-C | TN-S | TN-C-S | TT | IT
118 | 5.2.3 | Additional or unusual conditions : | Input Data
119 | 5.2.3, 7.5.4 | Cable Size (cross-section area) - input mains (Float) : | Input Data |  | sq.mm.
120 | 7.5.4 | Cable Size (cross-section area) - input mains (Boost) : | Input Data |  | sq.mm.
121 | 7.4.8, 8.1.1.1 | Input isolation transformer required : | Select |  |  |  |  | Select | Yes | No
122 | 7.4.10 | Input isolation transformer winding : | Select |  |  |  |  | Select | copper | aluminum | copper or aluminum
123 |  | DC AND BATTERY SPECIFICATIONS
124 | 5.4.2.2 | DC voltage level : | Select |  | V d.c. |  |  | Select | 110 | 220 | 380 | other
125 | 5.4.2.2 | Design life : | Input Data |  | years
126 | 5.4.2.2 | Float service life : | Input Data |  | years
127 | 5.4.2.2 | Shelf life of battery : | Input Data |  | months
128 | 5.4.2.2 | Quantity of cells and strings : | Input Data |  | nos.
129 | 5.4.2.2 | Nominal voltage (total) : | Input Data |  | V d.c.
130 | 5.4.2.2 | Battery technology : | Select |  |  |  |  | Select | nickel cadmium partial gas recombination | vented nickel cadmium | sealed nickel cadmium | valve regulated lead acid - AGM | valve regulated lead acid - gel | vented lead acid | other
131 | 5.4.2.2 | Nominal AH capacity : | Input Data |  | AH
132 | 5.4.2.2 | Discharge rate (C-rate) : | Select |  |  |  |  | Select | C5 | C10
133 | 5.4.2.2 | Electrolyte fill status : | Select | Select |  |  |  | Select | manufacturer standard | dry-uncharged | dry-charged | wet-charged | filled-uncharged | filled-charged
134 | 8.1.2.3 | Purchaser's requirement (% of battery recharge level - 1) : | 80 |  | % |  |  | Select | 80 | 85 | 90 | 100
135 | 8.1.2.3 | Purchaser's requirement (time for battery recharge level - 1) : | 10 |  | Hours |  |  | Select | 10 | 12 | 8 | 24
136 | 8.1.2.3 | Purchaser's requirement (% of battery recharge level - 2) : | 100 |  | % |  |  | Select | 80 | 85 | 90 | 100
137 | 8.1.2.3 | Purchaser's requirement (time for battery recharge level - 2) : | 24 |  | Hours |  |  | Select | 10 | 12 | 8 | 24
138 | 5.4.2.2 | Stored energy time (back-up time at 100% rated load) : | Input Data | Input Data | min
139 | 5.4.2.2 | Restored energy time (recharge time to 80% capacity) : | Input Data |  | hours
140 | 5.4.2.2 | Ambient reference temperature : | Input Data |  | °C
141 | 5.4.2.2 | Earth condition/isolation : | Select | Select |  |  |  | Select | floating | positive earthed | negative earthed
142 | 5.4.2.2 | Ripple current (R.M.S) : | Select |  | % |  |  | Select | battery manufacturer standard | 5 | 2 | 1
143 | 5.4.2.2 | Maximum discharge current : | Input Data |  | A
144 | 5.4.2.2 | DC Fault current rating : | Input Data |  | A d.c.
145 | 5.4.2.2 | Cable volt drop recommendation (≤ % at nominal discharge current) : | Input Data |  | %
146 | 5.4.2.2 | Charging regime : | Input Data
147 | 5.4.2.2 | Charge voltage (float) and tolerance band : | Input Data |  | V d.c.
148 | 5.4.2.2 | Charge voltage (boost) and tolerance band : | Input Data |  | V d.c.
149 | 5.4.2.2 | Charge voltage (equalising) and tolerance band : | Input Data |  | V d.c.
150 | 5.4.2.2 | Minimum end of discharge voltage : | Input Data |  | V d.c.
151 | 5.4.2.2 | Charge current limit (or range) : | Input Data |  | A d.c.
152 | 5.4.2.2 | Temperature compensated charging required : | Select |  |  |  |  | Select | Yes | No
153 | 5.4.2.3 | Battery isolation box required : | Select |  |  |  |  | Select | Yes | No
154 | 5.4.2.3 | Additional or unusual conditions : | Input Data
155 | 5.4.2.3 | Load profile for battery design, attached : | Yes |  |  |  |  | Select | Yes | No
156 | 5.4.2.3 | Battery rack design : | Select |  |  |  |  | Select | standard | seismic rated
157 |  | BATTERY ROOM
158 | 4.2.1.1 | Minimum ambient reference temperature : | Input Data |  | °C
159 | 4.2.1.1 | Maximum ambient reference temperature : | Input Data |  | °C
160 | 5.4.2.1 | Area classification : | Select |  |  |  |  | Select | safe | hazardous
161 | 5.4.2.1 | Hazardous area classification : | Select |  |  |  |  | Select | N/A | Zone 1 | Zone 2
162 | 5.4.2.1 | Minimum Gas Subdivision and Temperature Class (for equipment in Battery room) : | Select |  |  |  |  | Select | N/A | IIB+H2 T3 | IIC T3
163 | 8.1.2.10 | Temperature sensor (for VRLA / partial gas recombination batteries) : | Select |  |  |  |  | Select | Yes | No
164 |  | BATTERY ISOLATOR BOX SPECIFICATIONS
165 | 7.9.1 | Enclosure material : | Select | Select |  |  |  | Select | manufacturer standard | sheet steel | light alloy | stainless steel
166 | 7.9.1 | Mounting : | Select |  |  |  |  | Select | on wall | on structural steel pedestal | on stainless steel frame
167 | 7.9.1 | Breathing valve required : | Select | Select |  |  |  | Select | Yes | No | manufacturer to advise
168 | 7.9.1 | Internal earth bar : | Select |  |  |  |  | Select | copper | tinned copper
169 | 7.9.3 | Minimum design temperature : | Input Data |  | °C
170 | 7.9.3 | Maximum design temperature : | Input Data |  | °C
171 | 7.9.3 | Maximum relative humidity : | Input Data |  | %
172 | 7.9.3 | Temperature at which relative humidity is specified : | Input Data |  | °C
173 | 7.9.4 | Degree of protection : | Select |  |  |  |  | Select | IP44 | IP55 | IP66 | other
174 | 7.9.5 | Area classification : | Select |  |  |  |  | Select | safe | hazardous
175 | 7.9.5 | Hazardous Area Certification required : | Select |  |  |  |  | Select | none | ATEX | IECEx | EAC
176 | 7.9.5 | Hazardous area classification : | Select |  |  |  |  | Select | N/A | Zone 1 | Zone 2
177 | 7.9.5 | Hazardous area level of protection : | Select |  |  |  |  | Select | N/A | Refer to section "SAFETY" above | Ex-db eb IIB T3 Gb | Ex-db eb IIB+H2 T3 Gb | Ex-db eb IIC T3 Gb | Ex-db eb IIB T4 Gb | Ex-db eb IIC T4 Gb | Ex-db eb IIB T6 Gb | Ex-db eb IIC T6 Gb
178 | 7.9.6 | Cable entry : | Select |  |  |  |  | Select | bottom | top | bottom & side | top & side | all sides
179 | 7.9.6 | Cable indirect entry via 'ex e' enclosure : | Select |  |  |  |  | Select | Yes | No
180 | 7.9.6 | Battery cable size (cross-section area) : | Input Data |  | sq.mm.
181 | 7.9.6 | Cable entry diameter in battery isolator box (ISO metric) : | Input Data
182 | 7.9.7 | Battery isolator type : | Select |  |  |  |  | Select | MCCB | switch fuse unit
183 | 7.9.8 | Rated current of breaker / switch fuse unit : | Input Data |  | A
184 | 7.9.8 | Rated breaking current (Icu) - (if breaker used) : | Input Data |  | kA
185 | 7.9.10 | Breaker status potential free contact (NO) : | Select |  |  |  |  | Select | two | one | none
186 | 7.9.9 | Under Voltage trip feature required : | No |  |  |  |  | Select | No | Yes
187 | 7.9.9 | Under Voltage trip coil for : | N/A |  |  |  |  | Select | N/A | deep discharge protection | black start reserve
188 | 8.1.2.12 | ESD trip required : | Select |  |  |  |  | Select | No | Yes - via undervoltage trip | Yes - via shunt trip
189 | 8.1.2.12 | ESD override key switch : | Select |  |  |  |  | Select | N/A | key captive in overridden position and with status contact
190 | 7.9.9 | Over voltage trip required : | No |  |  |  |  | Select | No | Yes
191 |  | DC OUTPUT SPECIFICATIONS
192 | 5.3.2 | DC power distribution system - compatibility : | Select |  |  |  |  | Select | TN-C | TN-S | TN-C-S | TT | IT
193 | 5.3.2 | Voltage (steady state) - rated : | Input Data | Input Data | V d.c.
194 | 5.3.2 | Voltage - normal mode variation at no load : | Input Data | Input Data | %
195 | 5.3.2 | Voltage - normal mode variation at full load : | Input Data | Input Data | %
196 | 5.3.2 | Voltage - storage energy mode variation at no load : | Input Data | Input Data | %
197 | 5.3.2 | Voltage - storage energy mode variation at full load : | Input Data | Input Data | %
198 | 5.3.2 | % Voltage transient - transfer normal mode to storage energy mode : | Input Data |  | %
199 | 5.3.2 | Voltage transient time - transfer normal mode to storage energy mode : | Input Data |  | s
200 | 5.3.2 | % Voltage transient - transfer storage energy mode to normal mode : | Input Data |  | %
201 | 5.3.2 | Voltage transient time - transfer storage energy mode to normal mode : | Input Data |  | s
202 | 5.3.2 | % Voltage variation - normal mode at step load : | Input Data |  | %
203 | 5.3.2 | Duration of voltage variation - normal mode at step load : | Input Data |  | s
204 | 5.3.2 | % Voltage variation - storage energy mode at step load : | Input Data |  | %
205 | 5.3.2 | Duration of voltage variation - storage energy mode at step load : | Input Data |  | s
206 | 5.3.2 | Current - rated : | Input Data |  | A d.c.
207 | 5.3.2 | Current - overload capability (% of rated current for ten minutes) : | Input Data |  | %
208 | 5.3.2 | Current - overload capability (% of rated current for one minute) : | Input Data |  | %
209 | 5.3.2 | Current - short circuit capability (% of rated current) : | Input Data | Input Data | %
210 | 5.3.2 | Current - short circuit capability (time duration) : | Input Data | Input Data | s
211 | 5.3.2 | Current - limitation (% of rated current) : | Input Data |  | %
212 | 5.3.2 | Current - limitation (time duration) : | Input Data |  | s
213 | 5.3.2 | Current - fault clearing capability (normal mode) : | Input Data |  | A
214 | 5.3.2 | Current - fault clearing capability (stored energy mode) : | Input Data |  | A
215 | 5.3.2 | AC / DC efficiency in normal mode - 100% load : | Input Data |  | %
216 | 5.3.2 | AC / DC efficiency in normal mode - 75% load : | Input Data |  | %
217 | 5.3.2 | AC / DC efficiency in normal mode - 50% load : | Input Data |  | %
218 | 5.3.2 | AC / DC efficiency in normal mode - 25% load : | Input Data |  | %
219 | 5.3.2 | No load losses : | Input Data |  | W
220 | 7.1.6 | Reference document to DC output distribution board : | Input Data
221 | 5.3.3 | Additional or unusual conditions : | Input Data
222 | 5.3.3 | Cable size (cross-section area) - output : | Input Data |  | sq.mm.
Note on C6: Specify supplier's name, if supplier is not the manufacturer
Note on C7: Select the stage of procurement that this datasheet is being issued. (Default - Select)
Note on C8: Specify confirmed purchase order details
Note on C9: Supplier's Name
Note on C10: Specify the Product Series, Range or Model number, etc.
Note on C11: Specify the Product Serial number
Note on C12: Purchaser to select the intended application of the DC UPS.
Note on C13: Purchaser to specify the rated output current requirement
Note on C14: Specify quantity of DC UPS system being procured
Note on C15: Select CAS level as applied in S-702Q, Annex A. (Default - D)
Note on C17: Specify the DC UPS configuration. If other selected, use Additional notes to specify. (Default - Select)
Note on C18: Select whether blocking diode is required at output of single DC UPS. (Default - Select)
Note on C19: Select the scalability option. (Default - Select)
Note on C20: Select the desired UPS topology. (Default - Select)
Note on C21: Select the option for component / sub-assembly used on the output side. (Default - Select)
Note on C22: Select the desired battery configuration (where 50% implies 50% load for 100% autonomy time). If other selected, use Additional notes to specify. (Default - Select)
Note on C23: Select the performance classification based on the application intended. (Default - Select)
Note on C24: Select this feature (active front end), if battery is to be discharged and fed back in to source supply. (Default - Select)
Note on C25: Select if DC UPS system needs to be accessed from a central location or a remote location through intranet or internet. (Default - No)
Note on C26: Select if any specific hardware is required for interface with existing installation or other third party systems. (Default - No)
Note on C27: Select if additional system is envisaged for monitoring of storage energy batteries. (Default - No)
Note on C28: Select if feature is required for allowing rectifier to be blocked and battery to be drained for a specified time for on-line testing of storage energy batteries. (Default - Select)
Note on C29: Select the requirement if an interface (connection to load bank) is required. (Default - No)
Note on C30: Select if earth leakage protection is required for storage energy batteries. (Default - No)
Note on C31: Select the way in which Single line diagram and status shall be displayed. (Default - Select)
Note on C32: Select whether black start feature (deliver specified output voltage to load with only batteries connected) is required or not. (Default - Select)
Note on C33: Select option for use of earth screen in isolation transformer. (Default - Select)
Note on C35: Purchaser to select preferred mounting option of UPS (whether wall or floor mounting). (Default - Select)
Note on C36: Specify the overall cabinet dimensions - Length
Note on C37: Specify the overall cabinet dimensions - Width
Note on C38: Specify the overall cabinet dimensions - Height
Note on C39: Supplier to specify the GA drawing number for cross reference.
Note on C40: Specify the overall cabinet mass (excluding batteries)
Note on C41: Specify the overall cabinet mass including batteries (if batteries are integral to the cabinet)
Note on C42: Select cable entry location based on the installation planned. (Default - Select)
Note on C43: Supplier to select the type of cable entry considered for the cabinet (gland plate or MCT). (Default - Select)
Note on C44: Select the gland plate material type considering type of input power cable (1C or 3C). (Default - Select)
Note on C45: Select choice of external paint shade for cabinet. If other selected, use Additional notes to specify. (Default - supplier standard)
Note on C46: Select choice of canopy for cabinet. (Default - No)
Note on C47: Purchaser to specify requirement of document holder inside cabinet. (Default - Yes)
Note on C49: Select choice of UPS installation site. (Default - Select)
Note on C50: Select choice of location for installation of UPS. (Default - Select)
Note on C51: Specify front clearance dimension required in mm.
Note on C52: Specify side clearance dimension required in mm
Note on C53: Specify rear clearance dimension required in mm.
Note on C54: Select as per location of storage energy battery. (Default - Select)
Note on C55: Purchaser to specify the allocated space for DC UPS, in case of space constraint
Note on C57: Select the accessibility permitted for the area where DC UPS is installed. (Default - Select)
Note on C58: Select whether key is required for gaining access to the cabinet. (Default - Select)
Note on C59: Select ingress protection as per the installation location with cabinet doors closed. (Default - IP31)
Note on C60: Select ingress protection as per the installation location with cabinet doors opened. (Default - IP2X)
Note on C61: Select whether cabinet is installed in Safe or Hazardous area. (Default - Select)
Note on C62: Select which certification is required for DC UPS. (Default - Select)
Note on C63: Select the hazardous area level of protection, (Default - Select)
Note on C64: Select the gas group. (Default - Select)
Note on C65: Select temperature class. (Default - Select)
Note on C66: Specify equipment protection level. (Default - Select)
Note on C67: Purchaser to select whether it is required for the UPS cooling fan to be replaced while UPS is in service. (Default - No)
Note on C68: Purchaser to specify additional local / Native language to be used for describing Caution / Danger / Warning information on the labels of equipment.
Note on C70: Select category applicable for EMC emission. (Default - UPS Cat C3)
Note on C71: Select category applicable for EMC immunity. (Default - UPS Cat C3)
Note on C73: Specify minimum ambient temperature expected during operation
Note on C74: Specify maximum ambient temperature expected during operation
Note on C75: Specify maximum relative humidity expected during operation
Note on C76: Specify temperature at which relative humidity is specified while in operation
Note on C77: Specify installation altitude above mean sea level
Note on C78: Specify minimum ambient temperature expected during storage and transportation
Note on C79: Specify maximum ambient temperature expected during storage and transportation
Note on C80: Specify maximum relative humidity expected during storage and transportation
Note on C81: Specify temperature at which relative humidity is specified during storage and transportation
Note on C82: Specify seismic data in terms of 'g'force or acceleration.
Note on C83: Select choice of DC UPS storage site. (Default - Select)
Note on C84: Specify additional or unusual conditions expected during operation
Note on C85: Specify additional or unusual conditions expected during storage and transportation
Note on C86: Select acoustic noise at 1 m - during operation in normal mode. If other selected, use Additional notes to specify. (Default - Select)
Note on C87: Specify acoustic noise at 1 m - during operation in storage energy mode. If other selected, use Additional notes to specify. (Default - Select)
Note on C89: Select the Interface media as per project requirement. If other selected, use Additional notes to specify. (Default - Select)
Note on C90: Specify the limitation of communication cable length, if any.
Note on C91: Select interface protocol as per project requirement. If other selected, use Additional notes to specify. (Default - Select)
Note on C92: Select the Interface media as per project requirement. (Default - Select)
Note on C93: Specify the limitation of communication cable length, if any.
Note on C94: Select interface protocol as per project requirement. If other selected, use Additional notes to specify. (Default - Select)
Note on C95: Select whether Remote access / monitoring software is required or not. (Default - Select)
Note on C96: Select the Interface media as per project requirement. (Default - Select)
Note on C97: Specify the limitation of communication cable length, if any.
Note on C98: Select interface protocol as per project requirement. If other selected, use Additional notes to specify. (Default - Select)
Note on C100: Specify rated input voltage
Note on C101: Specify input voltage tolerance
Note on C102: Select rated input frequency. (Default - Select)
Note on C103: Specify input frequency tolerance
Note on C104: Select number of phases of input supply. (Default - Select)
Note on C105: Select whether neutral available for input supply. (Default - Select)
Note on C106: Specify rated input current drawn with the energy storage device charged
Note on C107: Specify input power factor
Note on C108: Specify current inrush as % of rated current.
Note on C109: Specify current inrush time.
Note on C110: Specify maximum current drawn with the input voltage at the minimum (-ve) tolerance and the energy storage device getting charged
Note on C111: Specify the time for which 125 % overload current can be sustained
Note on C112: Specify the time for which 150 % overload current can be sustained
Note on C113: Specify the total harmonic distortion of current
Note on C114: Specify the input supply short circuit current capacity
Note on C115: Specify the prospective short circuit current on the input side
Note on C116: Specify the earth leakage current characteristics (where in excess of 3.5mA)
Note on C117: Select applicable power system earthing schemes. (Default - Select)
Note on C118: Specify additional or unusual conditions expected at the input supply end
Note on C119: Mention input power cable details for Float module
Note on C120: Mention input power cable details of Boost module
Note on C121: Select whether isolation transformer is required at the input side. (Default - Select)
Note on C122: Select the transformer winding material. (Default - Select)
Note on C124: Select the DC Voltage level. If other selected, use Additional notes to specify. (Default - Select)
Note on C125: Specify the design life as declared for the batteries
Note on C126: Specify the float service life as declared for the batteries
Note on C127: Supplier to specify the shelf life (storage) of the selected battery
Note on C128: Specify the quantity of cells and strings as per the battery bank arrangement
Note on C129: Specify the rated battery bank voltage
Note on C130: Select the battery type as per project requirement. If other selected, use Additional notes to specify. (Default - Select)
Note on C131: Specify the nominal AH capacity of the selected cell to form the battery bank
Note on C132: Specify the discharge rate of the selected cell. (Default - Select)
Note on C133: Select the status (electrolyte fill and charge) of battery before it is transported. (Default - Select)
Note on C134: Purchaser to select the intermediate level of state of charge which needs to be achieved following a discharge at rated load. (Default - 80%).
Note on C135: Purchaser to select the time to attain the intermediate level of state of charge following a discharge at rated load. (Default - 10 Hours).
Note on C136: Purchaser to select the final level of state of charge which needs to be achieved following a discharge at rated load. (Default - 100%).
Note on C137: Purchaser to select the time to attain the final level of state of charge following a discharge at rated load. (Default - 24 Hours).
Note on C138: Specify the duration of back up available from battery bank feeding 100% rated load
Note on C139: Specify the duration of charging time required to restore 80% capacity of the battery bank
Note on C140: Specify the value of ambient temperature considered as reference value
Note on C141: Specify the polarities, if any, that are earthed by the installer (remote battery only). (Default - Select)
Note on C142: Select the value of ripple current as % of the numerical AH (C10) capacity of batteries. (Default - Select)
Note on C143: Specify the value of maximum discharge current at the end of the discharge during stored energy mode of operation
Note on C144: Specify the value of d.c. fault current rating
Note on C145: Specify the value of recommended voltage drop across battery cable (≤ % at nominal discharge current).
Note on C146: Specify one or more of the charging methods, namely, constant voltage, constant current, boost, equalization, two-state charging.
Note on C147: Specify the charging voltage (float) with tolerance band
Note on C148: Specify the charging voltage (boost) with tolerance band
Note on C149: Specify the charging voltage (equalising) with tolerance band
Note on C150: Specify the minimum value of end of discharge voltage
Note on C151: Specify the value of current limit during charging or range of charging current
Note on C152: Select whether charging rate shall be controlled using the temperature feedback from batteries. (Default - Select)
Note on C153: Select as required. (Default - Select)
Note on C154: Specify additional or unusual conditions expected at the input supply end
Note on C155: Select whether the battery load profile is attached or not. (Default - Yes)
Note on C156: Select the basis for battery rack design. (Default - Select)
Note on C158: Specify minimum ambient reference temperature expected in battery room
Note on C159: Specify maximum ambient reference temperature expected in battery room
Note on C160: Select the area classification of the battery room. (Default - Select)
Note on C161: Select the Hazard zone classification within the battery room. (Default - Select)
Note on C162: Select the minimum gas subdivision and Temperature Class for equipment in the battery room other than batteries. (Default - Select)
Note on C163: Select inclusion of temperature sensor in scope of supply, if temperature controlled charging is envisaged. (Default - Select)
Note on C165: Select the material of construction for Isolator box. (Default - Select)
Note on C166: Select the mounting provision required for the isolator box. (Default - Select)
Note on C167: Select whether breathing valve is required for Isolator box. (Default - Select)
Note on C168: Select the material of construction for internal busbars of Isolator box. (Default - Select)
Note on C169: Specify minimum design temperature for the Isolator box
Note on C170: Specify maximum design temperature for the Isolator box
Note on C171: Specify maximum relative humidity of area where Isolator box is installed
Note on C172: Specify temperature at which relative humidity is specified where battery box is installed
Note on C173: Select ingress protection as per the installation location. If other selected, use Additional notes to specify. (Default - Select)
Note on C174: Select whether cabinet is installed in Safe or Hazardous area. (Default - Select)
Note on C175: Select which certification is required for battery isolator box. (Default - Select)
Note on C176: Select Hazardous area classification type. (Default - Select)
Note on C177: Select Hazardous area certification type. (Default - Select)
Note on C178: Select cable entry location based on the installation planned. (Default - Select)
Note on C179: Select whether the cable entry is via 'ex-e' enclosure. (Default - Select)
Note on C180: Supplier to specify battery cable size as per cable sizing calculation considering type of cable, discharge current, cable laying route, distance, etc.
Note on C181: Specify the metric size of entry in battery isolator box for cable entry
Note on C182: Purchaser to select option as per project philosophy. (Default - Select)
Note on C183: Specify the standard (rated) ampere value of battery breaker
Note on C184: Specify the maximum breaking capacity of a circuit breaker at an associated rated operational voltage
Note on C185: Select whether potential free contact is required as wired out contacts. (Default - Select)
Note on C186: Purchaser to select whether Undervoltage trip feature is required in the Battery Isolator Box. (Default - No)
Note on C187: Purchaser to select the purpose for which Under voltage trip coil is considered in the Battery isolator box. (Default - N/A)
Note on C188: Purchaser to select whether ESD trip feature is required in the Battery Isolator box. (Default - Select)
Note on C189: Purchaser to select whether ESD override switch key switch is required and with captive feature. (Default - Select)
Note on C190: Purchaser to select whether Over voltage trip is required in the Battery Isolator box. (Default - No)
Note on C192: Select applicable DC power system earthing schemes. (Default - Select)
Note on C193: Specify rated steady state output voltage
Note on C194: Specify output voltage variation while in normal mode operation at no load
Note on C195: Specify output voltage variation while in normal mode operation at full load
Note on C196: Specify output voltage variation while in storage energy mode operation at no load
Note on C197: Specify output voltage variation while in storage energy mode operation at full load
Note on C198: Specify the % voltage transient (output) during transfer from normal mode to storage energy mode
Note on C199: Specify the output voltage transient time during transfer from normal mode to storage energy mode
Note on C200: Specify the % voltage transient (output) during transfer from storage energy mode to normal mode
Note on C201: Specify the output voltage transient time during transfer from storage energy mode to normal mode
Note on C202: Specify % voltage variation (output) while in normal mode operation when a step load in two steps (20% and then 80%) is applied.
Note on C203: Specify duration of voltage variation (output) while in normal mode operation when a step load in two steps (20% and then 80%) is applied.
Note on C204: Specify % voltage variation (output) while in storage energy mode operation when a step load in two steps (20% and then 80%) is applied.
Note on C205: Specify duration of voltage variation (output) while in storage energy mode operation when a step load in two steps (20% and then 80%) is applied.
Note on C206: Specify value of rated output current drawn by the 100% rated load
Note on C207: Specify value of additional current drawn by the increased load (overload) as a % of rated current for ten minutes
Note on C208: Specify value of additional current drawn by the increased load (overload) as a % of rated current for one minute
Note on C209: Specify the short circuit current (%of rated current)
Note on C210: Specify the time duration (time in seconds) to withstand the short circuit current.
Note on C211: Specify value of maximum current that can be drawn by the load.
Note on C212: Specify value of time duration for which the maximum current that can be drawn by the load.
Note on C213: Specify the fuse type and its rating for the maximum value of output current that shall be cleared by this protection device with normal mode operation
Note on C214: Specify the fuse type and its rating for the maximum value of output current that shall be cleared by this protection device with stored energy mode operation
Note on C215: Specify value of efficiency at 100% load during normal mode of operation
Note on C216: Specify value of efficiency at 75% load during normal mode of operation
Note on C217: Specify value of efficiency at 50% load during normal mode of operation
Note on C218: Specify value of efficiency at 25% load during normal mode of operation
Note on C219: Specify value of no load losses during normal mode of operation
Note on C220: Specify reference details to documents of DC distribution board
Note on C221: Specify additional or unusual conditions expected at the input supply end
Note on C222: Specify power cable details of output side.

## Supplement
Row |  | S-702D Data Sheet for DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3) | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95

## Guidance
Data Sheet for
DC Uninterruptible Power Systems (UPS) (IEC 62040-5-3)
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-702 Supplementary Specification to IEC 62040-5-3 DC Uninterruptible Power Systems (UPS).
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.