## Front & Preliminaries
|  |  |  | SPECIFICATION | September
|  |  |  | S-732D | 2020
Data Sheet for
Low Voltage Motor Control Centers
(UL 845)
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | September 2020 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
Data Sheet for
Low Voltage Motor Control Centers (UL 845)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
Data Sheet for
Low Voltage Motor Control Centers (UL 845)
Introduction
The purpose of this equipment data sheet is to define buyer specific requirements for the procurement of low voltage motor control center built to UL 845 in accordance with IOGP S-732, for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-732, information requirements specification IOGP S-732L and quality requirements specification IOGP S-732Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Data Sheet
Row | S-732D Data Sheet for Low Voltage Motor Control Centers (UL845) |  |  |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  |  |  |  | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | Conformity assessment system (CAS) level : | Select |  |  |  | Select | A | B | C | D
6 |  | Site conditions
7 | 7.2 a | Ambient air temperature - upper limit : | 40 | °C |  |  | Select | 40 | 45 | 50
8 | 7.2 a | Ambient air temperature - lower limit : | 0 | °C |  |  | Select | 0 | -40 | -30 | -20
9 | 7.2 d | Altitude of installation : | < 1000 | m |  |  | Select | < 1000 | < 2000 | other
10 | 7.2 c | Humidity limit : | 95 | % |  |  | Select | 95 | other
11 | 8.1.2.9 | Seismic : | not required |  |  |  | Select | IBC | CBC | not required | other
12 | 8.1.2 | Location installation : | indoors climate controlled |  |  |  | Select | indoors climate controlled | indoor ventilated | outdoor
13 | 7.3.1, 7.3.2 | Application/operating environment : | onshore |  |  |  | Select | onshore | offshore – fixed | offshore – floating | marine (ship) | other
14 | 8.2.6, 8.2.6.2 | Environmental contamination : | not required |  |  |  | Select | not required | salt-laden | H2S | salt-laden and H2S | other
15 | 1.1.1, 5.1.5, 7.3.1 | Certification (additional) : | not required |  |  |  | Select | not required | USCG/ABS | CSA | other
16 | 8.1.2.8.2, 8.1.2.8.7 | Certification arc resistance : | 3rd party testing |  |  |  | Select | 3rd party testing | self declared
17 |  | Electrical power parameters
18 | 5.1.1 a, 5.1.2 a | Voltage : | 480 | V |  |  | Select | 208 | 480 | 600 | other
19 | 5.1.1 c, 5.1.2 c | Frequency : | 60 | Hz |  |  | Select | 50 | 60 | other
20 | 5.1.1 b, 5.1.2 b | Phase : | 3 phase 3-wire |  |  |  | Select | 3 phase 3-wire | 3-phase 4-wire | 1-phase 2-wire | other
21 | 8.2.12.4 | Grounding system : | Resistance (HRG) |  |  |  | Select | Resistance (HRG) | solid | ungrounded
22 | 5.4.4 | Available fault current (symmetrical) : | Input Data | kA
23 | 5.4.4 | System X/R ratio : | Input Data
24 | Table 1 | System connection : | wye |  |  |  | Select | wye | delta | other
25 |  | MCC structure
26 | 6.2.3, 8.1.2.8.1 | Arc resistant construction : | required |  |  |  | Select | required | not required
27 | 8.1.2.8.3 | Arc plenum : | not required |  |  |  | Select | not required | plenum interior exhaust | plenum exterior exhaust
28 | 6.2.1 b, 8.1.2.1, 8.1.2.3, 8.1.2.4 | NEMA enclosure rating : | Type 1 w/ gasket |  |  |  | Select | Type 1 w/ gasket | Type 12 | Type 3R (non walk-in) | other
29 | 8.1.2.5 | Section depth : | 20 inches |  |  |  | Select | 20 inches | 15 inches | other
30 | 8.2.6 | Paint : | supplier standard |  |  |  | Select | supplier standard | ANSI 61
31 | 8.2.9.10 | Back to back arrangement : | not required |  |  |  | Select | not required | required
32 | 8.2.39.1, 8.2.39.4 d | Space heater : | required |  |  |  | Select | required | not required
33 | 8.2.39.1 c, 8.2.39.2, 8.2.39.4 d | Space heater control : | fixed (constant ON) |  |  |  | Select | N/A | fixed (constant ON) | thermostat | hygrostat
34 | 8.1.2.3, 8.1.2.4 | Outgoing cables : | top |  |  |  | Select | top | bottom
35 |  | Incoming line section
36 | 8.2.34.5, 8.2.34.6 | Cable/bus entry : | top |  |  |  | Select | top | bottom | transition section
37 | 8.2.18.1, 8.2.19.1 | Service entrance : | not required |  |  |  | Select | required | not required
38 | 5.3.1.1, 8.2.34.5, 8.2.34.6 | Incoming line termination : | circuit breaker |  |  |  | Select | circuit breaker | main lugs only | fusible disc | bus connection
39 | 8.2.34.4 | Incoming line metering : | not required |  |  |  | Select | required | not required
40 | 8.2.34.1 | Circuit breaker : | not required |  |  |  | Select | required | not required
41 | 8.2.11.14 | Circuit breaker type : | Select |  |  |  | Select | MCCB | ICCB | PCB | not required
42 | 8.2.34.2 | Protection type : | Select |  |  |  | Select | thermal mag | trip unit-LSI | trip unit-LSIG | trip unit-LI | not required
43 | 8.2.34.3 | Arc reducing maintenance switch : | Select |  |  |  | Select | required | not required | N/A
44 | 8.2.16.2 | Cable : | Select |  |  |  | Select | required | not required
45 | 8.2.34.5, 8.2.34.6 | Cable size : | Input Data | AWG
46 | 8.2.34.5, 8.2.34.6 | Cable material : | Select |  |  |  | Select | copper | aluminum
47 | 8.2.34.5, 8.2.34.6 | Cable - No. conductors per phase : | Select | no. |  |  | Select | not required | 1 | 2 | 3 | 4 | other
48 | 8.2.34.7 | Bus duct : | Select |  |  |  | Select | required | not required
49 | 8.2.34.7 | Bus duct ampacity : | Input Data
50 | 8.2.34.7 | Cable bus : | Select |  |  |  | Select | required | not required
51 | 8.2.34.7 | Cable bus size : | Input Data | AWG
52 | 8.2.34.7 | Cable bus - no. conductors per phase : | Select | no. |  |  | Select | not required | 1 | 2 | 3 | 4 | other
53 | 8.2.30.2 | Main grounding conductor : | required |  |  |  | Select | required | not required
54 | 8.2.30.2, 8.2.33.1.1 | Main grounding conductor - cable size : | Input Data | AWG
55 | 8.2.33.1.1 | Main grounding conductor - cable quantity : | Input Data | no.
56 |  | Wireways
57 | 8.2.28.3.8.1, 8.2.28.3.8.2 | Vertical wireway width : | standard |  |  |  | Select | standard | wide
58 |  | Bus
59 | 5.3.2, 5.1.1 d, 5.1.2 d, 5.3.2.1 | Horizontal bus rating : | Select | A |  |  | Select | 600 | 800 | 1000 | 1200 | 2000 | 2500 | 3000
60 | 5.1.1 e, 5.1.2 e, 5.4.1.1, 5.4.1.2 | Power bus bracing : | 42 | kA |  |  | Select | 22 | 25 | 42 | 50 | 65 | 85 | 100 | 125 | 150 | 200
61 | 5.3.2.2, 8.2.9.1 | Power bus plating material : | tin |  |  |  | Select | tin | silver
62 | 8.2.9.12, 8.2.9.7 | Insulated main horizontal bus : | not required |  |  |  | Select | not required | required
63 | 5.1.1 d | Vertical bus rating : | 600 | A |  |  | Select | 600 | 300 | 800
64 | 5.1.1 d, 8.2.9.3 | Neutral bus rating : | not required |  |  |  | Select | not required | full | half
65 | 8.2.21.1 | Neutral bus load termination point (location) : | Select |  |  |  | Select | all sections | incoming section only | not required
66 | 8.2.33.1.1, 8.2.33.1.3 to 8.2.33.1.6 | Horizontal ground bus (location) : | bottom |  |  |  | Select | bottom | top
67 | 8.2.33.1.1, 8.2.33.1.2 | Horizontal ground bus rating : | 300 | A |  |  | Select | 300 | 600 | Table 24 (UL845)
68 |  | Combination motor starter/contactor unit
69 | 8.2.11.16, 8.2.11.17, 8.2.11.18 | Overload relay type : | micro-processor |  |  |  | Select | micro-processor | solid-state | mechanical | multiple types
70 | 8.2.11.14, 8.2.12.3 | Unit disconnect type : | MCP |  |  |  | Select | MCP | MCCB | fused disconnect
71 | 8.2.11.24 | Control power source : | individual Unit CPT |  |  |  | Select | individual Unit CPT | line voltage | external
72 | 5.2.1, 5.2.2 | Control circuit voltage : | 120 VAC |  |  |  | Select | 120 VAC | 24 VDC
73 | 8.2.11.21, 8.2.11.22, 8.2.11.23 | Control power transformer capacity : | extra capacity |  |  |  | Select | extra capacity | standard capacity
74 | 8.2.41.1 | Status indicator lights : | run-stopped |  |  |  | Select | not required | run-stopped | run-stopped-trip
75 | 8.2.11.31 | Auto trip reset : | not required |  |  |  | Select | not required | required
76 |  | Accessories
77 | 8.2.42.1 | Continuous thermal monitoring : | not required |  |  |  | Select | not required | required
78 | 8.2.42.2 | Condition based monitoring analytical software : | required |  |  |  | Select | required | not required
79 | 8.2.4.8 | Thermal scanning inspection windows : | not required |  |  |  | Select | not required | required
80 | 8.2.10.5 | Absence of voltage tester : | not required |  |  |  | Select | not required | required
81 | 8.2.40.1 | Communication protocol : | not required |  |  |  | Select | not required | Profibus | Modbus TCP | Ethernet/IP | Devicenet | IEC61850 | multiple | other
82 | 8.3.4 | Undervoltage ridethrough : | not required |  |  |  | Select | not required | required
83 | 8.1.2.8.8 | Arc resistant blank unit (# per unit size) : | 1 |  |  |  | Select | not required | 1 | 2 | 3 | other
84 | 8.2.20.1, 8.2.12.4 | Ground fault detection system : | not required |  |  |  | Select | not required | phase detection indicators | indicating meter | pulsing system
85 | 8.2.2.10 | Ventilation filters : | not required |  |  |  | Select | not required | required
86 |  | Shipping and preservation
87 | H.5.2 | Equipment preservation : | supplier standard |  |  |  | Select | supplier standard | special
88 | H.5.2 | Energizing space heaters for temporary storage : | not required |  |  |  | Select | not required | required
89 | H.5.1 | Dessicant bags installed for shipping : | not required |  |  |  | Select | not required | incoming only | each unit
Public Review Draft
Public Review Draft
Note on C5: Select conformity assessment system level of this equipment. This will be used with the Quality Requirements Specification S-732Q.
Note on C7: Select the upper limit ambient air temperature measured outside of the enclosure and the 24h average for 40°C does not exceed 35°C. Default value per UL 845 is 40°C.
Note on C8: Select the lower limit ambient air temperature. Default value per UL 845 is 0°C.
Note on C9: Select the LV MCC installation altitude. UL 485 is based on the altitude not to exceed 2 000 m (6 600 ft), or 1 000 m (3 300 ft) if the equipment includes solid-state controllers. If other is selected, enter the altitude in the 'Additional notes' column.
Note on C10: Select the humidity limit. Per UL 485, default value measured over 24h not to exceed 95%. If other is selected, enter the humidity in the 'Additional notes' column.
Note on C11: Select standard to determine proper seismic ratings. If seismic required, consult with Civil/Structural Engineering staff for details.
Note on C12: Select installation location of the LV MCC.
Note on C13: Select the operating environment for LV MCC. If other is selected, enter the operating environment in the 'Additional notes' column.
Note on C14: Select any contaminant exposure to the LV MCC. If other is selected, enter the contaminant exposure in the 'Additional notes' column.
Note on C15: Select certification requirements (in addition to UL). If other is selected, enter the additional certification in the 'Additional notes' column.
Note on C16: Select the required certification for arc resistance testing.
Note on C18: Reference UL 845, Table 1. If other is selected, enter the voltage in the 'Additional notes' column.
Note on C19: If other is selected, enter the frequency in the 'Additional notes' column.
Note on C20: If other is selected, enter the phase in the 'Additional notes' column.
Note on C21: Select the grounding system of the facility that the LV MCC will be connected to.
Note on C22: Specify the available fault current (symmetrical) of the system at the LV MCC.
Note on C23: Specify the X/R Ratio (system reactance / system resistance). Higher X/R ratio values can impact short circuit.
Note on C24: Select the system connection. If other is selected, enter the system connection in the 'Additional notes' column.
Note on C26: Select if LV MCC requires arc resistant construction.
Note on C27: Select if an arc plenum exhaust is required.
Note on C28: Select the NEMA enclosure rating. If other is selected, enter the system connection in the 'Additional notes' column.
Note on C29: Select the section depth. If other is selected, enter the system connection in the 'Additional notes' column.
Note on C30: Select the paint color
Note on C31: Select if a back to back LV MCC arrangement is required.
Note on C32: Select if section space heaters are required.
Note on C33: If space heaters are required, specify controls type.
Note on C34: Select the location of the outgoing cables.
Note on C36: Select incoming cable entry location.
Note on C37: Select the service entrance requirements.
Note on C38: Select the incoming line termination type.
Note on C41: Applicable only if circuit breaker is selected for incoming line termination. MCCB is the default selection
Note on C42: If circuit breaker required, enter protection type. Thermal mag is default selection for MCCB. LI is default for ICCB and PCB.
Note on C43: Available only with circuit breaker equipped with an integral trip unit.
Note on C44: Not required for bus selection.
Note on C45: If cable required, enter conductor size needed for incoming service.
Note on C46: If cable is selected for incoming line, enter material. Copper is the default selection.
Note on C47: If cable required, enter no of conducters per phase. If other is selected, enter the No of conductors in the 'Additional notes' column. Not required for bus selection.
Note on C48: Not required for cable selection..
Note on C49: if bus duct required, enter ampacity of bus duct
Note on C51: if cable bus required, enter size required.
Note on C52: If cable bus required, enter no of conducters per phase
Note on C54: If main grounding conductor required, enter cable size required
Note on C55: If main grounding conductor required, enter cable quantity required
Note on C57: Consult with supplier data for wide option offering.
Note on C59: Select the main bus rating. For 2500 A and above, arc resistance may not be available.
Note on C60: Select the power bus max fault rating - reference UL 845, Table 2.
Note on C61: Select the bus plating material. If none is selected, the ampacity and temperature rise will be affected.
Note on C62: Select the main bus insulation requirement.
Note on C63: Select the vertical bus rating
Note on C64: Select the neutral bus rating.
Note on C65: Select the neutral bus load connection location.This is for load neutral connection points.
Note on C66: Select the ground bus location.
Note on C67: Select the horizontal ground bus rating for values different than 300 A and 600 A, see Table 24 and 25 of UL 845.
Note on C69: Select the overload relay type. For multiple types, use the "supplement" tab or project drawings to provide additional information.
Note on C70: Select the unit disconnect type.
Note on C71: Select the control power source.
Note on C72: Select the control power voltage.
Note on C73: Select the CPT capacity. If extra capacity is selected, 50VA additional capacity is included in the sizing as per the supplementary specification.
Note on C74: Select the indicator lights requirements.
Note on C75: Select the requirement for auto-trip-reset capability.
Note on C78: Select CBM software requirement. This does not include computer hardware.
Note on C79: Select the requirement for thermal scanning inspection windows. Supplier to indicate recommended location.
Note on C80: Select the requirement for absence of voltage tester.
Note on C81: Select the communication protocol. If multiple is selected, indicate details on the project drawings. If other is selected, enter details in the "Additional note" column.
Note on C82: Select the requirements for undervoltage ridethrough. Supplier to recommend voltage and time parameters.
Note on C83: Select the number of blanks per unit size. If other is selected, use the "Additional notes" column for details.
Note on C84: Select the ground fault detection system type.
Note on C85: Select the requirement for ventilation filters.
Note on C87: Select the equipment preservation requirement. If special is selected, use "Additional note" column or "Supplement" tab for additional details.
Note on C88: Select the requirement for energizing space heater for temporary storage.
Note on C89: Select the requirements for decacent bags for shipping.

## Supplement
Row |  | S-732D Data Sheet for Low Voltage Motor Control Centers (UL 845) | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
Public Review Draft

## Guidance
Data Sheet for
Low Voltage Motor Control Centers (UL 845)
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-732 Supplementary Specification to UL 845 Low Voltage Motor Control Centers.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.
Public Review Draft

## Backcover
Public Review Draft