## Front & Preliminaries
|  |  |  | SPECIFICATION | September
|  |  |  | S714L | 2020
Information Requirements for
Diesel Generator Package
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | September 2020 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-714L Information Requirements for
Diesel Generator Package
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
S-714L Information Requirements for
Diesel Generator Package
Introduction
The purpose of this information requirements specification (IRS) is to define Information requirements for the procurement of diesel generator package, in accordance with IOGP S-714 for application in the petroleum and natural gas industries. This document defines the information requirements, including format, timing and purpose, for information to be provided by the manufacturer. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the supplementary requirements specification IOGP S-714, quality requirements specification IOGP S-714Q and equipment data sheet IOGP S-714D which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Supplier Instructions
S-714L Information Requirements for
Diesel Generator Package
Supplier Instructions
In response to Invitation To Tender (ITT)
Tenderers to submit information as defined in column E - 'Submit At Proposal' in 'Requirements' sheet, in accordance with ITT instructions
On award of contract
Specified Information requirements shall be submitted in accordance with contract information submission instructions. Suppliers to prepare and submit 'Supplier Master Information Schedule' (SMIS) incorporating information requirements in accordance with columns F - 'First Issue Post Purchase Order' in 'Requirements' sheet. Supplier to demonstrate compliance with each information requirement either by providing document number cross reference to the Requirement in 'Supplier Master Information Schedule' (SMIS) and, if specified in the Contract, using column J 'Fulfilled by Document Number(s)' in the IRS Requirements Sheet.
On completion of scope
Supplier to validate that the information delivered meets the IRS requirements either through cross reference to the deliverable type in a as-built version of the 'Supplier Master Information Schedule' SMIS and, if specified in the Contract, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in Requirement sheet populated with the specific document numbers issued to the Purchaser.
IRS Structure Contents
1 |  | 'Front & Preliminaries' Tab
The 'Front & Preliminaries ' tab includes an IOGP Front sheet for the IRS followed by Acknowledgements, a Disclaimer, Copyright Notice, Foreword and Introduction
2 |  | 'Supplier Instructions' Tab
This 'Supplier Instructions' tab provides instructions that Suppliers are to follow in response to this IRS.
3 |  | 'Requirements' Tab
The 'Requirements' tab lists the suite of information requirements that are to be supplied during tendering and following award of the purchase order to deliver the purchase order scope. The information requirements are grouped under three broad categories; Management information requirements: Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. Technical information requirements: Technical information developed by the supplier or their sub suppliers, during the design and development, acquisition, manufacture, assembly and testing of the contracted scope. Purchase Order Specific Information Requirements: Information requirements specified by individual owners-operators in addition to those specified by IOGP-JIP33 to meet specific operational, project or legislative requirements. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. "The 'Requirements' tab includes columns A to L, including Column A for the relevant requirement code and Column B for the Requirement for the different Information Requirements (Data, Documents and/or Models) to be provided by suppliers, based on the parent standard, IOGP Specification or the specified parent industry Standard. Condition Invoking Revoking Requirement Column C is included to allow any specific conditions to be identified that may require a additional deliverable(s). Typical Deliverable Column D is provided for Purchaser to identify the deliverable type that the information would typically appear within; this also allows the Purchaser's Requisitioning Engineers to group the various Information Requirements by Deliverable Type. Column E includes Submission Requirements (Yes or No) at Proposal, while columns F, G & H identify Issue Purpose (For Information or For Acceptance) and Durations (Period or Weeks/Months) for First Issue of the particular deliverable Post Purchase Order. Required As Built, Fulfilled by Document Number(s), Translation Required and Remarks columns I, J, K & L are also included. Definitions for each column are contained in the rows above the columns: Abbreviations used for various submission requirements in Column H are shown in table 3.1 below:
Table 3.1 - Information Submission Abbreviations
4 |  | 'Definitions' Tab
The 'Definitions' tab includes several columns A to F, including Column A for the relevant Code & Column B for the Requirement for the different Information (Data, Documents and/or Models) Requirements to be provided by Suppliers, all copied from the 'Requirements' tab. Column C includes a full description of the Information Requirement based on the Parent Standard, IOGP Specification or an Industry Standard. Column D gives a reference to the Parent Standard, IOGP Specification or an Industry Standard that the Information requirement is identified in. Column E identifies the Requirement format as listed in Table 9.1 below. Column F relates the CFIHOS discipline document type that could be used to classify the document having this IRS content. Definitions for each column are contained in the rows above the columns:
5 |  | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various tabs of this workbook.
Buyer |  |  | Organisation placing a Contract or Purchase Order with Supplier for equipment or services on project; may be alternatively referred to as 'User' or 'Purchaser'
CFIHOS |  |  | Capital Facilities Information Hand Over Specification
Company |  |  | Project Operating Entity or the organisation Contractor is under contract to
Contractor |  |  | Project Contractor responsible for procuring equipment.
Information |  |  | Data, Documents and/or Models
IRS |  |  | Information Requirements Specification
PO |  |  | Purchase Order
QRS |  |  | Quality Requirements Specification
SMIS |  |  | Supplier Master Information Schedule
Supplier |  |  | Organisation supplying equipment or services to Company and/or Contractor on project; may alternatively be referred to as "Vendor", "Seller" or “Manufacturer”.
6 |  | CFIHOS
The Information Requirements are also classified according to document classification published in v1.4 of Capital Facilities Information Hand Over Specification (CFIHOS). The objective of CFIHOS is to create a common information standards across the process industries. Further information on CFIHOS can be found at:
https://uspi.nl/index.php/projects/frameworks-methodologies/136-cfihos
7 |  | Document Metadata
Typical Metadata for Information Deliverables to be provided by Suppliers is shown in Table 7.1 below
Table 7.1 - Supplier Deliverable Metadata
8 |  | Deliverable Formats
The format of the relevant Information Deliverable to be submitted by Supplier for Buyer/Contractor is to be as described in table 8.1 below. Where required to be ‘As Built’, deliverables are to be updated and handed over in the native format.
Table 8.1 – Deliverable Formats
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Requirements
S-714L Information Requirements for Diesel Generator Package
Requirements
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement based on the description in the Parent Standard, IOGP Specification or an Industry Standard Information Requirement Title.
C | Condition Invoking Requirement - describes special condition(s) under which the Information Requirement is required; e.g.. service offshore and weight greater than 1 tonne means information is required. NB: if blank, always required
D | Typical Deliverable - Purchaser to advise the short description of the Information Deliverable that would typically include this Information Requirement
E | Submit With Proposal - Yes or No, where 'Yes' means the Information Requirement is required to be submitted with Suppliers Proposal or 'No' is not required
F, G & H | First Issue Post Purchase Order - issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the Information Requirement and Period defined after Purchase Order placement.
I | Required As Built - Yes or No, where 'Yes' means the Information Requirement is required to be 'As Built' on completion or delivery of equipment or 'No' is not required 'As Built'
J | Fulfilled by Information Deliverable Number(s) - identifies which Information Requirement(s) listed in the Supplier Master Information Schedule (SMIS) addresses the Purchasers requirements. NB; it should be noted that one Information Deliverable can fulfil more than one Information Requirement.
K | Translation Required -Yes or No, where 'Yes' means the Information Requirement should be translated into a language(s) (to be advised) other than English and 'No' means to be provided in English
L | Remarks - may include bid clarification questions & decisions (specify author & date)
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S714-IR-113 | Supplier master information schedule |  | Information Deliverables List | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-2 | Delivery schedule |  | Delivery/Production Schedule | Yes | For Information |  | WAO | No |  | No
S714-IR-3 | Progress report |  | Progress Report | No | For Information |  | WAO (Monthly) | No |  | No
S714-IR-4 | Quality plan |  | Quality Plan | Yes | For Information |  | WAO | No |  | No
S714-IR-5 | Sub-supplier list | Required for CAS A, B and C | Sub-Supplier List | - | - |  | - | - |  | -
S714-IR-6 | Inspection and test plan for complete package |  | Inspection and Test Plan (ITP) | Yes | For Acceptance |  | WAO | No |  | No
S714-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No |  | No
S714-IR-8 | Non-conformance records |  | Nonconformance History | No | For Acceptance |  | WAO | No |  | No
S714-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | WAO | No |  | No
Technical Information Deliverables
Analysis
S714-IR-126 | Failure Mode Effects Analysis (FMEA) |  | Failure Mode Effects Analysis (FMEA) | No | For Information |  | WAO | Yes |  | No
S714-IR-28 | Lateral Critical Speed Analysis |  | Lateral Critical Speed Analysis | No | For Information |  | WAO | Yes |  | No
S714-IR-29 | Torsional Critical Speed Analysis |  | Torsional Critical Speed Analysis | No | For Information |  | WAO | Yes |  | No
Performance Curves & Calculations
S714-IR-216 | Air Release / Relief Valve Calculation |  | Air Release / Relief Valve Calculation | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-30 | Engine Performance Curves |  | Engine Performance Curves | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-33 | Battery charge and discharge curve |  | Motor Performance & Electrical Data And Curves | No | For Information |  | WAO | No |  | No
S714-IR-34 | Battery sizing calculation |  | Design Calculation | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-159 | Generator Performance Curves |  | Motor Performance & Electrical Data And Curves | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-98 | HVAC Calculation |  | HVAC Calculation | No | For Information |  | WAO | Yes |  | No
S714-IR-99 | Diesel engine site rating calculation |  | Design Calculation | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-137 | Structural Design Report |  | Structural Design Report | No | For Acceptance |  | WAO | Yes |  | Yes
S714-IR-150 | Lighting level calculation |  | Design Calculation | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-200 | Instrument Calculations |  | Instrument Calculations | No | For Information |  | WAO | Yes |  | No
S714-IR-203 | Generator performance and protection relay calculations |  | Curves And Tables Calculations | Yes | For Acceptance |  | WAO | Yes |  | No
Certificates
S714-IR-214 | Declaration Of Conformity |  | Declaration Of Conformity | No | For Information |  | WAO | Yes |  | No
S714-IR-215 | Fire test certificate / approval report |  | Fire Test Certificate | No | For Information |  | WAO | No |  | No | To give evidence that the solution is fit for purpose. By a listed product (certificate and / or a approval report) or by fire scenario engineered solution.
S714-IR-108 | Hazardous Area Certificate (Type) |  | Hazardous Area Certificate (Type) | No | For Information |  | WAO | No |  | No
S714-IR-110 | Lifting Equipment Test Certificate |  | Lifting Equipment Test Certificate | No | For Information |  | WAT | Yes |  | No
S714-IR-141 | Welder Qualification Certificate | Required for CAS A and B only | Welder Qualification Certificate | - | - |  | - | - |  | -
S714-IR-145 | Materials Inspection Certificate (3.1) |  | Materials Inspection Certificate (3.1) | No | For Information |  | WAO | Yes |  | No
S714-IR-181 | Safety Integrity Level (SIL) Certificate |  | Safety Integrity Level (SIL) Certificate | No | For Information |  | WAO | Yes |  | No
S714-IR-194 | Materials Test Report (2.2) |  | Materials Test Report (2.2) | No | For Information |  | WAT | Yes |  | No
S714-IR-209 | Insulation material certificate |  | General Certificate | No | For Information |  | WAT | No |  | No
S714-IR-224 | Laboratory accreditation certificate |  | Laboratory accreditation certificate | No | For Information |  | WPTF | No |  | No
S714-IR-213 | Certificate Of Conformance - third party |  | Certificate Of Conformance | No | For Information |  | WAO | Yes |  | No
S714-IR-242 | Weight Certificate |  | Weight Certificate | No | For Acceptance |  | WAO | Yes |  | No
Data
S714-IR-80 | Diesel generator data sheet |  | Manufacturer Datasheet | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-81 | Noise Datasheet |  | Noise data sheet | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-97 | Material Safety Datasheet |  | Material Safety Datasheet | No | For Information |  | WAO | Yes |  | Yes
S714-IR-103 | Electric motor data sheet |  | Manufacturer Datasheet | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-105 | Generator datasheet |  | Manufacturer Datasheet | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-114 | Generator control panel datasheet |  | Manufacturer Datasheet | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-153 | Manufacturer product datasheet |  | Manufacturer Datasheet | No | For Information |  | WAO | No |  | No
S714-IR-185 | Instrument datasheet |  | Manufacturer Datasheet | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-192 | Diesel engine datasheet |  | Manufacturer Datasheet | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-204 | Electrical protection relay datasheet |  | Manufacturer Datasheet | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-235 | Air Release Valve Data Sheet |  | Air Release Valve Data Sheet. | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-243 | Weight Datasheet |  | Weight Datasheet | Yes | For Acceptance |  | WAO | Yes |  | No
Drawings & Diagrams
S714-IR-218 | Heat Tracing Diagram |  | Heat Tracing Diagram | No | For Information |  | WAO | Yes |  | No
S714-IR-212 | Detailed Drawing - Control Panel |  | Detailed Drawing | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-222 | HVAC Flow Diagram |  | HVAC Flow Diagram | No | For Information |  | WAO | Yes |  | No
S714-IR-223 | Layout Diagram - Lighting |  | Layout Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-237 | General Diagram - Transportation |  | General Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-238 | Lifting, Hoisting, And Rigging Plan / Drawing |  | Lifting, Hoisting, And Rigging Plan | No | For Information |  | WAO | Yes |  | No
S714-IR-23 | Piping And Instrumentation Diagram - Diesel Generator Package |  | Piping And Instrumentation Diagram | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-25 | Wiring Diagram |  | Wiring Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-79 | Schematic drawing |  | Schematic Diagram | No | For Information |  | WAO | Yes |  | No
S714-IR-116 | General arrangement drawing - Control panels |  | General Arrangement Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-117 | General arrangement drawing - Electrical |  | General Arrangement Diagram | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-118 | General arrangement drawing - Diesel Generator package |  | General Arrangement Diagram | Yes | For Information |  | WAO | Yes |  | No
S714-IR-133 | Acoustic enclosure drawing |  | General Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-134 | Name Plate Drawing |  | Name Plate Drawing | No | For Acceptance |  | WAO | Yes |  | Yes
S714-IR-138 | Foundation Loading Diagram |  | Foundation Loading Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-139 | Detailed Drawing - Baseplate |  | Detailed Drawing | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-156 | Earthing Diagram |  | Earthing Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-162 | System Topology Diagram |  | System Topology Diagram | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-164 | Layout Drawing - Instruments, Junction boxes, cable trays, MCT and earthing |  | Layout Drawing | No | For Information |  | WAO | Yes |  | No
S714-IR-166 | Termination Diagram |  | Termination Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-175 | Loop Diagram |  | Loop Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-182 | Hook Up Diagram |  | Hook Up Diagram | No | For Information |  | WAO | Yes |  | No
S714-IR-183 | Human Machine Interface (HMI) Graphics |  | Human Machine Interface (HMI) Graphics | No | For Information |  | WAO | Yes |  | No
S714-IR-199 | Logic Diagram |  | Logic Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-201 | Cause And Effect Diagram |  | Cause And Effect Diagram | No | For Information |  | WAO | Yes |  | No
S714-IR-205 | General arrangement drawing - Instruments and valves |  | General Arrangement Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-206 | Equipment Cross Section Diagram |  | Equipment Cross Section Diagram | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-219 | General Arrangement Drawing - Enclosure |  | General Arrangement Diagram | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-220 | Detailed Drawing - Enclosure penetrations and access panels |  | Detailed Drawing | No | For Acceptance |  | WAO | Yes |  | No
Lists
S714-IR-82 | Spare Part List |  | Spare Part List | Yes | For Acceptance |  | WAO | No |  | Yes
S714-IR-85 | Bill Of Materials |  | Bill Of Materials | No | For Information |  | WAO | Yes |  | No
S714-IR-87 | Utility Consumption List |  | Utility Consumption List | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-88 | Instrument List |  | Instrument List | No | For Information |  | WAO | Yes |  | No
S714-IR-89 | Lubrication List |  | Lubrication List | No | For Acceptance |  | WAO | Yes |  | Yes
S714-IR-90 | Alarm, Trip Setting List |  | Alarm, Trip Setting List | No | For Information |  | WAO | Yes |  | No
S714-IR-140 | Special Tools List |  | Special Tools List | Yes | For Information |  | WAO | Yes |  | Yes
S714-IR-172 | Communication Signals List |  | Communication Signals List | Yes | For Acceptance |  | WAO | Yes |  | No
S714-IR-184 | Cable List |  | Cable List | No | For Information |  | WAO | Yes |  | No
S714-IR-236 | Manual Valve List |  | Manual Valve List | No | For Information |  | WAO | Yes |  | No
S714-IR-241 | Tag/Equipment Register |  | Tag/Equipment Register | No | For Acceptance |  | WAO | Yes |  | Yes
Manuals and MRB
S714-IR-91 | Installation Manual |  | Installation Manual | No | For Acceptance |  | WPTD | Yes |  | Yes | Installation Manual index, if required, shall be provided in first revision of the document. When index agreed, Installation manual content shall be provided in subsequent revision of the document.
S714-IR-92 | Maintenance Manual |  | Maintenance Manual | No | For Acceptance |  | WAO | Yes |  | Yes | Maintenance Manual index, if required, shall be provided in first revision of the document. When index agreed, Maintenance manual content shall be provided in subsequent revision of the document. Recommended schedules for major and minor overhauls shall be provided at proposal stage to include list of required spare parts, estimate of required time and manpower.
S714-IR-93 | Operating Manual |  | Operating Manual | No | For Acceptance |  | WAO | Yes |  | Yes | Operating Manual index, if required, shall be provided in first revision of the document. When index agreed, Operating manual content shall be provided in subsequent revision of the document.
S714-IR-94 | Manufacturer Record Book (MRB) |  | Manufacturer Record Book (MRB) | No | For Acceptance |  | WAD | Yes |  | No | Manufacturer Record Book index, if required, shall be provided in first revision of the document. When index agreed, Manufacturer Record Book content shall be provided in subsequent revision of the document.
Philosophy
S714-IR-167 | Functional Design Specification |  | Functional Design Specification | No | For Acceptance |  | WAO | Yes |  | No
Procedures
S714-IR-44 | Non Destructive Test Procedure | Required for CAS A | Non Destructive Test Procedure | - | - |  | - | - |  | -
S714-IR-45 | Functional test procedure |  | Functional test procedure | No | For Information |  | WAO | No |  | No
S714-IR-46 | Factory acceptance test procedure |  | Factory Acceptance Test (FAT) Procedure | No | For Information |  | WAO | No |  | No
S714-IR-68 | Painting And Coating Procedure |  | Painting And Coating Procedure | No | For Information |  | WAO | Yes |  | No
S714-IR-71 | Welding Procedure Qualification Record |  | Welding Procedure Qualification Record | No | For Acceptance |  | WPTF | No |  | No
S714-IR-72 | Welding Repair Procedure |  | Welding Repair Procedure | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-73 | Pressure Test Procedure |  | Pressure Test Procedure | No | For Acceptance |  | WAO | No |  | No
S714-IR-96 | Commissioning Instruction |  | Commissioning Instruction | No | For Acceptance |  | WAO | Yes |  | Yes
S714-IR-130 | Mechanical Test Procedure |  | Mechanical Test Procedure | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-144 | Painting And Coating System Qualification |  | Painting And Coating System Qualification | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-146 | Insulation Procedure |  | Pickling and passivation Procedure | No | For Acceptance |  | WAO | No |  | No
S714-IR-169 | Lifting and Installation Procedure |  | Lifting Procedure | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-171 | Cyber Security Documentation |  | Cyber Security Documentation | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-173 | Safety And Automation System (SAS) Communication Interface Test Procedure (UFAT) |  | Facility Control System Communication Interface Test Procedure | No | For Information |  | WAO | No |  | No
S714-IR-187 | Obsolescence management plan |  | Obsolescence management plan | Yes | For Information |  | WPTD | No |  | No
S714-IR-195 | Material handling procedure |  | Lifting Procedure | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-230 | Welding Procedure Specification |  | Welding Procedure Specification | No | For Acceptance |  | WPTF | No |  | No
S714-IR-239 | Routine test procedure | Required only where tests in addition to those stated in IEC 60034-1 Table 16 have been specified by the purchaser in the data sheet | Test procedure | - | - |  | - | - |  | -
S714-IR-244 | Weighing Test Procedure |  | Weighing Test Procedure | No | For Acceptance |  | WAO | No |  | No
Records
S714-IR-100 | Noise Test Records |  | Noise Test Records | No | For Acceptance |  | WAT | Yes |  | No
S714-IR-109 | Hazardous Area Installation Records |  | Hazardous Area Installation Records | No | For Acceptance |  | WAT | Yes |  | No
S714-IR-119 | Factory Acceptance Test (FAT) Records |  | Factory Acceptance Test (FAT) Records | No | For Acceptance |  | WAT | Yes |  | No
S714-IR-121 | Non-Destructive Examination (NDE) Report |  | Non-Destructive Examination (NDE) Report | No | For Acceptance |  | WAT | Yes |  | No
S714-IR-143 | Painting And Coating Inspection Records |  | Painting And Coating Inspection Records | No | For Information |  | WAT | Yes |  | No
S714-IR-210 | Production parameter monitoring record |  | Production parameter monitoring record | No | For Information |  | WPTD | No |  | No
S714-IR-231 | Welding Traceability Records |  | Welding Traceability Records | No | For Acceptance |  | WPTF | Yes |  | No
S714-IR-225 | Non Destructive Examination (NDE) Personnel Qualification | Required for CAS A and B only | Non Destructive Examination (NDE) Personnel Qualification | - | - |  | - | - |  | -
S714-IR-227 | Welding Coordinator Qualification | Required for CAS A and B only | Welding Coordinator Qualification | - | - |  | - | - |  | -
S714-IR-228 | Welding Inspector Qualification | Required for CAS A and B only | Welding Inspector Qualification | - | - |  | - | - |  | -
S714-IR-245 | Positive Material Identification (PMI) Records | CAS A only | Positive Material Identification (PMI) Records | - | - |  | - | - |  | -
Reports
S714-IR-107 | Emissions Report |  | Emissions Report | No | For Information |  | WAT | Yes |  | No
S714-IR-120 | Pressure Test Report |  | Pressure Test Report | No | For Information |  | WAT | Yes |  | No
S714-IR-124 | Hazard Operability Input to HAZOP Report |  | Hazard Operability Report | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-158 | Type test report |  | Type Test Report | No | For Information |  | WAO | No |  | No
S714-IR-189 | Vibration Report |  | Vibration Report | No | For Acceptance |  | WAT | Yes |  | No
S714-IR-208 | Routine test report |  | Type Test Report | No | For Acceptance |  | WAT | No |  | No
S714-IR-240 | Motor Performance Test Report |  | Test Report | No | For Acceptance |  | WAT | Yes |  | No
S714-IR-35 | Safety Analysis Input To Safety Analysis Report |  | Safety Analyse Input To Safety Analysis Report | No | For Acceptance |  | WAO | Yes |  | No
S714-IR-246 | Dimensional Report |  | Dimensional Report | No | For Information |  | WAD | Yes |  | No
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Definitions
S-714L Information Requirements for Diesel Generator Package
Definitions
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement that would typically provide the Information required, based on the description in the Parent Standard, IOGP Specification or an Industry Standard Title.
C | Description - an excerpt from the Parent Standard, IOGP Specification or Industry Standard.
D | Reference - reference to the Parent Standard, IOGP Specification or Industry Standard that the Information Deliverable is identified in.
E | Format - defines the required format of the relevant Information Requirement to be submitted by Supplier for Purchaser/Contractor for information and acceptance as shown in Table 9.1 of Instructions Tab and selected from pick list.
F | CFIHOS Discipline Document Type Code - the CFIHOS discipline document type that could be used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Deliverables
S714-IR-113 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | PDF | CFIHOS-70000099
S714-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by [vendor/sub-vendors]. Schedule details typically** include; a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [vendor's] standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S714-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S714-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] |  | PDF
S714-IR-5 | Sub-supplier list | Definition of processes, products or services that will be externally provided and the controls to be applied by the DG package supplier to ensure conformance with agreed requirements. The list includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . Note: ISO 9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. |  | PDF
S714-IR-6 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. This should include the sub-supplier equipment ITP. | 5.7.3.1.4 | PDF | CFIHOS-70000180
S714-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. | 6.4.4.1, 6.4.4.2, 6.4.4.3, 6.4.5.1 | PDF | CFIHOS-70000154
S714-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S714-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000389
Technical Information Deliverables
Analysis
S714-IR-126 | Failure Mode Effects Analysis (FMEA) | an analytical procedure in which each potential failure mode in every component of a product is analysed to determine its effect on the reliability of that component and, by itself or in combination with other possible failure modes, on the reliability of the product or system and on the required function of the component; or the examination of a product (at the system and/or lower levels) for all ways that a failure may occur. For each potential failure, an estimate is made of its effect on the total system and of its impact. In addition, a review is undertaken of the action planned to minimize the probability of failure and to minimize its effects | 6.1.2.1, 6.5.2 | PDF
S714-IR-28 | Lateral Critical Speed Analysis | Lateral critical speed analysis report, including but not limited to the following: a. Complete description of the method used. b. Graphic display of critical speeds versus operating speed (speed vs phase & response amplitude showing Amplification Factor at x/y vibration probe location for each damped unbalance critical speed- Bode plot). c. Graphic display of bearing and support stiffness and its effect on critical speeds(Undamped critical speed-support stiffness map for bull gear rotor & both high speed pinion rotors). d. Graphic display of rotor response to unbalance (including damping) (deflected rotor shape showing the major-axis amplitude at key locations - radial bearing, shaft seal, oil seal to demonstrate amplitude well within diametral running clearance). e. Journal static loads. f. Stiffness and damping coefficients for min and max clearance (max and min pre-loads). g. Tilting-pad bearing geometry and configuration | 4.1.2.2 | PDF
S714-IR-29 | Torsional Critical Speed Analysis | Torsional critical speed analysis report, including but not limited to the following: a. Complete description of the method used. b. Graphic display of the mass elastic model. c. Tabulation identifying the mass moment and torsional stiffness of each component identified in the mass elastic system. d. Graphic display of exciting frequencies versus speed and natural torsional frequency (Campbell Diagram). e. Graphic display of torsional critical speeds and deflection angle for torsional vibration (mode-shape plot). f. Effects of alternative coupling on analysis. | 4.1.2.2 | PDF
Performance Curves & Calculations
S714-IR-216 | Air Release / Relief Valve Calculation | Air Release / Relief Valve calculation. The output is documented in the Process Safeguarding Memorandum. | 5.8.2.7 | PDF | CFIHOS-70000313
S714-IR-30 | Engine Performance Curves | Curves to indicate power developed at output shaft, fuel consumption, emissions over the operating range and ambient temperatures, with specified inlet and exhaust pressure loss and varying speeds. Guarantee points shall be clearly identified. [Torque, Power & Specific Fuel Consumption vs.Speed @ min, max, ISO ambient temperature, @site elevation, @reference fuel composition.] | 5.1.1 | PDF
S714-IR-33 | Battery charge and discharge curve | Curves showing discharge voltage per cell against percentage capacity, for different charging rate | 5.7.10.1 | PDF
S714-IR-34 | Battery sizing calculation | Basis for battery rated/ specified current based on base cranking current and applying correction factor for ambient temperature, cranking time, starter motor efficiency, cell voltage etc. | 5.7.10.4 | PDF
S714-IR-159 | Generator Performance Curves | Curves to indicate torque and current against speed for 80% and 100% voltage conditions and at rated frequency, superimposed on driven equipment torque curve to confirm that there is adequate net torque for acceleration. The following performance curves are required for both 80% and 100% voltage: - motor speed 'v' torque - motor speed 'v' Power factor - motor speed 'v' current - driver equipment torque 'v' speed for all start up conditions - Generator performance and capability charts | 5.7.8.5 | PDF
S714-IR-98 | HVAC Calculation | This document contains the HVAC calculation by the supplier based on the heat load produced by the diesel engine and ambient. As per NORSOK H-003. | 5.1.5.3, 5.3.6.1 | PDF
S714-IR-99 | Diesel engine site rating calculation | Diesel engine site rating calculation will be made according to Section 7 of ISO 15550. Mandatory content of information: – Calculation methods used; – Input data; – Results; – Analysis of the results. Optional content of information: – Case studies; – Verification of different technical solutions. Calculation will also demonstrate that engine site rating provides 10% margin over the DG power specified. | 5.1.1 | PDF | CFIHOS-70000086
S714-IR-137 | Structural Design Report | Structural design report detailing the following shall be provided if stated in the data sheet: - Input data - Assumptions made - Load cases and load combinations analysed - Accidental design calculations - Factor of safety achieved - Documentation of lifting equipment where applicable | 5.6.1.1, 5.6.1.1, 5.6.2.1, 5.6.2.2, 5.6.2.3, 5.6.2.4, 5.6.2.5, 5.6.3.1, 5.6.3.2, 5.6.3.3, 5.6.3.4, 5.6.3.5, 5.6.3.6, 5.6.3.7, 5.6.3.8, 5.6.3.9, 5.6.4.1.1 , 5.6.7.1.2, 5.6.7.2.1 | PDF
S714-IR-150 | Lighting level calculation | Document providing calculation of lighting level at DG package floor complying to the requirement specified. Calculation will consist of information about data, basic conditions and assumptions used for selection of appropriate system solutions, parts or material, as well as the way these data have been processed and evaluated Mandatory content of information: – Calculation methods used; – Input data; – Results; – Analysis of the results. Optional content of information: – Case studies; – Verification of different technical solutions. | 5.3.8.1, 5.3.8.2, 5.7.4.1, 5.7.4.2 | PDF | CFIHOS-70000086
S714-IR-200 | Instrument Calculations | This document shall support verification of component function according to company/project requirements. Shall include control valves and flow instruments. Information to be used into system engineering Characteristics and functional parameters shall be documented and performance shall be shown to be probable. This shall include but not be limited to calculations, curves, tables, reference to similar applications and test data. This shall as a minimum be at a level customary for the equipment and to the extent such data are of importance for interfaces to plant and system. | 5.8.2.3.14, 5.8.2.4.1, 5.8.2.4.2, 5.8.2.4.3, 5.8.2.4.4 | PDF
S714-IR-203 | Generator performance and protection relay calculations | Describe the main characteristic and limits of a product such as protection relays, Transformers. Information to be used into system engineering Characteristics and functional parameters should be documented and performance shall be shown to be probable. This should include but not be limited to calculations, curves, tables, reference to similar applications and test data. This shall as a minimum be at a level customary for the equipment and to the extent such data are of importance for interfaces to plant and system. Calculations related generator performance and protection relay set points, etc. will be provided. Following list some of these calculations: - Generator performance calculations for the transient response (largest step load/largest motor starting/load rejection); - Generator protection relay setting calculations and curves. | 5.7.8.5 | PDF
Certificates
S714-IR-214 | Declaration Of Conformity | Declaration that contains sufficient information to enable an recipient of the declaration of conformity to identify the issuer of the declaration, the object of the declaration, the standards and other specified requirements with which conformity is declared, and the person signing for and on behalf of the issuer of the declaration of conformity (first party). Mandatory content of information: Please refer to ISO/IEC 17000, clause 5.5 and ISO/IEC 17050-1:2004. | 5.5.1.1, 5.5.6.2, 5.5.6.3, 5.5.6.4, 5.5.7.1, 5.9.3.1.4, 5.9.3.3.1, 5.9.3.3.2, 5.9.3.3.3, 5.9.3.3.4, 5.9.4.1, 5.9.7.3 | PDF
S714-IR-215 | Fire test certificate / approval report | Fire test certificate / approval report that forms part of the listing, or the fire scenario engineered solution. | 5.9.3.1.5, 5.9.3.1.7, 5.9.3.1.8, 5.9.3.1.9 | PDF
S714-IR-108 | Hazardous Area Certificate (Type) | Attestation issued by a recognised independent authority certifying that a type test has satisfied the specified standards; e.g. ATEX, BASEEFA, PTB, UL, CSA, NEMA, EX, etc. Examples of ratings include Intrinsically Safe & Explosion Proof. To include any special requirements for safe use, barrier/isolator to be used, etc. | 5.7.4.2, 5.8.2.1.4, 5.8.2.1.5, 5.9.1, 5.9.7.3 | PDF | CFIHOS-70000160
S714-IR-110 | Lifting Equipment Test Certificate | Certificate to prove that the item can be used as lifting gear in accordance with an applicable standard. This will include slings, shackles, lifting frames, lifting instructions etc. To confirm that the equipment can be safely used for lifting and handling for the applicable load stated. All lifting equipment shall be certified by a Competent Enterprise approved by local authorities and approved by Company. The certification shall be documented with an ILO certificate form No 2 or No.3 or similar form according to ILO convention 152. | 5.6.7.1.1, 5.6.7.2.1 | PDF
S714-IR-141 | Welder Qualification Certificate | Certification demonstrating that a welder is qualified to perform work to welding procedure specification(s). | 5.4.2.1, 5.4.2.2.3.1, 5.4.2.2.3.2 | PDF | CFIHOS-70000413
S714-IR-145 | Materials Inspection Certificate (3.1) | A document with test results based on specific inspection and testing, issued by the Manufacturer and validated by the Manufacturer's authorised inspection representative independent of the manufacturing department. NOTE: see ISO/IEC 17000, clause 5.5 and ISO 10474 / EN 10204. | 5.4.1, 5.8.2.1.17, 5.8.2.1.18, 5.8.3.10, 5.8.3.11, 5.8.3.2 | PDF | CFIHOS-70000412
S714-IR-181 | Safety Integrity Level (SIL) Certificate | This document shall verify the level of SIL. This document shall provide input to Safety Analysis Report. This document shall include necessary performance data according to authority regulations. | 5.8.2.1.14 | PDF
S714-IR-194 | Materials Test Report (2.2) | A document in which the supplier declares that the products supplied are in compliance with the requirements of the PO, and in which test results are supplied based on non-specific inspection and testing NOTE: see ISO/IEC 17000, clause 5.5 and ISO 10474 / EN 10204. | 5.1.5.2, 5.4.1 | PDF | CFIHOS-70000412
S714-IR-209 | Insulation material certificate | A document certifying compliance with specified requirements of the insulation material. | 5.4.4.1.1 | PDF | CFIHOS-70000239
S714-IR-224 | Laboratory accreditation certificate | Certificate issued by a certification body. Certificate and schedule to be included. | 5.4.2.2.6 | PDF
S714-IR-213 | Certificate Of Conformance - third party | A statement of conformity where attestation is performed by the person or body that is independent of the person or organization that provides the object, and of user interests in that object (third party). Includes ingress protection certificates for instruments. CE Marking, UL/FM Type Tests, ATEX etc. | 5.6.7.2.3, 5.6.7.3.1, 5.6.7.3.3, 5.7.1.1, 5.7.3.1, 5.7.6.1, 5.7.6.2, 5.9.11, 5.9.2.1, 5.9.3.1.10, 5.9.3.1.6, 5.9.3.2.1, 5.9.3.2.2, 5.9.3.2.3, 5.9.3.2.4, 5.9.3.2.5, 5.9.3.2.7, 5.9.4.2, 5.9.8.4, 6.2.3.2.1.1, 6.2.3.2.1.3, 6.2.3.2.2.2, Figure 7, Table 7 | PDF | CFIHOS-70000013
S714-IR-242 | Weight Certificate | independent certification of correct gross weight for a piece of equipment including packing materials. This typically should also document the centre of gravity. Source ISO 19901-5. | 6.4.2.1 | PDF | CFIHOS-70000358
Data
S714-IR-80 | Diesel generator data sheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document shall provide information on technical data and characteristics about material, products or systems and their environment for proper implementation. | 4.1.1.2, 4.1.2.1, 4.1.2.3, 5.1.1, 5.1.2, 5.1.4, 5.7.1.1, 5.7.3.1.4 | PDF | CFIHOS-70000416
S714-IR-81 | Noise Datasheet | The equipment noise data sheet shall contain all the information that the equipment supplier requires to understand, comply with and measure compliance with, and the noise limits for the equipment to be supplied. The equipment noise data sheet shall be returned with the tender, with its guarantee section completed by the supplier, giving the following information: a) unsilenced sound power and sound pressure levels in octave bands, and the A-weighted overall levels of the equipment; b) sound power and sound pressure levels in octave-bands, and the A-weighted overall levels of the equipment, together with details of any silencing measures that are necessary to meet the specified noise limits; c) the minimum attainable sound power and sound pressure levels in octave bands, and the A-weighted overall levels, if the specified limits cannot be met; d) details of any tonal, impulsive, intermittent or fluctuating noise levels. Additionally the following information shall be given, where applicable: e) completed data/requisition sheets of any silencers and/or acoustic enclosures, if the tender comprises such silencing equipment. | 5.2.1.2 | PDF
S714-IR-97 | Material Safety Datasheet | A structured form containing information on the safety, health and environmental protection aspects of the chemical, including protective measures and emergency actions. ISO 11014 Safety data sheet for chemical products. A structured form containing information on the safety, health and environmental protection aspects of the material, including protective measures and emergency actions. SDS shall be according to local/national regulations and in the official language plant is/will be operated, or in English if accepted by local authorities. A collection of Safety Data Sheets (SDS) shall be delivered to Company, for chemicals delivered as part of equipment, as first fill or used for preservation before operation. Exceptions are • grease • fat • surface preservatives • coatings • oils in volume per equipment below 10 litres. The report shall include one SDS per unique chemical trade name. A cross reference table with each unique chemical trade name, equipment tag number(s) and SDS file name shall also be included. | 5.3.9.1, 5.3.9.2 | PDF | CFIHOS-70000211
S714-IR-103 | Electric motor data sheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document provides information on technical data and characteristics about material, products or systems and their environment for proper implementation. Document will be IOGP S-703D with supplier fields populated. | 5.4.1, 5.7.1.1, 5.7.5.1, 5.7.5.2, 5.7.5.3, 5.7.5.4 | PDF | CFIHOS-70000416
S714-IR-105 | Generator datasheet | Document providing information on technical data and characteristics about AC generator according to IEC or NEMA. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document will provide information on technical data and characteristics about performance of the generator and include the following reactances and resistances for saturated and unsaturated conditions - DIRECT AXIS TRANSIENT REACTANCE, Xd’(%) QUADRATURE AXIS TRANSIENT REACTANCE, Xq’ (%) DIRECT AXIS SUB TRANSIENT REACTANCE, Xd” (%) QUADRATURE AXIS SUB-TRANSIENT REACTANCE, Xq” (%) | 4.1.2.1, 4.1.2.4, 5.4.1, 5.7.1.1, 5.7.1.1.1, 5.7.1.1.13, 5.7.1.1.16, 5.7.1.1.2, 5.7.1.1.4, 5.7.1.1.8, 5.7.1.2, 5.7.1.2.8, 5.7.1.3, 5.7.1.4, 5.7.1.5, 5.7.1.5.3, 5.7.2.1.2, 5.7.2.1.5, 5.7.2.1.6, 5.7.2.1.8, 5.7.2.5.1, 5.7.3.1.1, 5.7.3.1.3, 5.7.3.1.6, 5.7.3.5.2, 5.7.7.1, 5.7.7.10, 5.7.7.13, 5.7.7.15, 5.7.7.2, 5.7.7.3, 5.7.7.4, 5.7.7.5, 5.7.7.6, 5.7.7.7, 5.7.7.8, 5.7.7.9, 5.7.8.1, 5.7.8.4, 5.7.8.5, 5.7.8.6, 5.7.8.7 | PDF | CFIHOS-70000416
S714-IR-114 | Generator control panel datasheet | Generator Control Panel providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. | 5.4.1, 5.7.3.3.1, 5.7.9.1, 5.7.9.3, 5.7.9.6, 5.8.1.2.1.10, 5.8.1.2.1.4, 5.8.1.2.1.9 | PDF | CFIHOS-70000416
S714-IR-153 | Manufacturer product datasheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document will provide information on technical data and characteristics about material, products or systems and their environment for proper implementation. Submit catalogue information of all items included in the DG package where standard manufacturer datasheet is not available. | 5.7.1.1, 5.7.1.3.3, 5.7.10.10, 5.7.10.12, 5.7.10.13, 5.7.10.2, 5.7.10.3, 5.7.10.4, 5.7.10.5, 5.7.10.6, 5.7.10.7, 5.7.10.8, 5.7.2.1, 5.7.2.2.1, 5.7.2.4.1, 5.7.2.4.3, 5.7.2.5.2, 5.7.2.5.3, 5.7.3.1, 5.7.3.2, 5.7.3.2.1, 5.7.3.3, 5.7.3.4, 5.7.3.4.1, 5.7.3.5, 5.7.3.5.1, 5.7.3.5.2, 5.7.4.1, 5.7.4.2, 5.7.4.3, 5.7.4.6, 5.7.6.1, 5.7.6.2, 5.7.7.1, 5.7.7.13, 5.7.7.16, 5.7.7.2, 5.7.7.5, 5.7.7.7, 5.7.8.2, 5.7.8.3, 5.7.8.5, 5.7.8.8, 5.7.9.2, 5.7.9.3, 5.7.9.4, 5.7.9.6, 5.8.1.2.3.3, 5.8.1.2.4.10, 5.9.11, 5.9.3.1.4, 5.9.3.1.5, 5.9.3.1.7, 5.9.3.1.8, 5.9.3.1.9, 5.9.3.2.1, 5.9.3.2.2, 5.9.3.2.3, 5.9.3.2.4, 5.9.3.2.5, 5.9.3.2.7, 5.9.3.3.1, 5.9.3.3.2, 5.9.3.3.3, 5.9.3.3.4, 5.9.3.3.5, 5.9.3.3.6, 5.9.4.2, 5.9.5.1 | PDF | CFIHOS-70000416
S714-IR-185 | Instrument datasheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information,operational data and limitations of the equipment. Document provides information on technical data and characteristics about material, products or systems and their environment for proper implementation. | 5.4.1, 5.8.1.1.3, 5.8.1.1.5, 5.8.2.1.1, 5.8.2.1.10, 5.8.2.1.11, 5.8.2.1.12, 5.8.2.1.15, 5.8.2.1.17, 5.8.2.1.18, 5.8.2.1.19, 5.8.2.1.20, 5.8.2.1.4, 5.8.2.1.5, 5.8.2.1.7, 5.8.2.1.8, 5.8.2.1.9, 5.8.2.2.1, 5.8.2.2.10, 5.8.2.2.11, 5.8.2.2.12, 5.8.2.2.13, 5.8.2.2.14, 5.8.2.2.2, 5.8.2.2.3, 5.8.2.2.4, 5.8.2.2.5, 5.8.2.2.6, 5.8.2.2.7, 5.8.2.2.8, 5.8.2.2.9, 5.8.2.3.1, 5.8.2.3.10, 5.8.2.3.11, 5.8.2.3.12, 5.8.2.3.13, 5.8.2.3.15, 5.8.2.3.16, 5.8.2.3.17, 5.8.2.3.18, 5.8.2.3.19, 5.8.2.3.2, 5.8.2.3.20, 5.8.2.3.21, 5.8.2.3.3, 5.8.2.3.4, 5.8.2.3.5, 5.8.2.3.6, 5.8.2.3.7, 5.8.2.3.8, 5.8.2.3.9, 5.8.2.4.1, 5.8.2.4.2, 5.8.2.4.3, 5.8.2.4.4, 5.8.2.4.5, 5.8.2.4.6, 5.8.2.4.7, 5.8.2.4.8, 5.8.2.5.1, 5.8.2.5.2, 5.8.2.5.3, 5.8.2.5.4, 5.8.2.6.1, 5.8.2.6.2, 5.8.2.7, 5.8.3.8, 5.9.11, Table 6 |  | CFIHOS-70000416
S714-IR-192 | Diesel engine datasheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. | 5.1.3.2, 5.1.3.2, 5.4.1 | PDF | CFIHOS-70000416
S714-IR-204 | Electrical protection relay datasheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document provides information on technical data and characteristics about material, products or systems and their environment for proper implementation for electrical protection relay of generator. | 5.8.1.2.1.7, 5.8.1.3.1, 5.8.1.3.2, Table 4 | PDF | CFIHOS-70000416
S714-IR-235 | Air Release Valve Data Sheet | a datasheet which provides precise information about a tag and compliments equipment specification for vertical pumps. | 5.5.3.1 | PDF
S714-IR-243 | Weight Datasheet | A datasheet which provides weight and centre of gravity of equipment. If large items are to be handled for equipment installation or maintenance, then the weight and centre of gravity of these individual parts should be shown. Source ISO 19901-5. Data sheet to be updated at calculated and final weighed stages. | 6.4.2.1 | PDF
Drawings & Diagrams
S714-IR-218 | Heat Tracing Diagram | a diagram detailing electrical tracing. Includes anchoring and expansion joint details where applicable. Drawings to indicate thicknesses, specification and limit of application. | 5.7.3.4, 5.7.3.5, 5.8.3.12 | PDF | CFIHOS-70000182
S714-IR-212 | Detailed Drawing - Control Panel | Drawing showing parts of a construction or a component, generally enlarged, and including specific information about the form and construction or about the assembly and parts. Also supports other documents where a cross-sectional view or part list is necessary for clarity. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. Front of panel layout clearly showing overall size and layout, with a table of instruments showing duty / label engraving / model number. Back of panel arrangement clearly showing same data as front of panel. Construction drawing showing main dimensions hinging / opening of doors, door restraints, method of locking, plinths, stiffeners, hold down details (fully dimensioned), anti-vibration methods, materials, panel finish procedure and colours. Mimic / annunciator drawing where applicable. Internal layout of panel showing: a. lighting; b. cable entries and terminal strip locations; c. wiring trays; d. segregation of voltage level, IS and non-IS equipment e. hydraulic, pneumatic layouts (where applicable). | 5.3.2.1, 5.3.2.2, 5.3.2.3, 5.7.2.1, 5.7.2.2, 5.8.1.2.4.1, 5.8.1.2.4.11, 5.8.1.3.6 | PDF | CFIHOS-70000116
S714-IR-222 | HVAC Flow Diagram | A schematic diagram depicting an HVAC ducting system, including all items of duct mounted equipment complete with tag numbers, flow rate and duct sizing information. | 5.3.6.1 | PDF | CFIHOS-70000168
S714-IR-223 | Layout Diagram - Lighting | a diagram showing the precise location of assets/objects at a plant, process unit, or area basis relative to surrounding structures and equipment. | 5.3.8.1, 5.3.8.2, 5.7.4.1, 5.7.4.2, 5.7.4.3, 5.9.5.1, 5.9.5.2, 5.9.6 | PDF | CFIHOS-70000277
S714-IR-237 | General Diagram - Transportation | A diagram showing engineered tie-down points required for securing equipment and lifting arrangement during transportation. | 5.6.4.1.3 | PDF | CFIHOS-70000118
S714-IR-238 | Lifting, Hoisting, And Rigging Plan / Drawing | a document capturing what particular activities and requirements will be executed and delivered for lifting, hoisting, and rigging. Should cover scope regardless of timing in asset lifecycle. Specific risks relating to simultaneous operations should be addressed | 5.6.7.3.1, 5.6.7.3.2 | PDF | CFIHOS-70000200
S714-IR-23 | Piping And Instrumentation Diagram - Diesel Generator Package | Description: The piping and instrument diagram (P&ID), based on the process flow diagram, represents the technical realization of a process by means of graphical symbols for equipment and piping together with graphical symbols or process measurement and control functions. Mandatory content of information: – Function or type of equipment, including drives, conveyors, as well as installed spares; – Identification number of equipment including drives, conveyors as well as installed spares; – Characteristic data of equipment; – Indication of line number, nominal diameter, pressure rating, material class and fluid class of all piping; - Identification of any special piping items; – Details of equipment, piping, valves and fittings, thermal insulation; – Process measurement and control functions with identification number; – Characteristic data of drives. Optional content of information: – Denomination of flow rates and amounts of energy or energy carriers; – Route and direction of flow of energy or energy carriers; – Type of essential primary elements and sensors; – Essential construction materials for equipment; – Elevation of platforms and approximate relative vertical position of equipment; – Reference designation for valves and fittings; – Denomination of equipment; - External piping interfaces. | 5.1.2, 5.1.5.5, 5.1.6.2, 5.3.5.1, 5.5.2.1, 5.5.2.2, 5.5.2.3, 5.5.2.7, 5.5.5.1.2, 5.5.5.1.3, 5.5.5.1.4, 5.5.5.2.1, 5.5.5.2.2, 5.5.5.3.1, 5.8.2.1.16, 5.8.2.1.2, 5.8.2.1.6 | PDF | CFIHOS-70000292
S714-IR-25 | Wiring Diagram | Description: Diagram providing information on the circuitry of an object. Mandatory content of information: – Graphical symbols representing the objects; – Graphical symbols representing the connections among objects; – Reference designations; – Terminal designations; – Signal level conventions (applicable to logic signals). – Information necessary to trace paths and circuits (signal designations, location references) – Supplementary information necessary for the understanding of functions Optional content of information: – Technical data; – Reference to other documents; – Information about wiring performance; – Cable and cable core identification. | 5.1.5.6, 5.1.6.6, 5.7.1.4.6.3 , 5.7.10.1, 5.7.10.10, 5.7.10.11, 5.7.10.12, 5.7.10.13, 5.7.10.15, 5.7.10.16, 5.7.10.17, 5.7.10.2, 5.7.10.3, 5.7.10.7, 5.7.10.8, 5.7.10.9, 5.7.4.1, 5.7.4.2, 5.7.7.12, 5.7.7.16, 5.7.7.6, 5.7.7.9, 5.7.8.1, 5.7.8.2, 5.7.8.3, 5.7.8.8, 5.7.9.7, 5.8.1.1.2, 5.8.1.1.4, 5.8.1.2.1.4, 5.8.1.2.1.5, 5.8.1.2.2.1, 5.8.1.2.2.12, 5.8.1.2.2.13, 5.8.1.2.2.14, 5.8.1.2.2.15, 5.8.1.2.2.16, 5.8.1.2.2.2, 5.8.1.2.2.3, 5.8.1.2.2.4, 5.8.1.2.2.8, 5.8.1.2.2.9, 5.8.1.2.4.1, 5.8.1.2.4.10, 5.8.1.2.4.11, 5.8.1.2.4.2, 5.8.1.2.4.3, 5.8.1.2.4.4, 5.8.1.2.4.5, 5.8.1.2.4.7, 5.8.1.2.4.8, 5.8.1.2.4.9, 5.8.1.3.2, 5.8.1.3.3, 5.8.1.3.4, 5.8.1.3.5, 5.8.1.3.6, 5.8.1.3.7, 5.8.2.1.13, 5.8.2.1.3, 5.8.2.3.3, 5.9.10.1, 5.9.10.2, 5.9.10.3, 5.9.10.4, 5.9.10.5, 5.9.10.6, 5.9.3.1.2, 5.9.7.14, 5.9.9.3, 5.9.9.4, 5.9.9.7, Table - 5.7.1.4.6.4 , Table 3, Table 4, Table 5 | PDF | CFIHOS-70000268
S714-IR-79 | Schematic drawing | A pictorial representation of the main elements and functions of a control circuit for electrical equipment with input/output sources (switches, relays etc.) and their relationships for control panels, lighting, heat tracing, etc. | 5.1.3.1, 5.1.5.6, 5.7.1.3.3, 5.7.1.4.6.3 , 5.7.10.1, 5.7.10.11, 5.7.10.12, 5.7.10.13, 5.7.10.14, 5.7.10.15, 5.7.10.16, 5.7.10.17, 5.7.10.2, 5.7.10.3, 5.7.10.7, 5.7.10.8, 5.7.10.9, 5.7.4.1, 5.7.4.2, 5.7.8.1, 5.7.8.2, 5.7.8.8, 5.7.9.3, 5.7.9.4, 5.7.9.5, 5.7.9.7, 5.8.1.2.2.15, 5.8.1.2.2.16, 5.8.1.2.4.1, 5.8.1.2.4.11, 5.8.1.2.4.12, 5.8.1.2.4.2, 5.8.1.2.4.3, 5.8.1.2.4.4, 5.8.1.2.4.5, 5.8.1.2.4.6, 5.8.1.2.4.7, 5.8.1.2.4.8, 5.8.1.2.4.9, 5.8.1.3.3, 5.8.1.3.4, 5.8.1.3.5, 5.8.1.3.6, Table - 5.7.1.4.6.4 , Table 3, Table 4, Table 5 | PDF | CFIHOS-70000328
S714-IR-116 | General arrangement drawing - Control panels | Control panel drawings showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing will contain reference to main specifications and standards. Panel drawing will include location of items mounted on panel front with cross sectional views. Document may contain the following information: • Main dimensions • Gland plate details • Weight • Centre of gravity • Withdrawal/installation and maintenance space. • Installation and mounting details • Lifting arrangement | 5.3.2.1, 5.3.2.2, 5.3.2.3, 5.3.7.4, 5.7.1.4.6.3 , 5.7.10.14, 5.7.10.15, 5.7.10.16, 5.7.10.9, 5.7.6.3, 5.8.1.1.10, 5.8.1.2.1.1, 5.8.1.2.1.11, 5.8.1.2.1.2, 5.8.1.2.1.3, 5.8.1.2.1.4, 5.8.1.2.2.10, 5.8.1.2.2.13, 5.8.1.2.2.14, 5.8.1.2.2.15, 5.8.1.2.2.16, 5.8.1.2.2.5, 5.8.1.2.3.1, 5.8.1.2.3.2, 5.8.1.2.4.1, 5.8.1.2.4.11, 5.8.1.2.4.12, 5.8.1.3.3, 5.8.1.3.6, 5.8.1.3.7, Table - 5.7.1.4.6.4 , Table 3 | PDF | CFIHOS-70000153
S714-IR-117 | General arrangement drawing - Electrical | The generator drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing will contain reference to main specifications and standards. For equipment / components the drawing may include cross sectional views, terminal boxes, etc. Document may contain the following information: • Main dimensions • Interface connections • Weight • Centre of gravity • Withdrawal/installation and maintenance space. • Installation and mounting details • Lifting arrangement • Terminal boxes Heat tracing drawing | 5.7.1.1.4, 5.7.2.1.2, 5.7.3.1, 5.7.7.2, 5.8.1.2.4.5 | PDF | CFIHOS-70000153
S714-IR-118 | General arrangement drawing - Diesel Generator package | A drawing showing outline dimensions with arrangement of components and accessories of the diesel generator package, part references, including the following details - • Size, type, rating and identification of all tie-in connections • Weight of the equipment assembly with overall erection weight and maintenance weight for mechanical handling • Principal dimensions including overall equipment assembly, maintenance clearance and tie-in point locations • Shaft centreline height (if applicable) • Location of Centre of gravity and lifting points • Installation and mounting details • Lifting arrangement • Weight components • Maintenance weight of major components Drawing will include general arrangement drawing of diesel engine, generator and other auxiliary equipment e.g. radiator cooler, exhaust cooler, exhaust silencer, hydraulic starter unit, pneumatic starter unit, battery cabinet, fuel tank, fire protection package, cable tray layout, lighting layout, etc. | 5.1.3.1, 5.1.5.1, 5.1.5.5, 5.1.5.6, 5.1.6.1, 5.1.6.2, 5.1.6.3, 5.1.6.4, 5.2.2.1, 5.3.1.4.5, 5.3.10.1, 5.3.3.1, 5.3.3.2, 5.3.3.3, 5.3.4.1, 5.3.4.2, 5.3.4.3, 5.3.4.4, 5.3.4.5, 5.3.4.6, 5.3.4.7, 5.3.4.8, 5.3.5.2, 5.3.7.1, 5.3.7.2, 5.3.7.3, 5.3.7.4, 5.3.9.1, 5.3.9.2, 5.3.9.3, 5.3.9.4, 5.5.2.7, 5.5.5.1.1, 5.5.5.1.5, 5.5.5.2.1, 5.5.5.2.2, 5.5.5.2.3, 5.5.6.1, 5.5.7.2, 5.6.1.1, 5.6.2.1, 5.6.2.2, 5.6.2.3, 5.6.2.4, 5.6.2.5, 5.6.3.1, 5.6.3.2, 5.6.3.3, 5.6.3.5, 5.6.3.6, 5.6.3.7, 5.6.3.8, 5.6.3.9, 5.6.4.1.1 , 5.6.7.1.2, 5.6.9.1, 5.6.9.2, 5.8.3.3 | PDF | CFIHOS-70000153
S714-IR-133 | Acoustic enclosure drawing | Acoustic enclosure or container details will be provided addressing the following functions: - access for routine maintenance and operation with doors lockable in open position; - removal of the generator horizontally through removable panels from the generator end; - removal of the diesel engine vertically through removable panels; - enclosure lighting; - fire and gas detectors; - distribution piping for water mist extinguisher; - fire dampers; - ventilation intake with filters; - single point lifting; - noise attenuation with silencers at ventilation air inlet and exhaust; - A60 rated panels; - panels designed for specified blast pressure. | 5.1.5.1, 5.1.5.2, 5.1.5.4, 5.1.6.2, 5.1.6.3, 5.1.6.4 | PDF | CFIHOS-70000118
S714-IR-134 | Name Plate Drawing | A drawing that depicts layout information required either by the nominated standard or supplementary specification | 6.4.1.1, 6.4.1.2, 6.4.1.3, 6.4.1.4, 6.4.1.5, 6.4.1.6 | PDF
S714-IR-138 | Foundation Loading Diagram | a diagram detailing static and dynamic forces or movements acting on foundations or other load bearing supports, anchor bolt details, lengths and pre-tensioning. May include Civil Structural for loads imposed, and Civil Foundations for foundation design. Also see Foundation Design Diagram, specifically for construction details | 5.6.2.1, 5.6.2.2, 5.6.2.3, 5.6.2.4, 5.6.2.5, 5.6.3.1, 5.6.3.2, 5.6.3.3, 5.6.3.5, 5.6.3.6, 5.6.3.7, 5.6.3.8, 5.6.3.9, 5.6.4.1.1 , 5.6.4.2.1, 5.6.4.2.5, 5.6.4.2.6 | PDF | CFIHOS-70000151
S714-IR-139 | Detailed Drawing - Baseplate | Drawing showing parts of a construction or a component, generally enlarged, and including specific information about the form and construction or about the assembly and joints Also supports other documents where a cross-sectional view or part list is necessary for clarity. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. | 5.6.4.1.3, 5.6.4.1.4, 5.6.4.2.1, 5.6.4.2.10, 5.6.4.2.2, 5.6.4.2.3, 5.6.4.2.5, 5.6.4.2.6, 5.6.4.2.7, 5.6.4.2.9, 5.6.6.1, 5.6.7.2.2, 5.6.8.1, 5.6.8.10, 5.6.8.11, 5.6.8.12, 5.6.8.2, 5.6.8.3, 5.6.8.4, 5.6.8.5, 5.6.8.6, 5.6.8.7, 5.6.8.8, 5.6.8.9, 5.6.9.1, 5.6.9.2, Figure 3, Figure 4, Figure 5, Figure 6 | PDF | CFIHOS-70000116
S714-IR-156 | Earthing Diagram | a diagram detailing earthing (grounding) for plant and equipment and between modules and dissimilar structural elements. | 5.8.1.2.2.12, 5.9.4.1, 5.9.9.1, 5.9.9.2, 5.9.9.3, 5.9.9.4, 5.9.9.5, 5.9.9.6, 5.9.9.7 | PDF | CFIHOS-70000103
S714-IR-162 | System Topology Diagram | Systems Topology Block Diagram shall show overall configuration of systems and subsystems to give a functional understanding on a high level. Typical contents shall be: • All related systems and subsystems represented by blocks • Location of the equipment, either by text labelling of each block or by blocks located in dotted area boxes. • Interface between blocks shall be indicated | 5.8.1.1.1, 5.8.1.1.2, 5.8.1.1.6 | PDF
S714-IR-164 | Layout Drawing - Instruments, Junction boxes, cable trays, MCT and earthing | A diagram showing the precise location of gauge boards, junction boxes and instruments on an equipment package relative to surrounding equipment. | 5.3.1.4.5, 5.3.1.4.6, 5.3.5.1, 5.3.7.4, 5.8.1.1.5, 5.8.1.2.3.3, 5.8.3.2, 5.8.3.3, 5.8.3.4, 5.8.3.5, 5.8.3.6, 5.8.3.7, 5.8.3.8, 5.9.5.1, 5.9.5.2, 5.9.6, 5.9.7.4, 5.9.7.7, 5.9.7.8, 5.9.8.1, 5.9.8.2, 5.9.8.3, 5.9.8.4, 5.9.8.5, 5.9.8.6, 5.9.9.1, 5.9.9.2, 5.9.9.3, 5.9.9.4, 5.9.9.5, 5.9.9.6, 5.9.9.7 | PDF | CFIHOS-70000277
S714-IR-166 | Termination Diagram | a diagram for motors, panels, junction boxes, etc. identifies all connections and cable terminations at input/output rails. Required for removal/hook up purposes and modifications. To include vendor interfaces. | 5.1.6.6, 5.9.10.1, 5.9.10.2, 5.9.7.1, 5.9.7.10, 5.9.7.11, 5.9.7.12, 5.9.7.13, 5.9.7.14, 5.9.7.2, 5.9.7.5, 5.9.7.6, 5.9.7.8, 5.9.7.9 | PDF | CFIHOS-70000330
S714-IR-175 | Loop Diagram | a diagram showing details all elements of a control loop, from sensing element through to controlling element, and cabling and wiring details for the associated instruments. Includes junction box, marshalling cabinet and control panel terminations and power supply details. |  | PDF | CFIHOS-70000205
S714-IR-182 | Hook Up Diagram | a diagram which may show the instrument impulse, pneumatic and electronic connections, pipe work, valves, fittings, flanges and support details with associated material take-off list. Used for removal/hook up purposes and modifications. Synonym: Installation details. | 5.8.2.1.6, 5.8.3.10, 5.8.3.11, 5.8.3.12, 5.8.3.13, 5.8.3.9 | PDF | CFIHOS-70000167
S714-IR-183 | Human Machine Interface (HMI) Graphics | Graphics describing human machine interface presented on screen for operator use. | 5.3.2.2, 5.3.2.3, 5.8.1.2.1.11, 5.8.1.2.1.3, 5.8.2.1.2 | PDF
S714-IR-199 | Logic Diagram | a graphical representation of a system using formal logic. It displays the existence of functional elements and the paths by which they interact with each other. Includes SAMA drawings | 5.1.6.5, 5.1.6.6, 5.8.1.2.4.10, 5.8.1.2.4.11, 5.8.1.2.4.2, 5.8.1.2.4.3, 5.8.1.2.4.4, 5.8.1.2.4.5, 5.8.1.2.4.6, 5.8.1.2.4.7, 5.8.1.2.4.8, 5.8.1.2.4.9 | PDF | CFIHOS-70000248
S714-IR-201 | Cause And Effect Diagram | Matrix cross-referencing logic control signals actuating a set of corrective actions. To define logic control and shutdown functions, alarms, trips to ensure sufficient process safety and shutdown. | 5.1.5.4, 5.1.6.5, 6.2.3.4.1 | PDF | CFIHOS-70000409
S714-IR-205 | General arrangement drawing - Instruments and valves | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing will contain reference to main specifications and standards For equipment / components the drawing may include cross sectional views. Document may contain the following information: • Main dimensions • Interface connections • Weight • Center of gravity • Withdrawal/installation and maintenance space. • Installation and mounting details • Lifting arrangement | 5.3.7.4, 5.8.2.1.12, 5.8.2.1.4, 5.8.2.1.5, 5.8.2.3.16, 5.8.2.5.1, 5.8.2.5.2, 5.8.2.5.3, 5.8.2.5.4, 5.8.3.2 | PDF | CFIHOS-70000153
S714-IR-206 | Equipment Cross Section Diagram | A detail and cross sectional drawing with parts list to facilitate dismantling, repair and assembly of parts and components shall be included. Relevant for assemblies and smaller components within assemblies. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. The manufacturer's standard detail cross sectional drawing shall be delivered. Typical information may be: • Items list with reference to supplier's part number. • Material definition with reference to relevant standards | 5.7.7.10, 5.7.7.11, 5.7.7.12, 5.7.7.14 | PDF | CFIHOS-70000116
S714-IR-219 | General Arrangement Drawing - Enclosure | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing shall contain reference to main specifications and standards For equipment / components the drawing may include cross sectional views. Document may contain the following information: • Main dimensions • Interface connections • Weight • Centre of gravity • Withdrawal/installation and maintenance space. • Installation and mounting details • Lifting arrangement • Water mist nozzle & piping layout | 5.3.1.1.1, 5.3.1.1.2, 5.3.1.1.3, 5.3.1.1.4, 5.3.1.1.5, 5.3.1.2.1, 5.3.1.2.2, 5.3.1.2.5, 5.3.1.2.6, 5.3.1.2.7, 5.3.1.3.1, 5.3.1.3.2, 5.3.1.3.3, 5.3.1.4.1, 5.3.1.4.2, 5.3.1.4.3, 5.3.1.4.4, 5.3.1.4.5, 5.3.1.4.6, 5.3.1.5.1, 5.3.1.5.2, 5.3.1.5.3, 5.3.1.5.4, 5.3.1.5.5, 5.3.1.5.6, 5.3.1.6.1, 5.3.1.6.2, 5.3.1.6.3, 5.3.1.6.4, 5.3.1.6.5, 5.3.1.6.6, 5.3.1.6.7, 5.3.10.1, 5.3.10.2, 5.3.10.3, 5.3.10.4, 5.3.10.5, 5.3.10.6, 5.3.10.7, 5.3.10.8, 5.3.3.2, 5.3.3.3, 5.3.4.1, 5.3.4.2, 5.3.4.3, 5.3.4.4, 5.3.4.5, 5.3.4.6, 5.3.4.7, 5.3.4.8, 5.3.5.2, 5.3.9.1, 5.3.9.2, 5.3.9.3, 5.3.9.4, 5.6.5.1, 5.6.7.1.2 | PDF | CFIHOS-70000153
S714-IR-220 | Detailed Drawing - Enclosure penetrations and access panels | Drawing showing parts of a construction or a component, generally enlarged, and including specific information about the form and construction or about the assembly and parts. Also supports other documents where a cross-sectional view or part list is necessary for clarity. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. | 5.3.1.2.3, 5.3.1.2.4 | PDF | CFIHOS-70000116
Lists
S714-IR-82 | Spare Part List | Table containing list items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for later use. Mandatory content of information: – Item reference number; – Quantity; – Part number or global identifier (together with manufacturer / supplier); – Part name. Optional content of information: – Type designation; – Specifying technical data; – Descriptive technical data; – Mass, dimensions; – Reference to document; – Remark. List to include start-up and commissioning, operational and capital spares |  | PDF | CFIHOS-70000374
S714-IR-85 | Bill Of Materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and references to specifications. Note when agreed includes details of sub-suppliers and associated purchase orders. | 5.5.2.4, 5.5.2.5, 5.5.2.8, 5.5.4.1, 5.5.7.3, 5.7.10.14, 5.8.1.2.1.5, 5.8.1.2.2.4, Table 2 | PDF | CFIHOS-70000028
S714-IR-87 | Utility Consumption List | Document providing input to engineering for design of the customer's installation or utility arrangement. Document stating the normal and maximum consumption of e.g. electric power, diesel oil, compressed air, heating/cooling media etc., for the equipment(-s) or unit(-s). The following generalised index shall be used: • Equipment tag no. • Type of consumption • Normal Mode - The mode of platform operation when main process, utility systems (including drilling) and other facilities are in operation. This mode of operation gives the peak power requirement. • Critical Mode - The mode of platform operation just after a generator shut down and only one generator is running. • Stabilized Mode - The same mode of platform operation as critical mode, but the situation is stabilized. • Emergency Mode - The mode of platform operation when main process, utility systems, supplies to existing facilities are shut down. - The main generators are shut down. - The emergency generator is running. The load list shall show individual consumers to high and low voltage switchboards. | 5.7.1.2, 5.7.1.3 | PDF
S714-IR-88 | Instrument List | an authoritative collection of values with a relationship to instrumentation. The columns of this collection is specified and controlled. Also known as Instrument Index | 5.8.1.1.5 | PDF | CFIHOS-70000418
S714-IR-89 | Lubrication List | Schedule to indicate type and grade of lubricants and other consumables required for all equipment supplied. For each schedule entry the following is also to be included as a minimum: Tag number, tag description / component (e.g. bearings, engine, gearbox, etc), lubricant manufacturer, lubricant type and grade (product code), first fill capacities, rate of consumption (litres / day) and frequency of change. |  | PDF
S714-IR-90 | Alarm, Trip Setting List | a collection of all instrument set points and/or alarms. Each instrument having an alarm or trip function is listed. Alarms and settings are given as percentages of transmitter range and in engineering units, together with transmitter range, location of the annunciation point, cabinet, identification and relevant P&IDs/PEFS or logic drawing. | 5.8.1.1.7, 5.8.1.2.1.3, 5.8.1.3.3, Table 4, Table 5 | PDF | CFIHOS-70000007
S714-IR-140 | Special Tools List | The Special Tools List shall identify all special tools necessary for handling, dismantling, maintenance etc. of equipment. Shall be part of the Spare part list Special Tools List shall include: • Identification - the tag number the special tool shall support • Description of the special tool • Storage, i.e. the location where the special tool can be found • Document references, if applicable Note that the actual special tool shall be marked with the identification, i.e. tag number that it supports. | 6.4.3.1, 6.4.3.2 | PDF
S714-IR-172 | Communication Signals List | A list which defines serial link communication signals and its protocol configuration parameters as agreed with plant control system supplier. | 5.8.1.1.7 | PDF
S714-IR-184 | Cable List | a collection of values relating to List of all cables, their specifications and end points. Indicates salient features of all cables in Vendor's supply and connecting cables supplied by Principal. Synonym: Cable Schedule | 5.9.3.1.3 | PDF | CFIHOS-70000033
S714-IR-236 | Manual Valve List | a list describing manually operated valves. Not check valves, not motor operated valves, not control valves, not PSVs, as these are all captured elsewhere (see instrument index for relief devices and actuated valves). | 5.5.3.1 | PDF | CFIHOS-70000346
S714-IR-241 | Tag/Equipment Register | an authoritative collection of values with a relationship to a specific equipment or tag. The columns of this collection is specified and controlled. | 6.3.1.1, 6.3.1.2 | PDF | CFIHOS-70000122
Manuals and MRB
S714-IR-91 | Installation Manual | Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. NOTE: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand alone document. | 5.7.4.2.8, 6.4.7.1 | PDF | CFIHOS-70000181
S714-IR-92 | Maintenance Manual | Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package supplier. Manual to include a detailed maintenance schedule for all the planned maintenance activities over a five year period including the activity, a high-level description, ​frequency, duration and equipment status during maintenance activity. NOTE: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand alone document. | 5.1.5.1, 5.2.2.1, 5.2.3.1, 5.3.10.2, 5.3.10.3, 5.3.4.8, 5.7.10.2, 5.7.7.13, 5.7.7.16, 5.8.1.2.4.10, 5.8.1.2.4.2, 5.8.1.2.4.3, 5.8.1.2.4.4, 5.8.1.2.4.6, 5.8.1.2.4.8, 5.8.1.2.4.9, 5.8.1.3.3, 5.8.1.3.4, 5.8.1.3.5, 6.1.2.1, 6.4.7.1 | PDF | CFIHOS-70000206
S714-IR-93 | Operating Manual | Description of methods of operating a piece of equipment or process unit, including but not limited to instructions, procedures, drawings, tables, etc. for the operation -stop, start, and emergency shutdown. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. NOTE: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand alone document. | 4.1.1.3, 5.2.2.1, 5.3.10.2, 5.7.1.1.13, 5.7.1.4.6.3 , 5.7.10.12, 5.7.10.13, 5.7.10.14, 5.7.10.15, 5.7.10.16, 5.7.10.17, 5.7.10.2, 5.7.10.4, 5.7.10.5, 5.7.10.8, 5.7.7.13, 5.7.7.16, 5.7.9.4, 5.8.1.2.4.10, 5.8.1.2.4.2, 5.8.1.2.4.3, 5.8.1.2.4.4, 5.8.1.2.4.6, 5.8.1.2.4.8, 5.8.1.2.4.9, 5.8.1.3.2, 5.8.1.3.3, 5.8.1.3.4, 5.8.1.3.5, 6.1.2.1, 6.4.7.1, Table 3 | PDF | CFIHOS-70000228
S714-IR-94 | Manufacturer Record Book (MRB) | Detailed information/description for the documents to be included in MRB as agreed between Purchaser and Vendor: Shall include but not be limited to documents Recording Compliance With Statutory and/or Local Regulations, and inspection and testing results / reports for all the testing (e.g. Mill tests on Material, production test coupon results, NDE, NDE personnel qualification, impact test, Heat treatment, leak testing etc.) carried out at Vendor/Sub-Vendor shop and at mill. | 5.4.1, 5.7.7.8, 6.2.4.2 | PDF
Philosophy
S714-IR-167 | Functional Design Specification | A specification that describes the technical and functional description of performance, control and monitoring parameters for operation/protection of the Diesel Generator and its sub-systems provided by the package supplier. The scope covered by this document is based on the scope of supply specified in the purchase order and covers all related main equipment of the DG. This document provides the information necessary to form a basis for an overall understanding of the relevant DG package applications, and will be used as the basis for the operating manual. | 4.1.1.1, 4.1.1.2, 4.1.1.3, 4.1.2.1, 4.1.2.3, 4.2.1 | PDF | CFIHOS-70000244
Procedures
S714-IR-44 | Non Destructive Test Procedure | This document is a part of the Quality Assurance Plan, and herein the Quality Assurance work process and verification. This document provides a procedure for NDT operator to ensure repeatability and formalism and hence prove the quality of the NDT work. Document describing how to perform NDT (i.e. MT, PT, RT, UT, VT or ET) for a given object, including acceptance criteria and reporting. FALSE) |  | PDF | CFIHOS-70000227
S714-IR-45 | Functional test procedure | Functional test of engine control panel software and related control interface with Purchaser's control system, overspeed trip functionalities and simulated testing of engine battery starting system | 6.2.3.2.2.1, 6.2.3.2.2.2, 6.2.3.4.2 | PDF
S714-IR-46 | Factory acceptance test procedure | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document will include all testing activities and their acceptance criteria according to applicable standards, specifications and requirements and to document the condition of the equipment as tested from factory. Test set-up and test equipment is defined. This will include engine performance test, generator load test, static load test, mechanical run test, noise test etc. Instrumentation, ECP, GCP and safety equipment will be function tested to ensure operation conforms to the cause and effect chart. Suppliers standard (routine) test procedures should be used as far as possible | 5.8.1.1.8, 6.2.1.1, 6.2.3.5.1, 6.2.3.5.4 | PDF
S714-IR-68 | Painting And Coating Procedure | Verification of suppliers compliance with surface protection and coating requirements. This document provides a procedure for coating operator to ensure repeatability and formalism and hence prove the quality of the coating work. This document details the work process and how the defined requirements to surface treatment, application and quality control shall be met. A procedure may cover wet paint, powder coating, or metallic coatings. The document shall include reference to applied standards and the information about revision of the applied standard. Procedure to include painting system. | 5.4.3.1, 5.4.3.2, 5.4.3.3, 5.4.3.4 | PDF | CFIHOS-70000384
S714-IR-71 | Welding Procedure Qualification Record | Records documenting welding and associated testing of welding processes to a defined set of essential variables. Typically includes all testing procedure references and both destructive and non-destructive testing results. | 5.4.2.1, 5.4.2.2.2.1, 5.4.2.2.2.2, 5.4.2.2.2.3 | PDF | CFIHOS-70000362
S714-IR-72 | Welding Repair Procedure | a document which describes a set of logically sequenced instructions to execute a weld repair | Table 1 | PDF | CFIHOS-70000363
S714-IR-73 | Pressure Test Procedure | a procedure documenting specific steps to conduct inspection of an asset/object. Typically details boundaries of the test, isolations, method of pressurization, required hold intervals etc. Includes hydrostatic, pneumatic, vacuum and leak test/examinations | 5.5.2.6, 6.2.2.2, 6.2.3.2.1.2 | PDF | CFIHOS-70000286
S714-IR-96 | Commissioning Instruction | Instruction providing information on the commissioning of the product. Instructions for commissioning are provided especially for large and highly complex products and for large industrial installations. The purpose of such instructions is to provide the user with the information needed for initial setting-up of the product. Mandatory content of information: These instructions should contain for example: - download program, software instructions according to IEC 61506; - checking instructions; - checks to be performed before connection to the supply network and before first operation; - details of specifications to apply to acceptance, inspection and performance tests. | 6.4.7.1 | PDF
S714-IR-130 | Mechanical Test Procedure | Defines procedures, test methods for confirming material properties against specified requirements. Methods typically based on industry standards such as ASTM. Acceptance criteria and extend of testing defined in the applicable material standards. | 5.4.1 | PDF
S714-IR-144 | Painting And Coating System Qualification | Test results establishing coating system conformance with specification requirements |  | PDF
S714-IR-146 | Insulation Procedure | Procedure explaining how insulation will be applied to the piping and equipment. Some of the insulation applications will be removable type to allow for service and maintenance. The procedure will also list insulation materials for different temperature applications and their thickness with respect to diameter. Details of various types of perforated guards will be included. | 5.3.5.1, 5.4.4.1.1, 5.4.4.2.1, 5.4.4.2.2, 5.4.4.2.3 | PDF
S714-IR-169 | Lifting and Installation Procedure | The [suppliers] proposed and acceptable transportation, lifting requirements and handling methods. Drawings shall be provided indicating size of containers / packages, centre of gravity, number off weight, identification, and packing list of contents. Also to include installation procedure. Note Copies of applicable lifting procedures are to be included in the delivery documentation which accompanies shipments of equipment. |  | PDF
S714-IR-171 | Cyber Security Documentation | This document shall contribute to gather all required information to perform an overall risk and vulnerability assessment of the final installation. Document definition: The Cyber Security document is intended to identify threats and risks related to information security of industrial automation and control systems that the equipment shall have countermeasures against to avoid damaging consequences. The documentation shall include: - A list of all relevant hardware components in the scope of supply. - A list of all physical ports (Ethernet, USB etc.) on each hardware - A list of all logical interfaces on the physical ports. - A list of all software components installed on the hardware components. This document shall be treated as confidential. This document should also provide information according to Norsok T-101 requirements of a cyber security vulnerability assessment.» | 5.8.1.4.1, 5.8.1.4.2, 5.8.1.4.3 | PDF
S714-IR-173 | Safety And Automation System (SAS) Communication Interface Test Procedure (UFAT) | Required by the facility control system supplier to configure the communication links prior to test activities This procedure should include the testing requirements to perform the communication interface. | 5.8.1.1.11, 5.8.1.1.6, 5.8.1.1.7, 5.8.1.1.8, 5.8.1.1.9 | PDF
S714-IR-187 | Obsolescence management plan | Plan defining the manufacturer's co-ordinated activities to direct and control the strategies for the identification and mitigation of the effects of obsolescence to the user, through all stages of the life of all components within the UPS System. An example of the principles of this plan is defined within IEC 62402, Obsolescence management – Application guide. | 5.8.1.2.1.8 | PDF
S714-IR-195 | Material handling procedure | Supplier will prepare lifting requirements and handling methods for the items included in the diesel generator package that will be removed out of the enclosure for maintenance or replacement. Removal panels of the enclosure will be identified in the drawings. Report will include drawings/sketches indicating size of items, centre of gravity, transportation outside the enclosure. | 5.1.5.1 | PDF
S714-IR-230 | Welding Procedure Specification | A specification that describes the welding procedure and process of a specific set of essential variables. | 5.4.2.1, Table 1 | PDF | CFIHOS-70000408
S714-IR-239 | Routine test procedure | Procedure documenting the manufacturers recommended testing activities and acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Procedure to define test set-up and test equipment. | 6.2.3.3.1 | PDF
S714-IR-244 | Weighing Test Procedure | Procedure for weighing each item of equipment. Dry weights and centre of gravity are to be verified. | 6.4.2.1 | PDF
Records
S714-IR-100 | Noise Test Records | Noise test reports based on the standard or plant noise acceptance test procedure, including measurement and calculation methods and tolerances. A final plant acceptance test shall be performed and reported in a noise verification report by the end-user or contractor, or by an independent party according to the test procedures agreed. Some authorities require certified or accredited organizations to be involved. The report may be prepared in accordance with the format shown in ISO 15664, Annex I. The verification report usually includes a noise survey of the plant. The results of the survey will be compared with the project requirements. The comparison of required and determined noise levels completes the verification process. The model noise survey report is not specifically intended to describe the measurement of sound pressure levels of individual items of equipment and the derivation of their sound power levels. However, while such activities may be part of the objectives of a verification report, such noise measurements are described in detail in other relevant International Standards. | 5.2.1.2, 5.2.1.3, 6.2.4.3 | PDF
S714-IR-109 | Hazardous Area Installation Records | Records demonstrating that equipment has been installed in accordance with specific requirements for the specified hazardous area. e.g. ATEX, BASEEFA, PTB, UL, CSA, NEMA, EX, etc. | 4.2.1 | PDF
S714-IR-119 | Factory Acceptance Test (FAT) Records | The FAT report will be used to verify that the equipment has been tested according to FAT procedure. The FAT report will be used for acceptance of the equipment delivery This document shall include all testing activities and their acceptance criteria according, , in accordance with the FAT procedure, to applicable standards, specifications and requirements,. to document the condition of the equipment as tested from factory. Test set-up and test equipment shall be defined. | 6.2.3.2, 6.2.3.2.2.1, 6.2.3.4, 6.2.3.5.1, 6.2.3.5.4 | PDF
S714-IR-121 | Non-Destructive Examination (NDE) Report | A document containing data which records compliance with specified procedure. Documents containing records of performed NDT (in typical NDT methods e.g. MT, PT, RT, UT, ET and VT). | 5.6.7.2.3, 5.6.7.3.3, Figure 7, Figure 8 | PDF
S714-IR-143 | Painting And Coating Inspection Records | This document is used for verification of compliance with surface protection and coating requirements. Document containing records of performed surface protection and coating work. | 5.4.3.1, 5.4.3.2, 5.4.3.3, 5.4.3.4 | PDF
S714-IR-210 | Production parameter monitoring record | Monitoring records shall: a) be traceable to a specific welder, WPS and production weld; b) verify correct fit-up and root pass penetration for single sided welds where full penetration is required, including weld'olets and/or attachment welds; c) detail the actual preheat and interpass temperature, welding parameters and resulting heat input; d) be endorsed by the welding coordinator or welding inspector; e) be made available to the purchaser upon request. | 5.4.2.2.9.1, 5.4.2.2.9.2, 5.4.2.2.9.3, 5.4.2.2.9.4, 5.4.2.2.9.5, Table 1 | PDF
S714-IR-231 | Welding Traceability Records | Welding records presented as data set, plan, drawing or map. Typically providing traceability for; - Weld number and welders identification, fabrication drawing number, systems and line number (piping systems), Welding Procedure Specification, Extent of NDE, NDE report number, inspection result, number of performed weld repairs, PWHT report number, repair report number, deviation report | 5.4.2.2.11, Table 1 | PDF | CFIHOS-70000360
S714-IR-225 | Non Destructive Examination (NDE) Personnel Qualification | Records demonstrating competence of NDE personnel in accordance with recognised certification program ASNT or ISO | 5.4.2.2.8.1, 5.4.2.2.8.2 | PDF
S714-IR-227 | Welding Coordinator Qualification | Welding coordinator certification and record of relevant qualification and experience. | 5.4.2.2.5.1, 5.4.2.2.5.2 | PDF
S714-IR-228 | Welding Inspector Qualification | Welding inspector certification and CV/description of relevant experience. | 5.4.2.2.4 | PDF
S714-IR-245 | Positive Material Identification (PMI) Records | Result of Positive Material Identification testing to a defined procedure confirming material subject to PMI are of the specified material grade. Note: PMI results do not constitute material certification | 5.4.1, 5.6.4.2.3, 5.8.1.2.1.1, 5.8.2.3.19, 5.8.2.3.6, 5.8.3.10, 5.8.3.11, 5.9.7.3, 5.9.9.5 | PDF
Reports
S714-IR-107 | Emissions Report | a report detailing accumulated environmental emissions over a set period of time. | 6.2.3.2.1.3 | PDF | CFIHOS-70000108
S714-IR-120 | Pressure Test Report | a report recording duration and results of hydro static, pneumatic, and leak test examinations. Typically includes a pressure chart to demonstrate satisfactory results | 6.2.2.1, 6.2.2.3 | PDF | CFIHOS-70000287
S714-IR-124 | Hazard Operability Input to HAZOP Report | Input to report summarizing all project HAZOP studies. To include action lists, follow up and close out action descriptions and acceptance. | 6.1.1.1, 6.5.1 | PDF | CFIHOS-70000158
S714-IR-158 | Type test report | The results of test performed to provide evidence that the design meets the requirements of the functional specification (See ISO 13880:1999). When specified, type test will be independently verified by a third part and supported by a Certificate of Conformance. Type test certificates for the following items will be provided: - diesel engine; - generator; - motor; - terminal box; - luminaire; - electric heater; - heat tracing components; - all electrical items included in the package; - all instrumentation items included in the package; - all bulk items. | 5.7.1.1, 5.7.10.1, 5.7.6.3, 5.7.7.1, 5.7.7.5, 5.7.8.7, 5.9.3.3.2, 6.2.3.1 | PDF
S714-IR-189 | Vibration Report | a report documenting vibration and displacement measurements of piping and equipment. | 6.2.3.5.2, 6.2.3.5.3 | PDF | CFIHOS-70000352
S714-IR-208 | Routine test report | Routine test is required to be conducted for all the mechanical, electrical and instrument items in the DG package and report will be submitted. Typically, following will be included: - control panels; - batteries; - battery charger; - light fillings; - mechanical items; - instrument items; - all other bulk items routine tested. | 5.7.10.1, 5.7.10.15, 5.7.10.4, 5.7.10.5, Table 3 | PDF
S714-IR-240 | Motor Performance Test Report | The results of test performed to provide evidence that the design meets the requirements of the functional specification (See ISO 13880:1999). Performance and routine tests in accordance with IEC 60034-1 in table 16. | 6.2.3.3.1 | PDF
S714-IR-35 | Safety Analysis Input To Safety Analysis Report | This document shall provide input to Safety Analysis Report (SAR), and to document acceptable level of SIL according to requirements. This document shall include necessary input to Safety Analysis Report. | 6.1.1.1 | PDF
S714-IR-246 | Dimensional Report | Verification of tolerances Measured real dimensions |  | PDF
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Backcover
Month XXXX
Public Review Draft

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
Intelligent Vector (CAD)
Multi media (Film)
Raster Image (Bitmap)
Structured Data (MS Apps)
Technical Publication (Text)
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: