## Front & Preliminaries
|  |  |  | SPECIFICATION | December
|  |  |  | S-732D | 2020
Data Sheet for
Low Voltage Motor Control Centers
(UL 845)
Revision history
| VERSION | DATE | PURPOSE
| 1 | December 2020 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
Data Sheet for
Low Voltage Motor Control Centers (UL 845)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
Data Sheet for
Low Voltage Motor Control Centers (UL 845)
Introduction
The purpose of this equipment data sheet is to define purchaser specific requirements for the procurement of low voltage motor control center built to UL 845 in accordance with IOGP S-732, for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-732, information requirements specification IOGP S-732L and quality requirements specification IOGP S-732Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet

## Data Sheet
Row |  | S-732D Data Sheet for Low Voltage Motor Control Centers (UL 845) |  |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  |  |  |  | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | Conformity assessment system (CAS) level : | D |  |  |  | Select | A | B | C | D
6 |  | Site conditions
7 | 7.2 a | Ambient air temperature - upper limit : | 40 | °C |  |  | Select | 40 | 45 | 50
8 | 7.2 a | Ambient air temperature - lower limit : | 0 | °C |  |  | Select | 0 | -20 | -30 | -40
9 | 7.2 d | Altitude of installation : | ≤ 1000 | m |  |  | Select | ≤ 1000 | ≤ 2000 | other
10 | 7.2 c | Humidity limit : | < 95 | % |  |  | Select | < 95 | other
11 | 8.1.2.7 | Seismic design : | not required |  |  |  | Select | not required | required
12 | 8.1.2.7 | Site location : | Input Data
13 | 8.1.2.7 | Risk category : | N/A |  |  |  | Select | N/A | I | II | III | IV
14 | 8.1.2.7 | Component importance factor (Ip) : | N/A |  |  |  | Select | N/A | 1 | 1.25 | 1.5
15 | 8.1.2.7 | Site class : | N/A |  |  |  | Select | N/A | A | B | C | D | E | F
16 | 8.1.2.7 | Seismic certificate : | not required |  |  |  | Select | not required | required
17 | 8.1.2 | Location installation : | indoors climate controlled |  |  |  | Select | indoors climate controlled | indoor ventilated | outdoor
18 | 7.3 | Application/operating environment : | onshore |  |  |  | Select | onshore | offshore – fixed | offshore – floating | marine (ship) | other
19 | 8.2.6, 8.2.6.2 | Environmental contamination : | not required |  |  |  | Select | not required | salt-laden | H2S | salt-laden and H2S | other
20 | 1.1.1, 5.1.5, 7.3 | Certification (additional) : | not required |  |  |  | Select | not required | USCG/ABS | other
21 | 8.1.2.8.1, 8.1.2.8.2 | Arc-resistant certification : | 3rd party certified |  |  |  | Select | 3rd party certified | self-declared | N/A
22 |  | Electrical power parameters
23 | 5.1.1 a, 5.1.2 a | Voltage : | 480 | V |  |  | Select | 208 | 480 | 600 | other
24 | 5.1.1 c, 5.1.2 c | Frequency : | 60 | Hz |  |  | Select | 50 | 60 | other
25 | 5.1.1 b, 5.1.2 b | Phase/wire : | 3 phase 3-wire |  |  |  | Select | 3 phase 3-wire | 3-phase 4-wire | 1-phase 2-wire | other
26 | 6.3.14.1, 6.3.14.2 | System grounding : | high resistance |  |  |  | Select | high resistance | solid | ungrounded
27 | 5.4.4 | Available fault current (symmetrical) : | Input Data | kA
28 | 5.4.4 | System X/R ratio : | Input Data
29 | Table 1 | System connection : | wye |  |  |  | Select | wye | delta | other
30 |  | MCC structure
31 | 6.2.3 | Arc resistant construction : | Type 2 |  |  |  | Select | type 2 | not required
32 | 8.1.2.8.4 | Arc plenum : | not required |  |  |  | Select | not required | plenum interior exhaust | plenum exterior exhaust
33 | 6.2.1 b, 8.1.2.1, 8.1.2.3, 8.1.2.4 | NEMA enclosure rating : | type 1 w/ gasket |  |  |  | Select | type 1 w/ gasket | type 12 | type 3R (non walk-in) | other
34 | H.7.1 | Section depth : | 20 inches |  |  |  | Select | 20 inches | 15 inches | other
35 | 8.2.28.3.8.1, 8.2.28.3.8.2 | Vertical wireway width : | standard |  |  |  | Select | standard | wide
36 | 8.2.6 | Enclosure paint color : | manufacturer standard |  |  |  | Select | manufacturer standard | ANSI 61
37 | 8.2.6 | Unit paint color : | manufacturer standard |  |  |  | Select | manufacturer standard | white
38 | 8.2.9.10 | Back-to-back arrangement : | not required |  |  |  | Select | not required | required
39 | 8.2.39.1 | Space heater : | not required |  |  |  | Select | not required | required
40 | 8.2.39.1, 8.2.39.2 | Space heater control : | N/A |  |  |  | Select | N/A | fixed (constant ON) | thermostat | hygrostat
41 | 8.1.2.3, 8.1.2.4 | Outgoing cables : | top |  |  |  | Select | top | bottom
42 |  | Incoming line section
43 | 8.2.34.2, 8.2.34.3 | Cable/bus entry location : | top |  |  |  | Select | top | bottom | transition section
44 | 8.2.18.1, 8.2.19.1 | Service entrance application : | no |  |  |  | Select | no | yes
45 | 5.3.1.1, 8.2.34.2, 8.2.34.3 | Incoming line termination : | Select |  |  |  | Select | circuit breaker | main lugs only | fusible disconnect | bus connection
46 | 8.2.34.5 | Incoming line metering : | not required |  |  |  | Select | not required | required
47 | 8.2.34.1 | Circuit breaker : | not required |  |  |  | Select | not required | required
48 | 8.2.34.1 | Circuit breaker type : | N/A |  |  |  | Select | N/A | MCCB | ICCB | PCB
49 | 8.2.34.1 | Protection type : | N/A |  |  |  | Select | N/A | thermal magnetic | trip unit-LSI | trip unit-LSIG | trip unit-LI
50 | 8.2.34.1 | Arc reducing maintenance switch : | N/A |  |  |  | Select | N/A | required | not required
51 | 8.2.16.2 | Cable entry : | Select |  |  |  | Select | required | not required
52 | 8.2.34.2, 8.2.34.3 | Conductor size : | Input Data | AWG
53 | 8.2.34.2, 8.2.34.3 | Conductor material : | Select |  |  |  | Select | copper | aluminum
54 | 8.2.34.2, 8.2.34.3 | No. conductors per phase : | Select | no. |  |  | Select | 1 | 2 | 3 | 4 | other
55 | 8.2.30.2, 8.2.33.1.1 | Incoming cable grounding conductor size : | Input Data | AWG
56 | 8.2.33.1.1 | No. of incoming cable grounding conductors : | Input Data | no.
57 | 8.2.34.4 | Bus duct entry : | Select |  |  |  | Select | required | not required
58 | 8.2.34.4 | Cable bus entry : | Select |  |  |  | Select | required | not required
59 |  | Bus
60 | 5.1.1 d, 5.1.2 d, 5.3.2 | Horizontal bus rating : | Select | A |  |  | Select | 600 | 800 | 1000 | 1200 | 1600 | 2000 | 2500 | 3000 | 3200
61 | 5.1.1 e, 5.1.2 e, 5.4.1.1, 5.4.1.2 | Power bus bracing : | 42 | kA |  |  | Select | 42 | 65 | 100 | other
62 | 5.3.2.1, 8.2.9.1 | Power bus plating material : | tin |  |  |  | Select | tin | silver | none
63 | 8.2.9.7, 8.2.9.12 | Insulated main horizontal bus : | not required |  |  |  | Select | not required | required
64 | 5.1.1 d, 5.3.3 | Vertical bus rating : | 600 | A |  |  | Select | 300 | 600 | 800 | 1200
65 | 5.1.1 d, 8.2.9.3, 8.2.21.1 | Neutral bus rating : | not required |  |  |  | Select | not required | full | half
66 | 8.2.19.11 | Neutral bus load termination point (location) : | N/A |  |  |  | Select | N/A | all sections | incoming section only
67 | 8.2.33.1.1, 8.2.33.1.3, 8.2.33.1.4, 8.2.33.1.5 | Horizontal ground bus (location) : | bottom |  |  |  | Select | bottom | top
68 | 8.2.33.1.1, 8.2.33.1.2 | Horizontal ground bus rating : | 300 | A |  |  | Select | 300 | 600 | table 24 of UL 845
69 |  | Combination motor controller unit
70 | 8.2.11.16, 8.2.11.17, 8.2.11.18 | Overload relay type : | microprocessor |  |  |  | Select | microprocessor | solid-state | mechanical | multiple types
71 | 8.2.11.17, 8.2.12.3 | Unit disconnect type : | MCP |  |  |  | Select | MCP | MCCB | fused disconnect
72 | 8.2.11.24 | Control power source : | individual unit CPT |  |  |  | Select | individual unit CPT | 24 Vdc power supply | external
73 | 5.2.1 | Control circuit voltage : | 120 VAC |  |  |  | Select | 120 VAC | 24 VDC
74 | 8.2.11.21, 8.2.11.22, 8.2.11.23 | Control power transformer capacity : | standard capacity |  |  |  | Select | extra capacity | standard capacity
75 | 8.2.11.28 | Minimum motor size for space heater : | not required | hp |  |  | Select | not required | ≥5 | ≥10 | ≥20 | ≥50
76 | 8.2.11.8, 8.2.41.1 | Status indicator lights : | run-stopped |  |  |  | Select | not required | run-stopped | run-stopped-trip
77 | 8.2.41.2 | Unit stop pushbutton : | not required |  |  |  | Select | not required | momentary | maintained
78 | 8.2.11.30 | Auto trip reset : | not required |  |  |  | Select | not required | required
79 |  | Accessories
80 | 8.2.11.18, 8.2.34.5 | Application software : | required |  |  |  | Select | required | not required
81 | 8.2.42 | Continuous thermal monitoring : | not required |  |  |  | Select | not required | required
82 | 8.2.42 | Thermal monitoring analytical software : | not required |  |  |  | Select | not required | required
83 | 8.2.4.8 | Thermal scanning inspection windows : | not required |  |  |  | Select | not required | required
84 | 8.2.10.5 | Absence of voltage tester : | not required |  |  |  | Select | not required | incoming line section | each unit | incoming line section and each unit
85 | 8.2.40.1 | Communication protocol : | not required |  |  |  | Select | not required | PROFIBUS | PROFINET | Modbus TCP/IP | EtherNet/IP | DeviceNet | IEC61850 | multiple | other
86 | 8.2.40.1, 8.2.40.2, 8.2.40.3 | Communication system power supply : | N/A |  |  |  | Select | N/A | simplex | redundant | external
87 | 8.3.4 | Undervoltage ridethrough : | not required |  |  |  | Select | not required | required
88 | 8.1.2.8.7 | Arc resistant blank unit (quantity per unit size) : | 1 |  |  |  | Select | not required | 1 | 2 | 3 | other
89 | 8.2.20.1 | Ground fault detection : | not required |  |  |  | Select | not required | phase detection indicators | indicating meter | pulsing system | unit detection
90 | 8.2.2.10 | Ventilation filters : | not required |  |  |  | Select | not required | required
91 |  | Shipping and preservation
92 | H.5.2 | Equipment preservation : | manufacturer standard |  |  |  | Select | manufacturer standard | special
93 | H.5.2 | Provisions for energizing space heaters for storage : | not required |  |  |  | Select | not required | required
94 | H.5.1 | Desiccant bags installed for shipping : | not required |  |  |  | Select | not required | incoming only | each unit
Note on C5: Select conformity assessment level of this equipment. The default selection of CAS level D is typically used for trusted manufacturers that the purchaser has experience with. For CAS level selection guidance, refer to the IOGP S-732Q.
Note on C7: Select the upper limit ambient air temperature measured outside of the enclosure. Default value as per UL 845 is 40 °C with the 24h average not exceeding 35 °C.
Note on C8: Select the lower limit ambient air temperature. Default value as per UL 845 is 0°C.
Note on C9: Select the LV MCC installation altitude. UL 845 is based on the altitude not to exceed 2 000 m (6 600 ft), or 1 000 m (3 300 ft) if the equipment includes solid-state controllers. If 'other' is selected, enter the altitude in the 'Additional notes' column.
Note on C10: Select the humidity limit. As per UL 845, default value measured over 24h not to exceed 95% non-condensing. If 'other' is selected, enter the humidity in the 'Additional notes' column.
Note on C11: Select seismic design requirement as per ASCE/SEI 7-16.
Note on C12: Provide site physical address or latitude and longitude to determine seismic acceleration values
Note on C13: Provide risk category as per ASCE/SEI 7-16 (Risk category of buildings and other structures for flood, wind, snow, earthquake, and Ice loads). Typical oil and gas category is IV.
Note on C14: Provide component importance factor of buildings and other structures for snow, ice, and earthquake loads. Typical oil and gas importance factor is 1.5.
Note on C15: Provide site class as per ASCE/SEI 7-16 (Chapter 20). Site Class D is to be specified if detailed soil properties are not known.
Note on C16: Provide seismic certificate by third party, only if selected on data sheet.
Note on C17: Select installation location of the LV MCC.
Note on C18: Select the operating environment for LV MCC. If 'other' is selected, enter the operating environment in the 'Additional notes' column.
Note on C19: Select any contaminant exposure to the LV MCC. If 'other' is selected, enter the contaminant exposure in the 'Additional notes' column.
Note on C20: Select certification requirements (in addition to NRTL or ACO). If 'other' is selected, enter the additional certification in the 'Additional notes' column.
Note on C21: Select the required certification for arc resistance testing.
Note on C23: Reference UL 845, Table 1. If other is selected, enter the voltage in the 'Additional notes' column.
Note on C24: If other is selected, enter the frequency in the 'Additional notes' column.
Note on C25: If other is selected, enter the phase in the 'Additional notes' column.
Note on C26: Select the grounding system of the facility that the LV MCC will be connected to.
Note on C27: Specify the available fault current (symmetrical) of the system at the LV MCC.
Note on C28: Specify the X/R Ratio (system reactance / system resistance). Higher X/R ratios can result in de-rating of short circuit ratings.
Note on C29: Select the system connection. If 'other' is selected, enter the system connection in the 'Additional notes' column.
Note on C31: Select if LV MCC requires arc resistant construction that is verified through testing for internal arcing faults. Arc resistant Type 2 enclosures provide protection for personnel and improve electrical safety.
Note on C32: Select if an arc plenum for exhaust is required due to the arrangement or configuration of the room or space where the LV MCC is located. A plenum design may not be available from all manufacturers.
Note on C33: Select the NEMA enclosure rating. If 'other' is selected, enter the system connection in the 'Additional notes' column.
Note on C34: Select the section nominal depth: 50 cm (20 in), 40 cm (15 in). The 20 inch depth is preferred to ensure adequate wiring space. If other is selected, enter the required nominal section depth in the 'Additional notes' column.
Note on C35: Vertical wireway widths vary by manufacturer. Typically the standard nominal width is 100 mm (4 in). Consult with manufacturer for the additional widths provided with the "wide" option.
Note on C36: Select the enclosure paint color.
Note on C37: Select the paint color for the unit interior. Units are normally the same color as the enclosure, white can be specified to enhance visibility.
Note on C38: Select if two separate MCC assemblies connected through a transition section are required (back-to-back LV MCC arrangement).
Note on C39: Select if section space heaters are required.
Note on C40: If space heaters are required, specify controls type.
Note on C41: Select the location of the outgoing cables.
Note on C43: Select incoming cable entry location.
Note on C44: Indicate if this LV MCC will be designated as service entrance equipment. Reference Annex G for service entrance requirements
Note on C45: Select the incoming line termination type. Although "main lugs only" may be the most cost effective option, arc resistant designs may require a current limiting breaker or fuse.
Note on C47: Select if main circuit breaker is specifcied. If required, then complete the three lines below.
Note on C48: If circuit breaker is specified, select the type of circuit breaker required. MCCB is the type that is typically supplied. (ICCB-insulated case circuit breaker, PCB-power circuit breaker, MCCB-molded case circuit breaker)
Note on C49: If circuit breaker is specified, select the protection type. Thermal magnetic is the typical protection type for MCCB. LI (long time and instantaneous) is the typical protection type for ICCB and PCB.
Note on C50: Available only with a circuit breaker that is equipped with an integral trip unit.
Note on C51: Select if cable entry is specified. If required, then complete the five lines below.
Note on C52: If cable entry is specified, enter conductor size needed for the incoming service.
Note on C53: If cable entry is specified, enter the conductor material. Copper is typically used.
Note on C54: If cable entry is specified, enter the number of conductors per phase. If 'other' is selected, enter the number of conductors in the 'Additional notes' column.
Note on C55: If cable entry is specified, enter the size of the incoming cable grounding conductor size.
Note on C56: If cable entry is specified, enter the number of the incoming cable grounding conductors.
Note on C57: Select if bus duct entry is specified. If required, then the manufacturer of the LV MCC will need to be provided the details of the bus duct (ampacity, size, dimensions, no. of bus bars, etc.).
Note on C58: Select if cable bus entry is specified. If required, then the manufacturer of the LV MCC will need to be provided the details of the cable duct (ampacity, size, dimensions, no. of cables, etc.).
Note on C60: Select the main bus rating. For 2500 A and above, arc resistance may not be available.
Note on C61: Select the power bus short-circuit current rating. For 'other' ratings reference UL 845, Table 2 and indicate the value in the 'Additional notes' column.
Note on C62: Select the bus plating material. If none is selected, the ampacity and temperature rise will be affected. Tin is preferred over silver in corrosive gas applications.
Note on C63: Select the main bus insulation requirement. Insulated main horizontal bus with insulated shipping split connections provides a higher degree of electrical safety and ingress protection.
Note on C64: Select the vertical bus rating. This will be the value for all vertical buses in the MCC assembly.
Note on C65: Select the neutral bus rating. When a neutral bus is required a full size neutral is recommended.
Note on C66: Select the location(s) where the neutral from outgoing load feeder cables will be connected in the MCC assembly. The selection of "incoming section" will require the load neutral feeder wire to routed to the incoming section for connection.
Note on C67: Select the ground bus location. The entry location of the incoming field wiring should be considered when selecting the location of the ground bus.
Note on C68: Select the horizontal ground bus rating for values different than 300 A and 600 A, see Tables 24 and 25 of UL 845.
Note on C70: Select the overload relay type. For multiple types, use the "supplement" tab or project drawings to provide additional information.
Note on C71: Select the unit disconnect type. If fused disconnect is selected then this type disconnect is normally provided for all units (motor controllers, feeders, contactors, etc.).
Note on C72: Select the control power source. The voltage level for control power should not exceed 120 V nominal.
Note on C73: Select the control power voltage.
Note on C74: Select the CPT capacity. If extra capacity is selected, 50VA additional capacity is included in the sizing as per the supplementary specification.
Note on C75: Select the minimum size motor for which provisions for motor space heater control is required. These motor sizes are provided to promote standardization. Other requirements can be detailed in the "Additional notes" column.
Note on C76: Select the indicator lights requirements. Additional status indicator lights can be specified on the project drawings or in the "additional notes" column, but will reduce standardization.
Note on C77: Select the requirement to add a stop pushbutton installed on the door (device panel) of each combination motor controller unit.
Note on C78: Select the requirement for auto-trip-reset capability.
Note on C80: Select if the application software for configuration of digital programmable devices is required. Provide specific requirements in the "Additional notes" column. This includes any nonstandard interface cables but does not include any computer hardware.
Note on C82: Select if thermal monitoring analytical software is required. This includes any nonstandard interface cables but does not include any computer hardware.
Note on C83: Select the requirement for thermal scanning inspection windows. Manufacturer to indicate recommended location.
Note on C84: Select the requirement and location for absence of voltage tester devices. The installation of these devices in each unit can be used to establish an electrically safe work condition and assist with LOTO procedures. Refer to the requirements in NFPA 70E.
Note on C85: Select the communication protocol. Depending on the selection, additional information regarding the physical layer may be required. If 'multiple' or 'other' is selected, provide details in the "Additional note" column and in the project drawings.
Note on C86: Select the requirement for the communication system power supply. This selection is to indicate the level of desired redundancy.
Note on C87: Select if undervoltage ridethrough is required. Manufacturer to provide voltage and time parameters for each starter size.
Note on C88: Select the number of blanks per unit size. If 'other' is selected, use the "Additional notes" column for details. The blank unit is used to maintain the arc resistant rating of the MCC when a unit is removed for maintenance.
Note on C89: The selections for 'phase indicators', 'meter', and 'pulsing' are for the incoming section only. The selection for 'unit detection' allows for identifying which unit has a ground fault.
Note on C90: Select the requirement for ventilation filters.
Note on C92: Select the equipment preservation requirement. Manufacturer standard shipping is appropriate for domestic shipping (not offshore) and indoor storage. If 'special' is selected, use 'Additional note' column or 'Supplement' tab for additional details.
Note on C93: Select the requirement for energizing space heater for storage. If required, the preservation packaging will allow for access to the space heater connections without compromising the preservation integrity.
Note on C94: Select the requirements for desiccant bags for shipping.

## Supplement
Row |  | S-732D Data Sheet for Low Voltage Motor Control Centers (UL 845) | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95

## Guidance
Data Sheet for
Low Voltage Motor Control Centers (UL 845)
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-732 Supplementary Specification to UL 845 Low Voltage Motor Control Centers.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.