## Errata 1
Date of issue:
August 2022
Affected publication:
IOGP S-732L, Information Requirements for Low Voltage Motor Control Centers (UL 845), First Edition, December 2020
ERRATA 1
Drop-down list choices corrected as follows in worksheet Requirement, column F Purpose excluding cell F18.
List of cells affected
F19, F20, F21, F22, F23, F24, F25, F26, F27, F29, F30, F31, F32, F33, F34, F35, F36, F37, F38, F39, F40, F41, F42, F43, F44, F45, F46, F47, F48, F49, F50, F51, F52 and F53.

## Front & Preliminaries
|  |  |  | SPECIFICATION | August 2022
|  |  |  | IOGP S-732L | Version 1.01
FIRST EDITION (DECEMBER 2020), ERRATA 1
Information Requirements for
Low Voltage Motor Control Centers
(UL 845)
Revision history
| VERSION | DATE | PURPOSE
| 1.01 | August 2022 | Errata 1
| 1.01 | December 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-732L Information Requirements for
Low Voltage Motor Control Centers (UL 845)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
S-732L Information Requirements for
Low Voltage Motor Control Centers (UL 845)
Introduction
The purpose of this information requirements specification (IRS) is to define Information requirements for the procurement of low voltage motor control centers built to UL 845 in accordance with IOGP S-732 for application in the petroleum and natural gas industries. This document defines the information requirements, including format, timing and purpose, for information to be provided by the manufacturer. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the supplementary requirements specification IOGP S-732, quality requirements specification IOGP S-732Q and equipment data sheet IOGP S-732D which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification

## Supplier Instructions
S-732L Information Requirements for
Low Voltage Motor Control Centers (UL 845)
Supplier Instructions
In response to Invitation To Tender (ITT)
Tenderers to submit information as defined in column E - 'Submit At Proposal' in 'Requirements' sheet, in accordance with ITT instructions
On award of contract
Specified Information requirements shall be submitted in accordance with contract information submission instructions. Suppliers to prepare and submit 'Supplier Master Information Schedule' (SMIS) incorporating information requirements in accordance with columns F - 'First Issue Post Purchase Order' in 'Requirements' sheet. Supplier to demonstrate compliance with each information requirement either by providing document number cross reference to the Requirement in 'Supplier Master Information Schedule' (SMIS) and, if specified in the Contract, using column J 'Fulfilled by Document Number(s)' in the IRS Requirements Sheet.
On completion of scope
Supplier to validate that the information delivered meets the IRS requirements either through cross reference to the deliverable type in a as-built version of the 'Supplier Master Information Schedule' SMIS and, if specified in the Contract, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in Requirement sheet populated with the specific document numbers issued to the Purchaser.
IRS Structure Contents
1 |  | 'Front & Preliminaries' Tab
The 'Front & Preliminaries ' tab includes an IOGP Front sheet for the IRS followed by Acknowledgements, a Disclaimer, Copyright Notice, Foreword and Introduction
2 |  | 'Supplier Instructions' Tab
This 'Supplier Instructions' tab provides instructions that Suppliers are to follow in response to this IRS.
3 |  | 'Requirements' Tab
The 'Requirements' tab lists the suite of information requirements that are to be supplied during tendering and following award of the purchase order to deliver the purchase order scope. The information requirements are grouped under three broad categories; Management information requirements: Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. Technical information requirements: Technical information developed by the supplier or their sub suppliers, during the design and development, acquisition, manufacture, assembly and testing of the contracted scope. Purchase Order Specific Information Requirements: Information requirements specified by individual owners-operators in addition to those specified by IOGP-JIP33 to meet specific operational, project or legislative requirements. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. "The 'Requirements' tab includes columns A to L, including Column A for the relevant requirement code and Column B for the Requirement for the different Information Requirements (Data, Documents and/or Models) to be provided by suppliers, based on the parent standard, IOGP Specification or the specified parent industry Standard. Condition Invoking Revoking Requirement Column C is included to allow any specific conditions to be identified that may require a additional deliverable(s). Typical Deliverable Column D is provided for Purchaser to identify the deliverable type that the information would typically appear within; this also allows the Purchaser's Requisitioning Engineers to group the various Information Requirements by Deliverable Type. Column E includes Submission Requirements (Yes or No) at Proposal, while columns F, G & H identify Issue Purpose (For Information or For Acceptance) and Durations (Period or Weeks/Months) for First Issue of the particular deliverable Post Purchase Order. Required As Built, Fulfilled by Document Number(s), Translation Required and Remarks columns I, J, K & L are also included. Definitions for each column are contained in the rows above the columns: Abbreviations used for various submission requirements in Column H are shown in table 3.1 below:
Table 3.1 - Information Submission Abbreviations
4 |  | 'Definitions' Tab
The 'Definitions' tab includes several columns A to F, including Column A for the relevant Code & Column B for the Requirement for the different Information (Data, Documents and/or Models) Requirements to be provided by Suppliers, all copied from the 'Requirements' tab. Column C includes a full description of the Information Requirement based on the Parent Standard, IOGP Specification or an Industry Standard. Column D gives a reference to the Parent Standard, IOGP Specification or an Industry Standard that the Information requirement is identified in. Column E identifies the Requirement format as listed in Table 9.1 below. Column F relates the CFIHOS discipline document type that could be used to classify the document having this IRS content. Definitions for each column are contained in the rows above the columns:
5 |  | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various tabs of this workbook.
Buyer |  |  | Organisation placing a Contract or Purchase Order with Supplier for equipment or services on project; may be alternatively referred to as 'User' or 'Purchaser'
CFIHOS |  |  | Capital Facilities Information Hand Over Specification
Company |  |  | Project Operating Entity or the organisation Contractor is under contract to
Contractor |  |  | Project Contractor responsible for procuring equipment.
Information |  |  | Data, Documents and/or Models
IRS |  |  | Information Requirements Specification
PO |  |  | Purchase Order
QRS |  |  | Quality Requirements Specification
SMIS |  |  | Supplier Master Information Schedule
Supplier |  |  | Organization manufacturing and/or supplying equipment or services to Company and/or Contractor on project; may alternatively be referred to as "Vendor", "Seller" or “Manufacturer”.
6 |  | CFIHOS
The Information Requirements are also classified according to document classification published in v1.4 of Capital Facilities Information Hand Over Specification (CFIHOS). The objective of CFIHOS is to create a common information standards across the process industries. Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org/about/
7 |  | Document Metadata
Typical Metadata for Information Deliverables to be provided by Suppliers is shown in Table 7.1 below
Table 7.1 - Supplier Deliverable Metadata
8 |  | Deliverable Formats
The format of the relevant Information Deliverable to be submitted by Supplier for Buyer/Contractor is to be as described in table 8.1 below. Where required to be ‘As Built’, deliverables are to be updated and handed over in the native format.
Table 8.1 – Deliverable Formats

## Requirements
S-732L Information Requirements for Low Voltage Motor Control Centers (UL 845)
Requirements
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement based on the description in the Parent Standard, IOGP Specification or an Industry Standard Information Requirement Title.
C | Condition Invoking Requirement - describes special condition(s) under which the Information Requirement is required; e.g.. service offshore and weight greater than 1 tonne means information is required. NB: if blank, always required
D | Typical Deliverable - Purchaser to advise the short description of the Information Deliverable that would typically include this Information Requirement
E | Submit With Proposal - Yes or No, where 'Yes' means the Information Requirement is required to be submitted with Suppliers Proposal or 'No' is not required
F, G & H | First Issue Post Purchase Order - issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the Information Requirement and Period defined after Purchase Order placement.
I | Required As Built - Yes or No, where 'Yes' means the Information Requirement is required to be 'As Built' on completion or delivery of equipment or 'No' is not required 'As Built'
J | Fulfilled by Information Deliverable Number(s) - identifies which Information Requirement(s) listed in the Supplier Master Information Schedule (SMIS) addresses the Purchasers requirements. NB: it should be noted that one Information Deliverable can fulfil more than one Information Requirement.
K | Translation Required -Yes or No, where 'Yes' means the Information Requirement should be translated into a language(s) (to be advised) other than English and 'No' means to be provided in English
L | Remarks - may include bid clarification questions & decisions (specify author & date)
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S732-IR-1 | Supplier master information schedule |  | Information Deliverables List | No | For Acceptance |  | WAO | Yes |  | No
S732-IR-2 | Delivery schedule |  | Delivery/Production Schedule | Yes | For Information |  | WAO | No |  | No
S732-IR-3 | Progress report |  | Progress Report | No | For Information |  | WAO (Monthly) | No |  | No
S732-IR-4 | Quality plan | Required for CAS A and B | Quality Plan | - | - |  | - | - |  | -
S732-IR-5 | Sub-vendor delivery schedule | Required for CAS A and B | Sub-Supplier List | - | - |  | - | - |  | -
S732-IR-6 | Inspection and test plan for complete package |  | Inspection and Test Plan (ITP) | No | For Information |  | WAO | No |  | No
S732-IR-7 | Handling, lifting, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No |  | No
S732-IR-8 | Non-conformance records |  | Nonconformance History | No | For Acceptance |  | WAO | Yes |  | No
S732-IR-9 | Concession requests |  | Concession request | Yes | For Acceptance |  | WAO | Yes |  | No
S732-IR-55 | Pre-production planning (minutes of meeting) | Required for CAS A, B and C | Minutes of meeting | - | - |  | - | - |  | -
Technical Information Deliverables
S732-IR-20 | Wiring Diagram |  | Wiring Diagram | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732-IR-22 | Single Line Diagram |  | Single Line Diagram | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732-IR-23 | Schematic Diagram |  | Schematic Diagram | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732-IR-24 | Name Plate Drawing |  | Name Plate Drawing | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732-IR-25 | General Arrangement Diagram |  | General Arrangement Diagram | Yes | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732-IR-27 | Detailed Drawing |  | Detailed Drawing | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732-IR-52 | Equipment Specification Sheet |  | Equipment Specification | No | For Acceptance |  | WAO | Yes |  | No | Part of the drawing submittal package.
S732-IR-28 | Communication Block Diagram |  | Block Diagram | Yes | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732-IR-30 | Cable Size Calculation | Required for CAS A and B | Cable Size Calculation | - | - |  | - | - |  | -
S732-IR-31 | Heat Dissipation Calculation & Loads |  | Heat Dissipation Calculation & Loads | No | For Information |  | WAO | No |  | No
S732-IR-32 | Reliability & Availability Calculations and Obsolescence Plan | Required for CAS A, B and C | Reliability, Availability, Safety Integrity Level Calculation | - | - |  | - | - |  | -
S732-IR-33 | Certificate Of Conformance |  | Certificate Of Conformance | Yes | For Information |  | WAO | Yes |  | No | UL 845 listing and Arc Resistance certifications
S732-IR-51 | Type Test Certificate of Conformance | Required for CAS A and B | Certificate of Conformance | - | - |  | - | - |  | -
S732-IR-34 | Regulatory Compliance Certificate |  | Regulatory Compliance Certificate | No | For Information |  | WAO | Yes |  | No
S732-IR-35 | Application Software |  | Application Software | No | For Information |  | WAO | Yes |  | No | Only when required by the datasheet.
S732-IR-36 | Bill Of Materials |  | Bill Of Materials | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings
S732-IR-39 | Spare Part List |  | Spare Part List | No | For Information |  | WAO | Yes |  | No
S732-IR-41 | Commissioning Instruction |  | Commissioning Instruction | No | For Information |  | WAO | Yes |  | No
S732-IR-42 | Installation Manual |  | Installation Manual | No | For Information |  | WAO | No |  | No | Installation Manual index, if required, should be provided in first revision of the document. When index agreed, Installation manual content shall be provided in subsequent revision of the document.
S732-IR-43 | Maintenance Manual |  | Maintenance Manual | No | For Information |  | WAO | No |  | No | Maintenance Manual index, if required, should be provided in first revision of the document. When index agreed, Maintenance manual content shall be provided in subsequent revision of the document.
S732-IR-44 | Operating Manual |  | Operating Manual | No | For Information |  | WAO | No |  | No | Operating Manual index, if required, should be provided in first revision of the document. When index agreed, Operating manual content shall be provided in subsequent revision of the document.
S732-IR-47 | Factory Acceptance Test (FAT) Procedure |  | Factory Acceptance Test (FAT) Procedure | No | For Acceptance |  | WPTT | No |  | No
S732-IR-49 | Routine test procedure |  | Routine test procedure | No | For Information |  | WPTT | Yes |  | No
S732-IR-50 | Factory Acceptance Test (FAT) Records |  | Factory Acceptance Test (FAT) Records | No | For Information |  | WAT | No |  | No
S732-IR-54 | Packing List |  | Packing List | No | For Information |  | WPTD | No |  | No
Purchase Order Specific Information Requirements

## Definitions
S-732L Information Requirements for Low Voltage Motor Control Centers (UL 845)
Definitions
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement that would typically provide the Information required, based on the description in the Parent Standard, IOGP Specification or an Industry Standard Title.
C | Description - an excerpt from the Parent Standard, IOGP Specification or Industry Standard.
D | Reference - reference to the Parent Standard, IOGP Specification or Industry Standard that the Information Deliverable is identified in.
E | Format - defines the required format of the relevant Information Requirement to be submitted by Supplier for Purchaser/Contractor for information and acceptance as shown in Table 9.1 of Instructions Tab and selected from pick list.
F | CFIHOS Discipline Document Type Code - the CFIHOS discipline document type that could be used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Deliverables
S732-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the Supplier and accepted by the Purchaser to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description, b. unique identification (code/number) in the Supplier's format unless agreed otherwise in the contract, c. planned submission arrangements including; purpose, formats, timing, frequency. Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. | (IOGP S-732 Annex H) | Native | CFIHOS-70000099
S732-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by supplier/sub-supplier. Schedule details typically include: a. Contractual milestones, b. Activity early/late start/completion dates, durations, dependencies (Calendar Dates), c. Critical path and float, d. Outsourced services and equipment (cross referenced to purchase order and supplier), e. Information deliverable submission dates identifying any execution activity dependencies. Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. NOTE: Schedule development tools, formats and submission protocols follow the supplier's standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S732-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. NOTE: The frequency and scope of the progress report may also be modified by the terms and conditions in the purchase order |  | PDF | CFIHOS-70000300
S732-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] |  | PDF
S732-IR-5 | Sub-vendor delivery schedule | Definition of processes, products or services that will be externally provided and the controls to be applied by the supplier to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . NOTE: ISO 9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. |  | Native
S732-IR-6 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated supplier, purchaser and independent party conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. | (IOGP S-732, 9.21, H.6.2) | PDF | CFIHOS-70000180
S732-IR-7 | Handling, lifting, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container(s), b. special packing/unpacking/handling and lifting requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning, e. drawings shall be provided indicating size of shipping splits, center of gravity, weight, identification, and packing list of contents. NOTE: Copies of applicable lifting procedures are included in the delivery documentation which accompanies shipments of equipment. | (IOGP S-732, 8.1.2.6, H.4.3, H.5.2) | PDF | CFIHOS-70000154
S732-IR-8 | Non-conformance records | Details of non-conformances raised by or to the supplier/sub-suppliers against technical requirements during manufacturing prior to or during the delivery of the products or services. Non-conformance is managed by the supplier in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. NOTE: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the purchaser in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S732-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000389
S732-IR-55 | Pre-production planning (minutes of meeting) | Minutes of meeting from a pre-production planning. Items to be covered during this meeting includes ITP, point of contact for supplier and third party inspection company, overall quality process, and inspection schedule. |  | PDF | CFIHOS-70000223
Technical Information Deliverables
S732-IR-20 | Wiring Diagram | Diagram providing information on the circuitry of an object. Mandatory content of information: a. graphical symbols representing the objects; b. graphical symbols representing the connections among objects; c. reference designations; d. terminal designations; e. signal level conventions (applicable to logic signals); f. information necessary to trace paths and circuits (signal designations, location references); g. supplementary information necessary for the understanding of functions; h. point to point wiring details. Optional content of information: Technical data; Reference to other documents; Information about wiring performance; Cable and cable core identification. | (IOGP S-732, 5.1.3, 5.2.1, 5.2.2, 6.2.1, 6.2.2, 6.3.64, 6.3.65, 8.2.11.17, 8.2.11.19, 8.2.11.26, 8.2.11.28, 8.2.11.30, 8.2.13.18 to 8.2.13.22, 8.2.18, 8.2.19, 8.2.19.1, 8.2.19.6, 8.2.19.10 to 8.2.19.14, 8.2.31.1, 8.2.35.3, 8.2.39, 8.2.42) | Native | CFIHOS-70000268
S732-IR-22 | Single Line Diagram | A diagram depicting the major equipment items (motors, switchboards, transformers etc.) and their relationships within the facility electrical distribution system including details of fault levels, current ratings, fixed or withdrawable equipment unit type, and voltage ratings. | (IOGP S-732, 5.1.3, 5.1.4, 5.3.2.2, 5.3.3, 5.4.1.4, 5.4.4, 6.2.1, 6.2.2, 6.4, 8.2.11.10, 8.2.11.11, 8.2.11.20, 8.2.12.1, 8.2.18, 8.2.19, 8.2.34 to 8.2.38) | Native | CFIHOS-70000371
S732-IR-23 | Schematic Diagram | A pictorial representation of the main elements and functions of a control circuit for electrical equipment with input/output sources (switches, relays etc.) and their relationships, details logic functions of the circuit and individual schematics for each unit type and designation. | (IOGP S-732, 5.1.3, 5.2.1, 5.2.2, 8.2.11.17 f, 8.2.11.25, 8.2.11.26, 8.2.11.28, 8.2.11.30, 8.2.13.18 to 8.2.13.22, 8.2.18, 8.2.19, 8.2.19.10 to 8.2.19.14, 8.2.34 to 8.2.36) | Native | CFIHOS-70000328
S732-IR-24 | Name Plate Drawing | A drawing that depicts the layout, font size, and lettering information for the identification of equipment tag names that will be illustrated on nameplates that will be installed on the individual equipment items. This would include the material of the nameplate and fastening method. | (IOGP S-732, 5.1.3, 6.1, 6.1.1, 6.2.2 f, 6.3.63 to 6.3.65, 8.2.37, 8.2.38) | Native
S732-IR-25 | General Arrangement Diagram | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing shall contain reference to main specifications and standards For equipment / components the drawing may include cross sectional views. Document may contain the following information: a. main dimensions, b. interface connections, c. weight, d. center of gravity, e. withdrawal/installation and maintenance space, f. installation and mounting details, g. lifting arrangement, h. shipping split details, i. elevation views. | (IOGP S-732, 5.1.3, 6.1b, 6.1.1, 6.3.64, 6.3.65, 8.1.2.6, 8.2.4.6, 8.2.6.2, 8.2.9.1, 8.2.9.5, 8.2.9.6, 8.2.9.7, 8.2.9.11, 8.2.9.12, 8.2.11.10 to 8.2.11.13, 8.2.12, 8.2.18, 8.2.19, 8.2.33.1, 8.2.33.7, 8.2.33.8, 8.2.34, 8.2.35.3, 8.2.36.1, 8.2.37 to 8.2.39, 8.2.41, 8.2.42 ) | Native | CFIHOS-70000153
S732-IR-27 | Detailed Drawing | Drawing or detail illustrating parts of a construction or a component, generally enlarged, and including specific information about the form and construction or about the assembly and joints. Also supports other documents where a cross-sectional view, side view or part list is necessary for clarity. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. These details may be part of another drawing or included in a document. The details necessary include: bus bar splices or connections, bus bar torqueing requirements, cable termination hole patterns, cable gland plate locations, floor mounting details including hold down bolt locations and sizes, side views of bus duct and cable bus connections, views for ventilation covers or filter locations, arc resistance construction installation details (space above, cable entry, plenum requirements), other details for regulatory compliance certificates (tilt and roll requirements, drip shield, hand rails, guard rails, seismic installation details). | (IOGP S-732, 5.1.3, 8.2.10.6, 8.2.11.28, 8.2.13.21, 8.2.16.9 to 8.2.16.11, 8.2.28.3.8, 8.2.28.3.9, 8.2.33.1, 8.2.33.7, 8.2.33.8, 8.2.9.5, 8.2.9.8) | Native | CFIHOS-70000116
S732-IR-52 | Equipment Specification Sheet | A specification or drawing that describes the physical equipment and technical details for the purpose of procurement or fabrication. It Compliments the datasheet. This includes, but is not limited to, details such as: a. all busing details including ratings, plating, and insulation requirements; b. space heater requirements; c. incoming and outgoing cable requirements; d. shipping split arrangements; e. voltage and current ratings including ambient conditions; f. specific application requirements (arc resistance construction features, marine/offshore, regulatory, etc.); g. incomer type and details; h. metering, protective relaying, and overload type details; i. communication, networking, and CBM requirements; k. dimensional data needed to perform arc flash incident energy calculations (IEEE1584): between each phase of the horizontal bus; between each phase of the vertical bus; between each phase of conductors terminating on the line side of the unit overcurrent protection devices (for each rating provided); size of the unit (this can be the smallest unit provided). | (IOGP S-732, 5.1.4, 5.3.2.1, 6.2, 6.3.36.1, 6.4, 8.1.2.5, 8.1.2.7, 8.1.2.8, 8.1.7.2, 8.1.9, 8.2.2.10, 8.2.4.6, 8.2.4.8, 8.2.6.1, 8.2.6.2, 8.2.8.2, 8.2.9.1, 8.2.9.7, 8.2.9.11, 8.2.9.12, 8.2.10.4 to 8.2.10.6, 8.2.11.12 to 8.2.11.15, 8.2.11.18, 8.2.11.20, 8.2.11.29, 8.2.11.30, 8.2.12, 8.2.13.1, 8.2.13.4, 8.2.33.1.1, 8.2.33.1.2, 8.2.33.7, 8.2.33.8, 8.2.34, 8.2.35.1, 8.2.35.2, 8.2.36 TO 8.2.39, 8.2.41, 8.2.42, Annex H.5.1) | PDF | CFIHOS-70000399
S732-IR-28 | Communication Block Diagram | The block diagram depicts the interconnected networks, cables and connections. Mandatory content of information includes: a. direction of main interfaces between communication equipment items; b. denomination of incoming and outgoing communication circuits; c. communication protocol designations and details (e.g. routers, hubs, ports, switches). | (IOGP S-732, 5.1.3, 8.2.40.1, 8.2.42) | Native | CFIHOS-70000237
S732-IR-30 | Cable Size Calculation | Calculations required for sizing of power cables internal to the MCC (e.g. cable connections from incoming breaker to main bus, internal transformer feed, transition section, etc.). This would be required if a temperature rise test for the specific application is not available. | (IOGP S-732, 8.2.34) | Native | CFIHOS-70000034
S732-IR-31 | Heat Dissipation Calculation & Loads | This document contains the calculation by the supplier to arrive at the heat load produced by the MCC to enable HVAC sizing and includes load factors and type of load provided to the supplier to produce accurate calculation. | (IOGP S-732, 8.2.36, 8.2.37, 8.2.38) | PDF
S732-IR-32 | Reliability & Availability Calculations and Obsolescence Plan | Demonstrates starting and operating reliability / availability of purchased equipment (e.g. mean time between failure data) calculations. This also provides details of the equipment obsolescence plan. | (IOGP S-732, 4.3.1, 4.4) | PDF | CFIHOS-70000312
S732-IR-33 | Certificate Of Conformance | A statement of conformity where attestation is performed by the person or body that is independent of the person or organization that provides the object, and of user interests in that object (third party). This includes the UL 845 certification (listing mark). | (IOGP S-732, 5.1.5, 6.2.3, 7.3, 8.1.2.7, 8.1.2.8, 8.2.4.8, 8.2.10.5) | PDF | CFIHOS-70000013
S732-IR-51 | Type Test Certificate of Conformance | The results of test performed to provide evidence that the design meets the arc resistance construction requirements of IEEE C37.20.7-2017, including the methodology used to achieve the arc resistant rating. When specified, type test shall be independently verified by a third part and supported by a Certificate of Conformance. This may also be included in the UL 845 certificate of conformance. NOTE: UL witnessing of the supplier's arc resistance tests does not satisfy this requirement. | (IOGP S-732, 5.1.4, 6.2.3, 8.1.2.8, 8.2.4.8) | PDF | CFIHOS-70000013
S732-IR-34 | Regulatory Compliance Certificate | A document certifying conformity to local regulations which accompanies shipment of equipment and/or goods. e.g., Official certificate issued by OEM/Supplier or approved licensed agent of OEM/Supplier. This would include USCG, ABS, or DNV type certifications or similar designations. | (IOGP S-732, 7.3, 8.2.18, 8.2.19) | PDF | CFIHOS-70000079
S732-IR-35 | Application Software | A computer program designed for a specific task or use including configuration, monitoring, diagnostics, and operations of control, protective, and communication devices within the MCC. Examples include ASDs, soft starters, trip units, condition based monitoring, metering devices and microprocessor overload relays. | (IOGP S-732, 8.2.36, 8.2.42) | Native | CFIHOS-70000012
S732-IR-36 | Bill Of Materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and references to specifications. NOTE: When agreed, it includes details of sub-suppliers. | (IOGP S-732, 6.3.64, 6.3.65, 6.4, 8.2.2.10, 8.2.4.8, 8.2.6.2, 8.2.9.1, 8.2.9.7, 8.2.9.11, 8.2.9.12, 8.2.10.5, 8.2.11.18, 8.2.11.20, 8.2.11.25, 8.2.11.26, 8.2.11.30, 8.2.16.1, 8.2.18, 8.2.19, 8.2.34 TO 8.2.39, 8.2.40.1, 8.2.41, 8.2.42) | Native | CFIHOS-70000028
S732-IR-39 | Spare Part List | Table containing list items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for later use. Mandatory content of information: a. item reference number (BOM); b. quantity; c. part number; d. part name. | (IOGP S-732, 8.2.11.18, 8.2.34, 8.2.34.1, 8.2.35.1, 8.2.35.2, 8.2.36 to 8.2.42) | PDF | CFIHOS-70000374
S732-IR-41 | Commissioning Instruction | Instruction providing information on the commissioning of the product. Instructions for commissioning are provided especially for large and highly complex products and for large industrial installations. The purpose of such instructions is to provide the user with the information needed for initial setting-up of the product. Mandatory content of information: These instructions should contain' for example: • download program, software instructions ; • checks to be performed before connection to the supply network and before first operation; NOTE: Unless otherwise agreed, can be delivered as part of supplier's standard Installation, operation and maintenance manual or as a stand alone document | (IOGP S-732, 8.2.9.1, 8.2.9.7, 8.2.9.11, 8.2.9.12, 8.2.10.5, 8.2.11.18, 8.2.18, 8.2.19, 8.2.36) | PDF
S732-IR-42 | Installation Manual | Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. NOTE: Unless otherwise agreed, can be delivered as part of supplier's standard Installation, operation and maintenance manual or as a stand alone document. | (IOGP S-732, 8.1.2.5, 8.1.2.8.3, 8.1.2.8.5, 8.1.2.8.6, 8.1.7.2, 8.1.9, 8.2.4.6, 8.2.9.1, 8.2.9.5, 8.2.9.7, 8.2.9.9, 8.2.9.11, 8.2.9.12, 8.2.10.4, 8.2.10.6, 8.2.11.29, 8.2.16.9 to 8.2.16.11, 8.2.18, 8.2.19, 8.2.28.3.8, 8.2.28.3.9, 8.2.33.1.4, H.4.3, H.5.1, H.6.1 | PDF | CFIHOS-70000181
S732-IR-43 | Maintenance Manual | Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package supplier. NOTE: Unless otherwise agreed, can be delivered as part of supplier's standard Installation, operation and maintenance manual or as a stand alone document. | (IOGP S-732, 4.3.2, 8.1.2.8.6, 8.1.7.2, 8.1.9, 8.2.2.10, 8.2.4.6, 8.2.9.1, 8.2.9.7, 8.2.9.9, 8.2.9.11, 8.2.9.12, 8.2.34, 8.2.35.1, 8.2.35.2, 8.2.36 to 8.2.39, 8.2.41, 8.2.42, H.4.3, H.5.1) | PDF | CFIHOS-70000206
S732-IR-44 | Operating Manual | Description of methods of operating a piece of equipment or process unit, including but not limited to instructions, procedures, drawings, tables, etc. for the operation - energization, switching and isolation. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. This normally includes the cut sheets and technical specification details for the components supplied as part of the MCC assembly. This would also include time current curves (TCC) for the protective devices that can be utilized in the electrical protection coordination studies by others. NOTE: Unless otherwise agreed, can be delivered as part of supplier's standard installation, operation and maintenance manual or as a stand alone document. | (IOGP S-732, 8.2.2.10, 8.2.10.4, 8.2.10.5, 8.2.11.18, 8.2.35.3, 8.2.36, H.4.3, H.5.1) | PDF | CFIHOS-70000228
S732-IR-47 | Factory Acceptance Test (FAT) Procedure | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document shall include all testing activities and their acceptance criteria according to applicable standards, specifications and requirements,. to document the condition of the equipment as tested from factory. Test set-up and test equipment is shall be defined. Suppliers standard (routine) test procedures should be used as far as possible. This will include all the functional tests as specific in the technical specification. | (IOGP S-732, 5.2.2, 8.2.11.17 f, 8.2.11.28, 8.2.35.3, 9.21, H.6.2) | PDF
S732-IR-49 | Routine test procedure | Procedure documenting the supplier's recommended testing activities and acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Procedure to define test set-up and test equipment. | (IOGP S-732 9.21, F.2) | PDF
S732-IR-50 | Factory Acceptance Test (FAT) Records | The FAT report will be used to verify that the equipment has been tested according to FAT procedure. The FAT report will be used for acceptance of the equipment delivery This document shall include all testing activities and their acceptance criteria according with the FAT procedure, to applicable standards, specifications and requirements to document the condition of the equipment as tested from factory. Test set-up and test equipment shall be defined. All equipment that was disconnected to facilitate the AC withstand testing (Annex F.2) and reconnected afterwards shall be documented in the FAT report. | (IOGP S-732, 5.2.2, 6.3.36.1 8.2.11.17 f, 8.2.11.28, 8.2.35.3, 8.2.40.1, 9.21, F.2, H.6.2) | PDF
S732-IR-54 | Packing List | A detailed list of the equipment being packaged and shipped. | (IOGP S-732, H.5.1, H.5.2) | PDF | CFIHOS-70000269
S732-IR-21 | Three Line Diagram [Delete] | A diagram depicting each line (each phase) including the neutral, if applicable (e.g., positive, negative, and ground on a DC System) describing an electrical system. This would include any auxiliary and external control power sources; example: the connection of a pump its control station and the MCC. | (IOGP S-732, 5.1.3, 5.3.2.2, 5.3.3, 5.4.1.4, 5.4.4, 6.2.1, 6.2.2, 6.3.64, 6.3.65, 6.4, 8.2.12.1, 8.2.18, 8.2.19, 8.2.33.1.1, 8.2.33.1.2, 8.2.33.7, 8.2.33.8, 8.2.34, 8.2.35.1, 8.2.35.2, 8.2.36, 8.2.37, 8.2.38) | Native | CFIHOS-70000410
Purchase Order Specific Information Requirements

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
Intelligent Vector (CAD)
Multi media (Film)
Raster Image (Bitmap)
Structured Data (MS Apps)
Technical Publication (Text)
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: