## Front & Preliminaries
|  |  |  | SPECIFICATION | January
|  |  |  | S-736D | 2021
Data Sheet for
Low Voltage AC Drives (IEC)
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | January 2021 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
Data Sheet for
Low Voltage AC Drives (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
Data Sheet for
Low Voltage AC Drives (IEC)
Introduction
The purpose of this equipment data sheet is to define customer specific requirements for the procurement of low voltage AC drives in accordance with IOGP S-736 for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the customer to define an application specific requirement. It also includes information required by the customer for technical evaluation purposes. Additional customer supplied documents are also listed in the data sheet, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-736, information requirements specification IOGP S-736L and quality requirements specification IOGP S-736Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Data Sheet
Row | S-736D Data Sheet for Low Voltage AC Drives (IEC) |  |  |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  |  |  |  | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | General
6 |  | Manufacturer : | Input Data
7 |  | Supplier : | Input Data
8 |  | Purchaser : | Input Data
9 |  | Order status : | Select |  |  |  | Select | for enquiry | for purchase
10 |  | Tag number - delete : | Input Data
11 |  | Model number : | Input Data
12 |  | Project Requirements
13 |  | Conformity assessment system : | D |  |  |  | Select | A | B | C | D
14 |  | Project number - delete : | Input Data
15 |  | Project name - delete : | Input Data
16 |  | Quantity : | Input Data
17 |  | Location/area : | Select |  |  |  | Select | onshore – coastal | onshore – desert | onshore – inland | offshore – fixed | offshore – floating | marine (ship)
18 |  | Installation country : | Input Data
19 |  | Environmental conditions
20 | 5.9.2.1.1 | Location Environment : | Indoor unconditioned |  |  |  | Select | indoor conditioned | indoor unconditioned | outdoor unconditioned
21 |  | Unusual service conditions
22 | 5.9.2.3 | Exposure to damaging fumes : | No |  |  |  | Select | Yes | No
23 | 5.9.2.3 | Exposure to excessive moisture : | No |  |  |  | Select | Yes | No
24 | 5.9.2.3 | Exposure to excessive dust : | No |  |  |  | Select | Yes | No
25 | 5.9.2.3 | Exposure to abrasive dust : | No |  |  |  | Select | Yes | No
26 | 5.9.2.3 | Exposure to steam or water condensation : | No |  |  |  | Select | Yes | No
27 | 5.9.2.3 | Exposure to oil vapour : | No |  |  |  | Select | Yes | No
28 | 5.9.2.3 | Exposure to abnormal vibration, shock or lifting : | No |  |  |  | Select | Yes | No
29 | 5.9.2.3 | Exposure to unusual transportation or storage conditions : | No |  |  |  | Select | Yes | No
30 | 5.9.2.3 | Exposure to extreme or sudden changes in temperature : | No |  |  |  | Select | Yes | No
31 | 5.9.2.3 | Unusual mounting space limitations : | No |  |  |  | Select | Yes | No
32 | 5.9.2.3 | Unusually high nuclear radiation : | No |  |  |  | Select | Yes | No
33 | 5.9.2.3 | Altitude for thermal consideration above 1000m : | No |  |  |  | Select | Yes | No
34 | 5.9.2.3 | Altitude for insulation coordination above 2000m : | No |  |  |  | Select | Yes | No
35 | 5.9.2.3 | Long periods not energized : | No |  |  |  | Select | Yes | No
36 | 5.9.2.3 | Severe restriction on audible noise : | No |  |  |  | Select | Yes | No
37 | 5.9.2.3 | Exposure to salt air : | No |  |  |  | Select | Yes | No
38 | 5.9.2.3 | Exposure to contamination of air by sour gas (H2S) (SO2) : | No |  |  |  | Select | Yes | No
39 | Table 14 | Seismic consideration : | Select |  |  |  | Select | 0 to 2 | 3 | 4
40 |  | Area classification
41 | 5.14 | Hazardous area classification : | Select |  |  |  | Select | Zone 1 | Zone 2 | Zone 21 | Zone 22 | Division 1 | Division 2 | non-hazardous
42 |  | Electrical system data
43 | 5.3.2.2 | Input voltage : | Select | V |  |  | Select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | 1500 | other
44 | 5.3.2.2 | Frequency : | 50 | Hz |  |  | Select | 50 | 60 | DC
45 | 5.3.2.2 | Number of phases : | 3 |  |  |  | Select | 3 | not applicable
46 | 5.4.1.5.2 | Maximum symmetrical fault current : | Input Data | kA
47 | 5.4.1.5.2 | Line side harmonic content : | Input Data | %
48 | 5.7 | EMC application environment : | second |  |  |  | Select | first | second
49 | 5.7 | PDS category : | C3 |  |  |  | Select | C2 | C3 | C4
50 | 5.4.1.5.2 | Supply system earthing : | Solidly earthed neutral |  |  |  | Select | solidly earthed neutral | low impedance | high impedance | isolated neutral
51 | Table 12 | Overvoltage category : | III |  |  |  | Select | III | IV
52 |  | BDM/CDM
53 |  | General
54 | 5.3.2.4 | Local isolation required : | No |  |  |  | Select | Yes | No
55 |  | BDM/CDM input ratings
56 | 5.3.2.2, 5.3.3.1 | Voltage : | Input Data | V
57 | 5.3.2.3 | Current : | Input Data | A
58 | 5.3.2.2, 5.3.3.1 | Frequency : | Input Data | Hz
59 |  | BDM/CDM output ratings
60 | 5.3.3.1 | Continuous rated output current : | Input Data | A
61 | 5.3.3.3 | Overcurrent capability : | Input Data | p.u/min
62 | 5.3.3.3 | Over torque capability : | Input Data | p.u/min
63 |  | BDM/CDM performance
64 | 5.4.1.5.1 | Drive operation : | Quadrant I |  |  |  | Select | Quadrant I | Quadrant I and III | all quadrants
65 | 5.4.1.5.1 | Control type : | Select |  |  |  | Select | variable torque | constant power | constant torque
66 | 5.4.1.4.1.1 | Dynamic braking required : | No |  |  |  | Select | No | Yes-resistive braking | Yes-regenerative braking
67 | 5.4.1.2.3 | Steady state deviation band : | Select | % |  |  | Select | ±5 | ±2 | ±1 | ±0.5
68 |  | Analog input
69 | 5.4.4.2.3 | Number : | 2 |  |  |  | Select | 1 | 2 | 3
70 |  | Analog output
71 | 5.4.4.2.2 | Number : | 1 |  |  |  | Select | 1 | 2 | 3
72 |  | Digital input
73 | 5.4.4.2.4 | Number : | Input Data
74 |  | Digital output
75 | 5.4.4.2.5 | Number : | Input Data
76 |  | Communication interface/ports
77 | 5.4.4.2.6 | Number : | Input Data
78 | 5.4.4.2.6 | Protocol : | Input Data
79 | 5.2.3 | Converter type : | Voltage source |  |  |  | Select | current source | voltage source
80 | 5.2.3 | Additional DC link capacitance required : | No |  |  |  | Select | Yes | No
81 | 5.1 | Converter duty class : | II |  |  |  | Select | I | II | III | IV | V
82 | 5.3.6.3.4.1 | Output filter type : | Select |  |  |  | Select | common mode filter | dv/dt filter | sine wave filter
83 |  | Cooling
84 | 5.2.4.1 | Cooling type : | Natural ventilation |  |  |  | Select | natural ventilation | forced air | water cooled
85 | 5.2.4.1 | Redundant cooling system required : | Select |  |  |  | Select | Yes | No
86 | 5.2.4.4 | Cooling water type : | Select |  |  |  | Select | fresh water | salt water
87 | 5.2.4.3 | Water inlet temperature : | Input Data | °C
88 | 5.2.5 | Bypass configuration required : | Select |  |  |  | Select | Yes | No
89 |  | Enclosure
90 |  | Dimensions
91 |  | Height : | Input Data | mm
92 |  | Length : | Input Data | mm
93 |  | Depth : | Input Data | mm
94 |  | Weight : | Input Data | kg
95 |  | Mounting arrangement : | Select |  |  |  | Select | wall | floor | inside switchgear
96 | 5.9.2.1.1 | Ingress protection : | Input Data
97 |  | Painting shade : | Input Data
98 |  | Heat loss : | Input Data | Watts
99 |  | Anti condensation heaters : | Select |  |  |  | Select | Yes | No
100 | 5.9.2.5 | Noise level : | Input Data | dBA
101 |  | Motor
102 | 5.3.6.3.3.1 | Power rating : | Input Data | kW
103 | 5.3.6.3.3.1 | Voltage : | Input Data | V
104 | 5.3.6.3.3.1 | Rated speed : | Input Data | r/min
105 | 5.3.6.3.6 | Speed range : | Input Data | r/min
106 | 5.3.6.3.3.1 | Starting torque : | Input Data | N-m
107 | 5.3.6.3.4.1, 5.3.6.3.5.1 | Cable length : | Input Data | m
108 | 5.4.1.4.1.2 a), b), c) | Inertia of driven equipment : | Input Data | kg.m2
109 |  | Cables
110 |  | Power cable entry : | Select |  |  |  | Select | top | bottom
111 | 5.3.6.3.5.1 | Incoming cable type : | Select |  |  |  | Select | armoured | unarmoured | shielded
112 | 5.3.6.3.5.1 | Incoming cable size : | Input Data | sq.mm
113 | 5.3.6.3.5.1 | Outgoing cable type : | Select |  |  |  | Select | armoured | unarmoured | shielded
114 | 5.3.6.3.5.1 | Outgoing cable size : | Input Data | sq.mm
115 |  | Transformer
116 |  | Converter transformer
117 | 5.3.6.2.2 | Transformer rating : | Input Data | kVA
118 | 5.3.6.2.2 | Transformer voltage ratio : | Input Data
119 | 5.3.6.2.2 | Transformer type : | Dry type |  |  |  | Select | dry type | liquid filled
120 | 5.3.6.2.3.2 | Connection and phase displacement symbol : | Input Data
121 |  | Input transformer
122 | 5.3.6.2.2 | Transformer rating : | Input Data | kVA
123 | 5.3.6.2.2 | Transformer voltage ratio : | Input Data
124 | 5.3.6.2.2 | Transformer type : | Dry type |  |  |  | Select | dry type | liquid filled
125 | 5.3.6.2.3.2 | Connection and phase displacement symbol : | Input Data
126 |  | Output transformer
127 | 5.3.6.2.2 | Transformer rating : | Input Data | kVA
128 | 5.3.6.2.2 | Transformer voltage ratio : | Input Data
129 | 5.3.6.2.2 | Transformer type : | Dry type |  |  |  | Select | dry type | liquid filled
130 | 5.3.6.2.3.2 | Connection and phase displacement symbol : | Input Data
Public Review Draft
Public Review Draft
Note on C6: Confirm BDM or BDM/CDM supplier (OEM)
Note on C7: Confirm the system integrator if different from the OEM.
Note on C8: Agency responsible for placing purchaser order on the equipment supplier. Could be an EPC contractor or Operating Company.
Note on C9: Advise order status, this shall allow both purchaser and manufacturer to more accurately define values as they become available.
Note on C10: Indicate the customer/end user's unique tag number for the product or the package. Input "N/A" in case no unique tag number available.
Note on C11: Supplier to advise on model number of the BDM/CDM.
Note on C13: Select CAS level as applied in S-736Q, Annex A. CAS A reflects the highest risk and associated extent of verification. CAS D is the lowest.
Note on C14: Confirm project number
Note on C15: Confirm project name
Note on C16: Specify quantity of drives
Note on C17: Select location in accordance with the installation area
Note on C18: Advise the country for final installation of the BDM/CDM to enable the manufacturer to provide the required product marking and certification for the region.
Note on C20: Select environmental service conditions in accordance with S-736, table 12
Note on C22: IEC 61800-2 lists potential unusual service conditions to consider, which may require optional construction or protective features. No guidance is given in IEC 61800-2 as to definition of damaging fumes. IOGP default is set at "No".
Note on C23: Specify whether drive will be subjected to exposure to excessive moisture (relative humidity greater than specified)
Note on C24: Specify whether drive will be subjected to exposure to excessive dust
Note on C25: Specify whether drive will be subjected to exposure to abrasive dust
Note on C26: Specify whether drive will be subjected to exposure to steam or water condensation
Note on C27: Specify whether drive will be subjected to exposure to oil vapour
Note on C28: Specify whether drive will be subjected to exposure to abnormal vibration, shock or lifting
Note on C29: Specify whether drive will be subjected to exposure to unusual transportation or storage conditions
Note on C30: Specify whether drive will be subjected to exposure to extreme or sudden changes in temperature (exceeding 5 K/h)
Note on C31: Specify whether drive will be subjected to unusual mounting space limitations
Note on C32: Specify whether drive will be subjected to unusually high nuclear radiation
Note on C33: Specify whether drive will be operated at altitude above 1000m
Note on C34: Specify whether drive will be operated at altitude above 2000m
Note on C35: Specify whether drive will be operated after long periods not energized
Note on C36: Specify whether drive will be subjected to severe restriction on audible noise during operation
Note on C37: Specify whether drive will be subjected to exposure to salt air
Note on C38: IOGP default is "No". If special service conditions are present, user to select "Yes" and provide additional information on the prevailing conditions. No further guidance available in IEC.
Note on C39: Input either UBC or IEC seismic zone. IEC 61800-2, table 14 doesn't cover earthquakes. IEC 60721-2-6 provides more details.
Note on C41: Specify the area classification for the motor fed from the BDM/CDM in accordance with IEC 60079-10, API RP 505 or API RP 500.
Note on C43: Specify the input supply voltage for the BDM/CDM in accordance with IEC 61800-2, cl.5.3.2.2
Note on C44: Specify the supply frequency in accordance with IEC 61800-2, cl.5.3.2.2
Note on C45: Default for AC input is 3 phase. Select "Not applicable" for DC input.
Note on C46: Specify the maximum fault current of the supply system in accordance with IEC 61800-2, cl.5.4.1.5.2
Note on C47: Specify the line side harmonic content in accordance with IEC 61800-2, cl.5.4.1.5.2
Note on C48: Specify the application environment for EMC in accordance with IEC 61800-3. First environment generally applies to domestic and commercial premises. Second environment applies to industrial networks.
Note on C49: C1 and C2 apply to PDS in the first environment. C3 applies to PDS for most second environment low voltage industrial applications. C4 applies to second environment with voltage greater than 1000V or 400A.
Note on C50: Specify the supply system earthing type in accordance with IEC 61800-2, cl.6.6.2.
Note on C51: Specify overvoltage category in accordance with IEC 61800-5-1. IOGP default is category III and also aligns with the default in IOGP S-560 for L.V switchgear.
Note on C54: Specify whether local isolation switch at the input of the BDM/CDM is required. IOGP default is "no" for mass produced products. Purchaser option for customised products or special applications.
Note on C56: Specify input voltage of the BDM/CDM in accordance with IEC 61800-2, cl.5.3.2.2
Note on C57: Specify the input current rating of the BDM/CDM in accordance with IEC 61800-2, cl.5.3.2.3.
Note on C58: Specify the input frequency of the BDM/CDM in accordance with IEC 61800-2, cl.5.3.2.2.
Note on C60: Specify the continuous rated output current without overload for the BDM/CDM at the maximum ambient air temperature.
Note on C61: Specify the overcurrent capability of the BDM/CDM in accordance with table 8 of IEC 61800-2.
Note on C62: Specify the over torque capability of the BDM/CDM.
Note on C64: Specify the operating quadrants of the BDM/CDM. IOGP default is quadrant I. Quadrant I and III for reversing operation. All quadrant for braking operation.
Note on C65: IOGP default is set at variable torque as centrifugal pumps, compressors and fans fall in this category. Constant torque is typical for conveyors, elevators and constant power is typical for grinders and winding machines.
Note on C66: IOGP default selection is "No".
Note on C67: Application specific. IOGP default set at +/-1%. ±0.5% may require a motor shaft speed feedback sensor.
Note on C69: Specify the number of analog inputs required in the BDM/CDM, IOGP default is "2" which is provided by most suppliers.
Note on C71: Specify the number of analog outputs required in the BDM/CDM
Note on C73: Specify the number of digital inputs provided in the BDM/CDM. 6 digital inputs are generally provided by most suppliers.
Note on C75: Specify the number of digital outputs provided in the BDM/CDM. 2 digital outputs and 3 relay outputs are generally provided by most suppliers.
Note on C77: Specify the number of communication interface ports in the BDM/CDM
Note on C78: Specification indicates following minimum: PROFINET, PROFIBUS, EtherNet/IP, Modbus TCP, Modbus RTU
Note on C79: IOGP default is voltage source converter. Current source is rarely used for low voltage drives.
Note on C80: Additional DC link capacitance is required for enhanced power ride through over the limit specified in IEC 61800-2, table 7. The extent and duration of the enhanced ride through is subject to agreement between the purchaser and the supplier.
Note on C81: Duty class to be specified in accordance with IEC 60146-1-1. IOGP default is class II.110% overload is applicable for variable torque application and 150% overload is applicable for constant torque application.
Note on C82: Specify type of output filter in accordance with design of the BDM/CDM
Note on C84: Specify the type of cooling for the BDM/CDM.
Note on C85: Specify whether redundancy in cooling fans is required
Note on C86: Specify cooling water type for water cooled BDM/CDM.
Note on C87: Specify water temperature at the inlet of the heat exchanger
Note on C88: Specify whether bypass is required for the BDM/CDM for critical applications.
Note on C91: Specify the height of the BDM/CDM enclosure. For BDM/CDM mounted within cabinet specify the height of the cabinet. Total height including the cooling fans and louvers to be indicated.
Note on C92: Specify the length of the BDM/CDM enclosure. For BDM/CDM mounted within cabinet specify the length of the cabinet.
Note on C93: Specify the depth of the BDM/CDM enclosure. For BDM/CDM mounted within cabinet specify the depth of the cabinet..
Note on C94: Specify the weight of the BDM/CDM enclosure
Note on C95: Specify mounting arrangement of the BDM/CDM
Note on C96: BDM installed indoor inside switchgear or cabinet shall be minimum IP2X. BDM installed indoor free standing or wall mounting shall be minimum IP31. BDM/CDM installed outdoor shall be minimum IP55.
Note on C97: Specify the painting shade of the BDM/CDM enclosure
Note on C98: Specify the heat loss of the BDM/CDM enclosure or cabinet.
Note on C99: Specify whether anti condensation heaters are required within the BDM/CDM cabinet based on the variation in ambient temperature. Generally required for assembly of drives mounted in cabinets.
Note on C100: Specify the audible noise generated by the BDM/CDM.
Note on C102: Specify the kW rating of the motor driven from the BDM/CDM
Note on C103: Specify the rated operating voltage of the motor fed from the BDM/CDM
Note on C104: Specify the rated speed of the motor fed from the BDM/CDM
Note on C105: Specify the operating speed range required for the motor
Note on C106: Specify the starting torque required to drive the motor
Note on C107: Specify the cable length from the BDM/CDM to the motor
Note on C108: Inertia of driven equipment to be provided for dynamic braking application.
Note on C110: Specify the power cable entry for the BDM/CDM enclosure
Note on C111: Specify the incoming cable type to the BDM/CDM
Note on C112: Specify incoming cable size to the BDM/CDM
Note on C113: Specify the output cable type from the BDM/CDM to the motor
Note on C114: Specify the outgoing cable size from the BDM/CDM to the motor
Note on C117: Specify the rating of the converter transformer, if any
Note on C118: Specify the voltage ratio of the converter transformer
Note on C119: Specify type of transformer in accordance with cooling
Note on C120: Specify the transformer vector group
Note on C122: Specify the rating of the input transformer, if any
Note on C123: Specify the voltage ratio of the input transformer
Note on C124: Specify type of transformer in accordance with cooling
Note on C125: Specify the transformer vector group
Note on C127: Specify the rating of the output transformer, if any
Note on C128: Specify the voltage ratio of the output transformer
Note on C129: Specify type of transformer in accordance with cooling
Note on C130: Specify the transformer vector group

## Supplement
Row |  | S-736D Data Sheet for Low Voltage AC Drives (IEC) | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
Public Review Draft

## Guidance
Data Sheet for
Low Voltage AC Drives (IEC)
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-736 Supplementary Specification to IEC 61800-2 Low Voltage AC Drives.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.
Public Review Draft

## Backcover
Public Review Draft