## Front & Preliminaries
|  |  |  | SPECIFICATION | November
|  |  |  | S-734D | 2020
Data Sheet for
AC Uninterruptible Power Supply (UPS)
System (PIP ELSAP04)
Revision history
| VERSION | DATE | PURPOSE
| 1 | November 2020 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
Data Sheet for
AC Uninterruptible Power Supply (UPS) System (PIP ELSAP04)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
Data Sheet for
AC Uninterruptible Power Supply (UPS) System (PIP ELSAP04)
Introduction
The purpose of this equipment data sheet is to define purchaser specific requirements for the procurement of AC uninterruptible power supply (UPS) systems in accordance with IOGP S-734 for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-734, information requirements specification IOGP S-734L and quality requirements specification IOGP S-734Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet

## Data Sheet
Row |  | S-734D Data Sheet for AC Uninterruptible Power Supply (UPS) System (PIP ELSAP04) |  |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  |  |  |  | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | Applicable to : | Select |  |  |  | Select | proposal | purchase
6 |  | General
7 | 1.2, 4.1.1, 4.8.2 | UPS type : | Select |  |  |  | Select | pulse-width modulated | ferroresonant
8 | 4.1.5, Figure 1 | UPS configuration : | single |  |  |  | Select | single | duplicate (not paralleled) | duplicate paralleled
9 | 4.1.5, Figure 1 | System one-line or block diagram drawing no : | PIP ELSAP04 Figure 1. Typical UPS Configuration |  |  |  | Select | PIP ELSAP04 Figure 1. Typical UPS Configuration | Other (provide reference drawing in notes column)
10 | 4.1.2 | Black start : | not required |  |  |  | Select | not required | required
11 | 4.1.2, 4.1.3 | Electrical installation code : | Select |  |  |  | Select | NFPA70 (NEC) | CSA22.1 Part 1 (CEC) | other
12 | 4.1.3 | Certification : | UL listed |  |  |  | Select | UL listed | CSA | other(s) | not required
13 | 4.1.17 | Maximum noise level : | 75 dBA |  |  |  | Select | 75 dBA | 70 dBA | other
14 | 4.1.19 | Cable entry : | Select |  |  |  | Select | top | bottom
15 | 4.1.19 | Cable gland plate : | not required |  |  |  | Select | not required | required (see additional notes)
16 | 4.1.20, 4.1.21, 4.17.3 | Copper bus design : | tin plated |  |  |  | Select | tin plated | silver plated | bare
17 | 4.1.23 | Conformal PCB coating : | required |  |  |  | Select | required | not required
18 |  | Site conditions
19 | 4.2.4 | Maximum altitude : | 1000 m (3300 ft) |  |  |  | Select | 1000 m (3300 ft) | other
20 |  | Seismic design : | not required |  |  |  | Select | not required | required
21 |  | Site location : | Input Data
22 |  | Risk category : | Select |  |  |  | Select | I | II | III | IV
23 |  | Component importance factor (Ip) : | Select |  |  |  | Select | 1 | 1.25 | 1.5
24 |  | Site class : | D |  |  |  | Select | A | B | C | D | E | F
25 | 4.2.6 | Seismic certificate : | not required |  |  |  | Select | not required | required
26 |  | Marine service : | not required |  |  |  | Select | not required | required
27 | 4.2.2 | Maximum ambient temperature : | 104 | °F |  |  | Select | °F | °C
28 | 4.2.2 | Minimum ambient temperature : | 32 | °F |  |  | Select | °F | °C
29 | 4.2.3 | Maximum relative humidity : | ≤ 95 | %
30 |  | Electrical characteristics
31 | Table 1 | Power rating : | Input Data | Select |  |  | Select | kW | kVA
32 | Table 1 | Normal input voltage : | 480 | V |  |  | Select | 480 | 600 | other
33 |  | Input phase : | 3 |  |  |  | Select | 1 | 3
34 | Table 1 | Input frequency : | 60 | Hz |  |  | Select | 50 | 60
35 |  | Supply system configuration : | wye resistance grounded |  |  |  | Select | wye resistance grounded | delta | wye grounded | wye
36 | Table 1 | Input current harmonics (THD) : | ≤ 35 | % |  |  | Select | ≤ 35 | other
37 | 4.15.3, 4.16.2 | Input system fault current : | Input Data | kA
38 |  | Input Transient overvoltage immunity : | Cat. II |  |  |  | Select | Cat. II | Cat. III
39 | Table 1 | Bypass source voltage : | 480 | V |  |  | Select | 480 | 600 | other
40 |  | Bypass phase : | 3 |  |  |  | Select | 1 | 3
41 | 4.15.3, 4.16.2 | Bypass system fault current : | Input Data | kA
42 |  | Output voltage : | 120 | V |  |  | Select | 120 | 120/208Y | 120/240 | other
43 |  | Output system configuration : | wye grounded |  |  |  | Select | delta | wye grounded | single phase
44 |  | Load characteristics
45 |  | Linear load : | Input Data | %
46 |  | Non-linear load : | Input Data | %
47 |  | Motor load : | Input Data | Select |  |  | Select | hp | kW
48 |  | Overall system efficiency
49 |  | @ 100% Load : | Input Data | %
50 |  | @ 75% Load : | Input Data | %
51 |  | @ 50% Load : | Input Data | %
52 |  | Full load heat rejection rate : | Input Data | BTU/HR
53 |  | Isolation and bypass transformers
54 | 4.5.1 | Input transformer : | required |  |  |  | Select | required | not required
55 | Figure 1 | Internal or external to UPS : | internal |  |  |  | Select | internal | external
56 | 4.5.7 | Input transformer shielding : | shielded |  |  |  | Select | shielded | not shielded
57 | 4.5.6 | Input transformer k-factor rating : | K-4 |  |  |  | Select | K-4 | other
58 | 4.5.2 | Bypass transformer : | required |  |  |  | Select | required | not required
59 |  | Internal or external to UPS : | external |  |  |  | Select | external | internal
60 | 4.5.7 | Bypass transformer shielding : | shielded |  |  |  | Select | shielded | not shielded
61 | 4.5.6 | Bypass transformer k-factor rating : | K-4 |  |  |  | Select | K-4 | other
62 |  | Rectifier/charger
63 | 4.6.1.9, Table 1 | Recharging time : | 8 | hrs |  |  | Select | 8 | other
64 | 4.6.1 10 a to c | Duplicate rectifier/charger : | not required |  |  |  | Select | not required | required
65 | 4.6.1 11 | Temperature compensated battery charging : | Select |  |  |  | Select | not required | required
66 |  | Inverter
67 | 4.7.4 a, 4.7.4 b | Inverter turn-off voltage : | Select | Vdc |  |  | Select | 1.75 (Lead Acid) | 1.00 (NiCad) | other
68 |  | Internal manual bypass switch
69 | 4.9.1, 4.9.4 | Manual bypass switch w/LED position indication : | not required |  |  |  | Select | not required | required
70 |  | Remote maintenance bypass switch
71 | 4.10.1, 4.4.6 | Remote maintenance bypass switch : | required |  |  |  | Select | required | not required
72 | 4.10.4, Figure 1 | Bypass input circuit breaker : | required |  |  |  | Select | required | not required
73 | 4.10.4, Figure 1 | AC output circuit breaker : | required |  |  |  | Select | required | not required
74 |  | Inverter test load connection
75 | 4.11.1, Figure 1 | Test load connection : | not required |  |  |  | Select | not required | circuit breaker | disconnect switch | fused disconnect switch
76 | 4.11.2, Figure 1 | Circuit breaker or disconnect current rating : | Input Data | A
77 |  | Battery disconnect
78 | 4.1.9, 4.12.1, Figure 1 | Internal battery disconnect : | circuit breaker |  |  |  | Select | not required | circuit breaker | fused switch
79 | 4.1.9, 4.12.1, Figure 1 | External battery disconnect : | not required |  |  |  | Select | not required | circuit breaker | fused switch
80 | 4.1.9, 4.12.1, Figure 1 | Battery shunt trip : | not required |  |  |  | Select | not required | internal disconnect | external disconnect
81 | 4.1.9, 4.12.1, Figure 1 | Battery disconnect (area classification) : | Select |  |  |  | Select | non hazardous | hazardous
82 |  | Batteries
83 | 4.13.1, Figure 1 | Batteries : | required |  |  |  | Select | required | not required
84 | 4.13.1 | Type : | Select |  |  |  | Select | Lead Acid Valve Regulated (VRLA) - AGM | Lead Acid Valve Regulated (VRLA) - Gel | Lead Acid Vented | Nickel Cadmium sealed | Nickel Cadmium vented | other
85 | 4.13.1 | Battery specifications : | Select |  |  |  | Select | PIP ELSAP11/11D | PIP ELSAP12/12D | other
86 | 4.13.1 | Nominal battery voltage : | Input Data | V
87 | 4.6.2 2 a to d | Other battery type - float voltage : | Input Data | V/cell
88 | 4.6.2, 4.6.2 3 a to d | Other battery type - equalize voltage : | Input Data | V/cell
89 | 4.14.12 | Battery location : | rack mount (remote) |  |  |  | Select | rack mount (remote) | cabinet (UPS adjacent) | cabinet (remote) | other
90 | 4.14.12 | Adjacent battery cabinet (lock/interlock) provision (if applicable) : | lockable |  |  |  | Select | not required | lockable | interlocked | lockable and interlocked
91 | 4.13.2 | Backup time : | Input Data | min
92 | 4.13.2 | Power factor : | 1 | pf |  |  | Select | 0.8 | 1 | other
93 |  | UPS enclosure
94 | 4.14.1 | Enclosure, NEMA rating : | manufacturer's standard |  |  |  | Select | manufacturer's standard | NEMA 1 | NEMA 1 gasketed | other
95 | 4.14.11 | Enclosure finish : | manufacturer's standard |  |  |  | Select | manufacturer's standard | other
96 | 4.14.3 | Lifting base : | required |  |  |  | Select | required | not required
97 | 4.14.4 | UPS enclosure access : | front access only |  |  |  | Select | front access only | front and rear access
98 | 4.14.10 | Air inlet dust filters : | Select |  |  |  | Select | required | not required
99 | 4.14.13 | UPS enclosure(s) temperature sensor : | Select |  |  |  | Select | required | not required
100 |  | Space heater : | not required |  |  |  | Select | required | not required
101 |  | Controls monitoring and communications
102 | 4.18.1.3 | Automatic battery on-load testing : | Select |  |  |  | Select | required | not required
103 | 4.1.15, 4.1.22, 4.18.2 | Status indication : | HMI integrated |  |  |  | Select | HMI integrated | discrete LED
104 | 4.1.22, 4.18.2, 4.18.4.2 | Additional indication : | Input Data
105 | 4.19.1, 4.1.15, 4.18.3.1 | Mimic screen : | HMI |  |  |  | Select | HMI | other
106 | 4.18.3.2, 4.18.3.2 a, b | Meters : | HMI |  |  |  | Select | HMI | digital meter | analog meter
107 |  | Bypass source measurement : | required |  |  |  | Select | required | not required
108 | 4.18.4.7 | Audible alarm : | not required |  |  |  | Select | not required | required
109 | 4.18.7.1, 4.18.7.2 | Communications interface : | Select |  |  |  | Select | ethernet | fiber | wireless | RS485 | RS232 | hardwired dry contacts | other | not required
110 | 4.18.7.1, 4.18.7.3 | Communication protocol : | Input Data
111 |  | Tagging and nameplates
112 | 4.19.4 | Additional nameplate information : | Input Data
113 |  | Inspection and Testing
114 | 4.20.6 | Full rated capacity burn in test : | manufacture std duration |  |  |  | Select | manufacture std duration | other duration
115 | 4.20.8 | Conformity assessment system : | Select |  |  |  | Select | A | B | C | D
116 |  | Battery capacity test : | not required |  |  |  | Select | not required | vented lead acid per IEEE 450 | VRLA per IEEE 1188 | Ni-Cad per IEEE 1106 | other battery type/standard
117 |  | Shipping
118 | 4.21.2 | Weatherproof packaging : | Select |  |  |  | Select | required | not required
Note on C5: Select the stage of procurement that this data sheet is being issued for.
Note on C7: Select the UPS type
Note on C8: Select the UPS configuration. Duplicate provides multiple UPS units for redundancy. Paralleled UPS are duplicate and connected to common output.
Note on C9: Select the one-line or block diagram to be used for the UPS design. Default is PIP ELSAP04 Figure 1. Typical UPS Configuration if project specific information not provided.
Note on C10: UPS purchaser to specify Black Start when UPS is required to start up on battery only (i.e. loss of main power supply connection).
Note on C11: Select the applicable local installation code. If other is selected, enter the installation code in the 'Additional notes' column.
Note on C12: Select the certification requirements. If other is selected, enter the required certification in the 'Additional notes' column. Manufacturers may propose alternate certification bodies.
Note on C13: Select the maximum noise level at 1 meter (3 feet). If "other" is selected, enter the additional information in the "additional notes" column.
Note on C14: Select the input and output cable entry.
Note on C15: Select if cable gland plate is required. If required, purchaser can provide information on pre-drilled holes and non-magnetic material requirements.
Note on C16: Select the copper bus plating type.
Note on C17: Select the PCB coating requirement.
Note on C19: Select the site maximum altitude. Default value is ≤ 1000 m (3300 ft). If "other" is selected, use the "additional note" column to indicate value (if value greater than 1000 m (3300 ft))
Note on C20: Select seismic design requirement per ASCE 7-16
Note on C21: Provide site physical address or latitude and longitude to determine seismic acceleration values
Note on C22: Provide risk category per ASCE 7-16 (Risk category of buildings and other structures for flood, wind, snow, earthquake, and Ice loads). Typical Oil and Gas category is IV.
Note on C23: Provide component importance factor of buildings and other structures for snow, ice, and earthquake loads. Typical Oil and Gas importance factor is 1.5.
Note on C24: Provide site class per ASCE 7-16 (Chapter 20). Site Class D is specified if detailed soil properties are not known.
Note on C25: Provide seismic certificate by third party, only if selected on data sheet..
Note on C26: Select marine service requirements to account for vessel motions for offshore installations. If "required" is selected, Purchaser to provide pitch and roll requirements in degrees.
Note on C27: Specify the maximum ambient temperature. Default value is 104°F (40°C).
Note on C28: Specify the minimum ambient temperature. Default value is 32°F (0°C).
Note on C29: Specify the maximum relative humidity. Default value is ≤ 95% non-condensing.
Note on C31: Specify the UPS power rating. kW is more commonly used for smaller UPS units and kVA for larger units.
Note on C32: Select the rated input voltage. If "other" is selected, specify the value in "Additional notes" column.
Note on C33: Select the number of phase for the input power supply.
Note on C34: Select the input voltage frequency.
Note on C35: Select the supply system type configuration.
Note on C36: Select the input current total harmonic distortion. If other is selected, specify the value in the "additional note" column.
Note on C37: Specify the input system fault current level.
Note on C38: Select transient input immunity per IEC 62040-1. Category II is typical for industrial systems. Category III may be needed for islanded power systems (close to generation source) or UPS without input transformers.
Note on C39: Select the input voltage for the bypass. If other is selected, specify the value in the "additional note" column.
Note on C40: Select the number of phase for the bypass power supply.
Note on C41: Specify the bypass system fault current level.
Note on C42: Select the output voltage. Larger UPS systems may be more economical to select 3 phase output. If other is selected, specify the value in the "additional note" column.
Note on C43: Select the output system type configuration.
Note on C45: Specify the linear load percentage. Total load (linear, non-linear and motor) not to exceed 100%.
Note on C46: Specify the non linear load percentage. Total non linear load to account for motor inrush currents. Total load (linear and non linear and motor) not to exceed 100%.
Note on C47: Specify the motor load in hp or kW.
Note on C49: Specify the overall system efficiency at 100% load.
Note on C50: Specify the overall system efficiency at 75% load.
Note on C51: Specify the overall system efficiency at 50% load.
Note on C52: Specify the full load heat rejection rate.
Note on C54: Select the input transformer requirement.
Note on C55: Select internal or external input transformer. Typically suppliers provide internal input transformers.
Note on C56: Select input transformer shielding requirement. The datasheet provides non shielded options for transformer not provided by the PIP ELSAP04.
Note on C57: Select the input transformer k-factor rating. If "other" is selected, specify the value in "Additional notes" column. Minimum of k-4 is specified by the PIP ELSAP04.
Note on C58: Select the bypass transformer requirement. If bypass and output are the same voltage, a transformer may not be required.
Note on C59: Select internal or external bypass transformer.
Note on C60: Select bypass transformer shielding requirement. The datasheet provides non shielded options for transformer not provided by the PIP ELSAP04.
Note on C61: Select the bypass transformer k-factor rating. If "other" is selected, specify the value in "Additional notes" column. Minimum of k-4 is specified by the PIP ELSAP04.
Note on C63: The recharging time to 90% of full battery capacity should be within 10 times the discharge time of the battery and typically not greater than 8 hours. If "other" is selected, input value in "Additional notes"
Note on C64: Select the duplicate (parallel) rectifier/charger requirement.
Note on C65: Temperature compensation is generally required for VRLA batteries and when batteries are not located within the same ambient conditions.
Note on C67: If UPS and batteries are supplied together, the supplier will input the selection otherwise purchaser will provide input. If "other" is selected, specify value in "Additional notes" column.
Note on C72: Select the bypass input circuit breaker configuration; per PIP ELSAP04 Figure 1 or purchaser single line diagrams
Note on C73: Select the AC output circuit breaker configuration; per PIP ELSAP04 Figure 1 or purchaser single line diagram
Note on C75: Select the test load connection requirement.
Note on C76: Provide rated current of disconnect device for test load
Note on C78: Select the requirement for the battery disconnect internal to the UPS.
Note on C79: Select the requirement for the battery disconnect external to the UPS.
Note on C80: If circuit breaker is selected for internal or external battery disconnect, Battery shunt trip can be selected to provide battery isolation on minimum voltage or discharge duration.
Note on C81: If hazardous is selected, Class/Div/Zone and gas group to be added in additional notes.
Note on C83: If required, UPS supplier to include batteries in their scope of supply.
Note on C84: Select the battery type.
Note on C85: Select battery specification. If "other' is selected, indicate battery specifications in "Additional notes" column.
Note on C86: Provide nominal Battery DC Voltage
Note on C87: Supplier to provide float voltage for batteries other than lead acid or Ni-Cad (Lead acid and Ni-Cad float voltage provided by PIP ELSAP04)
Note on C88: Supplier to provide equalize voltage for other than lead acid or Ni-Cad (Lead acid and Ni-Cad float voltage provided by PIP ELSAP04).
Note on C89: Select the batteries installation location requirements. Cabinet information in PIP ELSAP04 section 14, rack mount information provided in PIP ELSAP11 and PIP ELSAP12. If "other' is selected, specify the value in "Additional notes" column.
Note on C90: When adjacent battery cabinet is selected lock / interlock measures can be selected
Note on C91: Input the battery backup time in minutes. PIP ELSAP04 defaults to minimum 30 minutes (4.13.2) which may be insufficient for some applications.
Note on C92: Select the power factor measured at full load. If "other' is selected, specify the value in "Additional notes" column. Power factor (0.8) is typically specified when supplying inductive loads (i.e. motors, valves, solenoids, etc).
Note on C94: If "other' is selected, specify the value in "Additional notes" column.
Note on C95: If "other' is selected, specify the value in "Additional notes" column.
Note on C96: Select UPS lifting base channel mounting requirement
Note on C97: Select the UPS internal components access door location.
Note on C98: Select air inlet filter requirement. Dust particle filter size to be manufacturer standard.
Note on C99: Typically provided for over temperature protection. (i.e. loss of fan, dirty filter)
Note on C100: If condensation or high humidity is expected in the environment of operation, a space heater should be considered.
Note on C103: Status indicators can be integrated into the HMI or as discrete LEDs
Note on C104: Specify additional list of indication as needed.
Note on C106: Digital metering can be included in the HMI.
Note on C107: Bypass measurements to include L-L voltage, Current per phase and Frequency
Note on C109: Select communication media type. If "other' is selected, specify the details in "Additional notes" column.
Note on C110: Specify the communication protocol (e.g. modbus, modbus TCP/IP, profibus, etc.)
Note on C112: Specify additional nameplate requirement not included in the PIP ELSAP04 para. 4.19.4; additional customer or project specific information for example.
Note on C114: Purchaser to specify burn in test duration in hours. If "other duration' is selected, specify the test hours in the "Additional notes" column.
Note on C115: Select CAS level for QRS.
Note on C116: This load test is conducted at purchaser site. If required, load test will be included in the scope of service. If other than lead acid or Ni-Cad battery, customer and supplier to agree on test procedure.

## Supplement
Row | S-734D Data Sheet for AC Uninterruptible Power Supply (UPS) System (PIP ELSAP04) |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95

## Guidance
Data Sheet for
AC Uninterruptible Power Supply (UPS)
System (PIP ELSAP04)
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-734 Supplementary Specification to PIP ELSAP04 AC Uninterruptible Power Supply (UPS) System.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.