## Front & Preliminaries
|  |  |  | SPECIFICATION | December
|  |  |  | S-740D | 2020
Data Sheet for
Batteries (IEC)
Revision history
| VERSION | DATE | PURPOSE
| 1 | December 2020 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
Data Sheet for
Batteries (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
Data Sheet for
Batteries (IEC)
Introduction
The purpose of this equipment data sheet is to define buyer specific requirements for the procurement of batteries, in accordance with IOGP S-740 for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-740, information requirements specification IOGP S-740L and quality requirements specification IOGP S-740Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet

## Data Sheet
Row | S-740D Data Sheet for Batteries (IEC) | [5 empty] | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description | [5 empty] | Default
4 | Ref. Clause | Description | Purchaser Identified Values | Manufacturer Declared Values |  | Additional notes
5 |  | GENERAL
6 | 10.5.2 | Vendor : | Input Data |  |  |  |  | Select
7 | 10.5.2 | Order status : | Select |  |  |  |  | Select | for enquiry | for purchase
8 | 10.5.2 | Purchase order number and date : | Input Data |  |  |  |  | Select
9 | 10.5.2 | Manufacturer : | Input Data |  |  |  |  | Select
10 | 10.5.2 | Model number : | Input Data |  |  |  |  | Select
11 | 10.5.2 | Battery application : | Input Data |  |  |  |  | Select
12 | 10.5.2, 5.2 | Battery technology : | Select | Select |  |  |  | Select | nickel-cadmium partial gas recombination | vented nickel-cadmium | sealed nickel-cadmium | valve regulated lead-acid - AGM | valve regulated lead-acid - gel | vented lead-acid | other
13 | 10.5.2, 5.1, 7 | Minimum load voltage : | Input Data |  | V d.c.
14 | 10.5.2, 5.1 | Battery bank voltage : | Input Data |  | V d.c.
15 | 7 | Load profile for battery design attached : | Yes |  |  |  |  | Select | Yes | No
16 | 10.5.2, 5.1, 7 | Autonomy time : | Input Data |  | minutes
17 | 10.5.2 | Rated capacity at 20 °C (± 5 °C) : | Input Data | Input Data | Ah
18 |  | Conformity assessment system (CAS) level : | D |  |  |  |  | Select | A | B | C | D
19 |  | CONFIGURATION
20 |  | General
21 | 6.1.1 | Cell container material (flame retardant) : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | HB according to UL94 | V0 according to UL94
22 | 5.1 | Cell connection within the bank : | Select |  |  |  |  | Select | series | parallel | series-parallel
23 | 4.1 | Cell assembly : | Select |  |  |  |  | Select | none | rack | cabinet | enclosure
24 | 10.1.3 | Stacking tier : | Select | Select |  |  |  | Select | one tier | two tiers | three tiers | four tiers
25 | 10.1.3 | Steps within each tier : | Select | Select |  |  |  | Select | no step | single step | two steps | three steps
26 | 10.1.3 | Minimum vertical distance between the two tiers of batteries on rack or cabinet : | Input Data | Input Data | mm
27 | 9.1.1 | Cell connection between the tiers : | manufacturer's standard | manufacturer's standard |  |  |  | Select | manufacturer's standard | insulated flexible copper cable | insulated flexible copper strip
28 | 10.1.6 | Spill containment system under the rack or cabinet : | No |  |  |  |  | Select | Yes | No
29 | 4.1 | On-line battery monitoring facility mounting provision : | Not required |  |  |  |  | Select | not required | string monitoring | cell monitoring
30 | 4.1 | Temperature sensor mounting provision : | Select |  |  |  |  | Select | required | not required
31 | 5.1 | Provision for battery isolation switches in parallel strings : | No |  |  |  |  | Select | Yes | No
32 | 10.1.2, 10.2.1 | Maximum battery rack or cabinet footprint dimension (length) : | Input Data |  | mm
33 | 10.1.2, 10.2.1 | Maximum battery rack or cabinet footprint dimension (depth) : | Input Data |  | mm
34 | 9.1.4 | Battery cable size (cross section area) : | Input Data |  | mm²
35 | 9.1.4 | Battery cable runs (number of runs per polarity) : | Input Data
36 | 4.4 | Language for caution, danger and warning labels : | Input Data |  |  |  |  | Select
37 |  | Rack
38 | 10.1.2 | Material for rack : | Select |  |  |  |  | Select | manufacturer's standard | non-insulated galvanized steel | chemical resistant and electrical insulation coated steel
39 | 10.1.4 | Maximum height from the top of battery on the top tier to the floor : | 1600 |  | mm |  |  | Select | 1600 | 1800 | other
40 | 10.1.2 | Rack length : | Input Data | Input Data | mm
41 | 10.1.2 | Rack width : | Input Data | Input Data | mm
42 | 10.1.2 | Rack height : | Input Data | Input Data | mm
43 | 10.1.2 | Mass of rack without batteries : | Input Data |  | kg
44 | 10.1.2 | Mass of rack with batteries : | Input Data |  | kg
45 | 10.1.2 | Rack reference outline drawing number : | Input Data |  |  |  |  | Select
46 |  | Cabinet/enclosure
47 | 10.2.1 | Cabinet or enclosure material : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | painted steel | stainless steel | FRP | GRP
48 | 10.2.5 | Cabinet or enclosure length : | Input Data | Input Data | mm
49 | 10.2.5 | Cabinet or enclosure width : | Input Data | Input Data | mm
50 | 10.2.5 | Cabinet or enclosure height : | Input Data | Input Data | mm
51 | 10.2.5 | Cabinet or enclosure mass without batteries : | Input Data |  | kg
52 | 10.2.5 | Cabinet or enclosure mass with batteries : | Input Data |  | kg
53 | 10.2.5 | Cabinet or enclosure reference outline drawing number : | Input Data |  |  |  |  | Select
54 | 9.1.4 | Cable entry location : | Select |  |  |  |  | Select | side | bottom | top | bottom and top
55 | 9.1.4 | Cabinet cable entry type : | Select |  |  |  |  | Select | removable - undrilled plate | multi cable transit (MCT)
56 | 10.2.1 | Cabinet paint colour : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | other
57 | 10.2.1 | Canopy for cabinet : | not required |  |  |  |  | Select | required | not required
58 | 10.2.3 | Cabinet ventilation : | Select | Select |  |  |  | Select | not applicable | manufacturer's standard | natural | forced ventilation | forced ventilation with outlet exhaust duct
59 |  | INSTALLATION
60 | 10.1.2, 10.2.5 | Front access clearance dimensions of rack or cabinet : | Input Data |  | mm
61 | 10.1.2, 10.2.5 | Side access clearance dimensions of rack or cabinet : | Input Data |  | mm
62 | 10.1.2, 10.2.5 | Rear access clearance dimensions of rack or cabinet : | Input Data |  | mm
63 |  | SAFETY AND ENVIRONMENTAL CONDITIONS
64 | 4.1 | Site : | Select |  |  |  |  | Select | onshore - coastal | onshore - desert | onshore - inland | offshore - fixed | offshore - floating | marine (ship)
65 | 4.1 | Installed location of battery : | Select |  |  |  |  | Select | battery room | inside equipment room | outdoor (safe area) | outdoor (hazardous area)
66 | 4.1 | Degree of protection (cabinet or enclosure with closed doors) : | IP31 | IP31 |  |  |  | Select | manufacturer's standard | IP31 | IP32 | IP42 | IP44 | IP55
67 | 4.1 | Degree of protection (cabinet or enclosure with open doors) : | IP2X | IP2X |  |  |  | Select | IP2X | IP3X
68 | 4.1 | Special safety equipment : | No |  |  |  |  | Select | Yes | No
69 | 4.1 | Minimum ambient temperature (operation) : | Input Data |  | °C
70 | 4.1 | Maximum ambient temperature (operation) : | Input Data |  | °C
71 | 4.1 | Normal ambient temperature (operation) : | Input Data |  | °C
72 | 4.1 | Maximum relative humidity (operation) : | Input Data |  | %
73 | 4.1 | Temperature at which relative humidity is specified (operation) : | Input Data |  | °C
74 | 4.1 | Maximum altitude (operation) : | Input Data |  | m
75 | 4.1 | Minimum ambient temperature (storage and transportation) : | Input Data |  | °C
76 | 4.1 | Maximum ambient temperature (storage and transportation) : | Input Data |  | °C
77 | 4.1 | Maximum relative humidity (storage and transportation) : | Input Data |  | %
78 | 4.1 | Temperature at which relative humidity is specified (storage and transportation) : | Input Data |  | °C
79 | 4.1 | Seismic requirement data : | Input Data |  |  |  |  | Select
80 | 4.1 | Storage site of batteries : | Select |  |  |  |  | Select | indoor - climate controlled (humidity and temperature) | indoor - temperature controlled only | indoor - natural ventilation | outdoor | unusual conditions
81 | 4.1 | Unusual conditions (operation) : | Input Data |  |  |  |  | Select
82 | 4.1 | Unusual conditions (storage and transportation) : | Input Data |  |  |  |  | Select
83 |  | BATTERY ROOM SPECIFICATIONS
84 | 4.1 | Area classification : | Select |  |  |  |  | Select | safe | hazardous
85 | 4.1 | Hazardous area classification : | Select |  |  |  |  | Select | not applicable | zone 1 | zone 2
86 | 4.1 | Minimum gas subdivision and temperature class (for equipment in battery room) : | Select |  |  |  |  | Select | not applicable | IIB+H2 T3 | IIC T3
87 | 4.3 | Recommended ventilation flow rate : | Input Data |  | m³/h
88 |  | BATTERY SPECIFICATIONS
89 | 7 | Nominal DC voltage : | Input Data | Input Data | V d.c.
90 | 5.2 | Plate type (lead-acid) : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | flat plate | modified plate | round | tubular | grid
91 | 5.2 | Plate type (Ni-Cd) : | manufacturer's standard |  |  |  |  | Select | manufacturer's standard | pocket | fiber | sintered | plastic bonded
92 | 5.3, 5.4 | Required service life : | Input Data | Input Data | years
93 | 5.4 | Float service life : | Input Data |  | years
94 | 11.1 | Battery shelf life : | Input Data |  | months
95 | 7 | Quantity of cells and strings : | Input Data |  | nos.
96 | 5.3 | Charge/discharge cycle : | Input Data |  | cycles
97 | 8 | Discharge rate (C-rate) : | Select |  |  |  |  | Select | C5 | C10
98 | 11.2 | Electrolyte fill and charge status on delivery : | Select | Select |  |  |  | Select | manufacturer's standard | dry and discharged | dry and charged | wet and charged | filled and discharged | filled and charged
99 | 5.6 | Maximum permissible ripple current (rms) : | Select | Select | % |  |  | Select | manufacturer's standard | 5 | 2 | 1
100 | 7 | End of discharge voltage : | Input Data | Input Data | V d.c.
101 | 6.2 | Maximum fault current (fully charged) : | Input Data |  | A
102 | 6.2 | Maximum fault current (end of discharge) : | Input Data |  | A
103 | 4.3 | Maximum hydrogen emission from cell : | Input Data |  |  |  |  | Select
104 |  | BATTERY CHARGING CHARACTERISTICS
105 | 8 | Float charge (constant voltage) : | Input Data |  | V d.c.
106 | 8 | Float charge (maximum voltage) : | Input Data |  | V d.c.
107 | 8 | Boost charge (constant voltage) : | Input Data |  | V d.c.
108 | 8 | Boost charge (maximum voltage) : | Input Data |  | V d.c.
109 | 8 | Boost charging (constant current) : | Input Data |  | A
110 | 8 | Equalizing charge (constant voltage) : | Input Data |  | V d.c.
111 | 8 | Equalizing charge (maximum voltage) : | Input Data |  | V d.c.
112 |  | SPECIAL TOOLS
113 | 9.2.1 | Insulated spanner or wrench : | No |  |  |  |  | Select | Yes | No
114 | 9.2.1 | Handheld digital voltmeter : | No |  |  |  |  | Select | Yes | No
115 | 9.2.1 | Electrically insulated and chemical resistant gloves and face shield : | No |  |  |  |  | Select | Yes | No
116 | 9.2.1 | Chemical resistant apron : | No |  |  |  |  | Select | Yes | No
117 | 9.2.2 | Densimeter/hydrometer (for flooded lead-acid batteries) : | No |  |  |  |  | Select | Yes | No
118 | 9.2.2 | Vent plug mounted thermometer : | No |  |  |  |  | Select | Yes | No
119 | 9.2.2 | Plastic jug, funnel and rubber bulb electrolyte dropper : | No |  |  |  |  | Select | Yes | No
120 | 9.2.4 | Battery lift or removal tool : | No | No |  |  |  | Select | Yes | No
Note on C6: Specify supplier's name, if supplier is not the manufacturer.
Note on C7: Select the stage of procurement that this data sheet is being issued.
Note on C8: Specify confirmed purchase order details.
Note on C9: Specify battery manufacturer's name.
Note on C10: Specify the product series, range, model number, etc.
Note on C11: Purchaser to specify the intended application of the batteries.
Note on C12: Select the desired battery technology. For any other battery technology, specify details in the additional notes.
Note on C13: Specify the minimum acceptable voltage for the load to calculate the number of cells for the specified end of discharge voltage.
Note on C14: Specify the desired battery bank voltage.
Note on C15: Select whether the battery load profile is attached or not.
Note on C16: Specify the desired autonomy time in minutes, if the load profile is not provided. Otherwise mention "see load profile".
Note on C17: Specify the rated capacity of the battery at 20 °C (± 5 °C). Load profile to be provided for vendor (as part of requisition) to verify the cell capacity.
Note on C18: Select CAS level as applied in IOGP S-701Q, Annex A.
Note on C21: Select the desired cell container material (flame retardant).
Note on C22: Select the connection method used for forming the battery bank.
Note on C23: Select whether the battery bank is to be placed on a rack, cabinet, enclosure or no such requirement.
Note on C24: Select the number of tiers to be considered in the rack, cabinet or enclosure.
Note on C25: Select the number of steps required in each tier of the rack or cabinet.
Note on C26: Specify the minimum vertical distance between the two tiers of batteries on rack or cabinet to permit unrestricted free, safe access for cell electrolyte level monitoring, water topping up, measurements and cell replacement.
Note on C27: Select the type of inter-cell connectors between the tiers
Note on C28: Select whether a spill containment system is required to be provided by the supplier.
Note on C29: Select if additional system is envisaged for monitoring of storage energy batteries including the mounting provision (trunking, sensors, etc.).
Note on C30: Select inclusion of temperature sensor mounting provision in scope of supply, if temperature controlled charging is envisaged.
Note on C31: Select whether the provision is required for battery isolation switches to be installed in the parallel strings in case of large capacity battery banks.
Note on C32: Purchaser to specify length of the allocated space for batteries (maximum battery rack/cabinet footprint dimension). In case of space constraint in height, mention the limiting value in additional comments.
Note on C33: Purchaser to specify depth of the allocated space for batteries (maximum battery rack/cabinet footprint dimension). In case of space constraint in height, mention the limiting value in additional comments.
Note on C34: Specify the battery cable size to be terminated at the terminal cell.
Note on C35: Specify the number of runs of battery cable per polarity to be terminated at the terminal cell.
Note on C36: Purchaser to specify additional language to be used for describing caution, danger and warning information on equipment labels.
Note on C38: Select the material to be used for fabrication of the battery rack.
Note on C39: Select the maximum height from the top of battery on the top tier to the floor considering the average height of the maintenance staff or the availability of floor space in battery room.
Note on C40: The overall length of the battery rack may be specified.
Note on C41: The overall width of the battery rack may be specified.
Note on C42: The overall height of the battery rack may be specified.
Note on C43: Supplier to declare the overall mass of the rack without batteries.
Note on C44: Supplier to declare the overall mass of the rack with batteries.
Note on C45: Supplier to specify the GA drawing number of the rack assembly.
Note on C47: Select the cabinet or enclosure material.
Note on C48: Specify the overall cabinet or enclosure length.
Note on C49: Specify the overall cabinet or enclosure width.
Note on C50: Specify the overall cabinet or enclosure height.
Note on C51: Specify the overall cabinet or enclosure mass without batteries.
Note on C52: Specify the overall cabinet mass with batteries.
Note on C53: Supplier to specify the GA drawing number of the cabinet or enclosure.
Note on C54: Select cable entry location based on the installation planned.
Note on C55: Supplier to select the type of cable entry considered for the cabinet (gland plate or MCT).
Note on C56: Select choice of external paint colour for cabinet. If other selected, use additional notes to specify.
Note on C57: Select choice of canopy for cabinet.
Note on C58: Select choice of cooling method for cabinet.
Note on C60: Specify in mm the clearance dimension required in front of rack or cabinet.
Note on C61: Specify in mm the clearance dimension required in the side of rack or cabinet.
Note on C62: Specify in mm the clearance dimension required in the rear of rack or cabinet.
Note on C64: Select choice of battery installation site.
Note on C65: Select as per location of storage energy battery.
Note on C66: Select ingress protection as per the installation location with cabinet or enclosure doors closed.
Note on C67: Select ingress protection as per the installation location with cabinet or enclosure doors opened.
Note on C68: Supplier to specify if any special safety equipment are required during monitoring and maintenance. If "Yes", use additional notes to provide detail.
Note on C69: Specify minimum ambient temperature expected during operation in case when HVAC system fails.
Note on C70: Specify maximum ambient temperature expected during operation in case when HVAC system fails.
Note on C71: Specify the normal ambient temperature expected during operation when HVAC system is functional.
Note on C72: Specify maximum relative humidity expected during operation.
Note on C73: Specify temperature at which relative humidity is specified while in operation.
Note on C74: Specify installation altitude above mean sea level.
Note on C75: Specify minimum ambient temperature expected during storage and transportation.
Note on C76: Specify maximum ambient temperature expected during storage and transportation.
Note on C77: Specify maximum relative humidity expected during storage and transportation.
Note on C78: Specify temperature at which relative humidity is specified during storage and transportation.
Note on C79: Specify the reference document number along with relevant information for rack design suitable for seismic conditions specified.
Note on C80: Select choice of battery storage site prior to its installation.
Note on C81: Specify unusual conditions expected during operation.
Note on C82: Specify unusual conditions expected during storage and transportation.
Note on C84: Select the area classification of the battery room.
Note on C85: Select the hazard zone classification within the battery room.
Note on C86: Select the minimum gas subdivision and temperature class for equipment in the battery room other than batteries.
Note on C87: Supplier to specify the recommended ventilation flow rate required to avoid hazardous environment in the room.
Note on C89: Specify the nominal DC voltage.
Note on C90: Select the plate type of lead-acid batteries.
Note on C91: Select the plate type for Ni-Cd batteries.
Note on C92: Specify the required service life for the batteries.
Note on C93: Specify the float service life as declared for the batteries.
Note on C94: Supplier to specify the shelf life (storage) of the selected battery.
Note on C95: Specify the quantity of cells and strings as per the battery bank arrangement.
Note on C96: Specify the charge/discharge (full charge and full discharge) cycles claimed by supplier.
Note on C97: Select the discharge rate of the selected cell.
Note on C98: Select the status (electrolyte fill and charge) of battery before it is transported.
Note on C99: Select the value of maximum permissible ripple current as a percentage of the numerical Ah (C10) capacity of batteries.
Note on C100: Specify the lowest limit of terminal voltage of cell up to which the cell will be discharged.
Note on C101: Specify the maximum fault current that the fully charged battery bank can deliver, without battery charger or externally connected sources.
Note on C102: Specify the maximum fault current that the fully discharged battery bank (cells reached end of discharge voltage at terminal) can deliver, without battery charger or externally connected sources.
Note on C103: Supplier to specify the maximum hydrogen evolution, depending on the battery technology, for all operating conditions at the maximum temperature.
Note on C105: Supplier to specify the constant voltage for float charging a cell.
Note on C106: Supplier to specify the maximum voltage for float charging a cell.
Note on C107: Supplier to specify the constant voltage for boost charging a cell.
Note on C108: Supplier to specify the maximum voltage for boost charging a cell.
Note on C109: Supplier to specify the constant current for boost charging a cell.
Note on C110: Supplier to specify the constant voltage for equalizing charge of a cell.
Note on C111: Supplier to specify the maximum voltage for equalizing charge of a cell.
Note on C113: Select whether an insulated spanner or wrench is required for tightening the cells connection hardware.
Note on C114: Select whether a handheld digital voltmeter for measuring the cell voltage at the terminals is required.
Note on C115: Select whether these regular protective items (PPEs) are to be supplied.
Note on C116: Select whether this regular protective item (PPE) is to be supplied.
Note on C117: Select whether a densimeter or hydrometer (for flooded lead-acid batteries) is required for measuring the density or specific gravity of the electrolyte.
Note on C118: Select whether a vent plug mounted thermometer (for flooded lead acid batteries) is required for measuring the temperature of the electrolyte.
Note on C119: Select whether a plastic jug, funnel and rubber bulb electrolyte dropper is required for electrolyte topping.
Note on C120: The battery lift or removal tool should be specified or supplied if the weight of cell is greater than 25 kg.

## Supplement
Row |  | S-704D Data Sheet for Batteries (IEC) | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95

## Guidance
Data Sheet for
Batteries (IEC)
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-740 Specification for Batteries (IEC).
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.