## Errata 1
Date of issue:
June 2022
Affected publication:
IOGP S-736D, Procurement Data Sheet for Low-voltage AC Drives (IEC), First Edition, September 2021
ERRATA 1
Drop-down lists added where missing in column F.
List of cells affected
F9, F12, F16, F17, F19, F24, F25, F29, F30, F34, F35, F36, F39, F40, F41, F42, F44, F45, F46, F47, F52, F53, F54, F56, F58, F59, F61, F62, F65, F69, F81, F82, F83, F84, F85, F86, F87, F92, F100, F103, F105, F108, F110 and F113.
Cell F9 example

## Front & Preliminaries
|  |  |  | SPECIFICATION | June 2022
|  |  |  | IOGP S-736D | Version 1.01
FIRST EDITION (SEPTEMBER 2021), ERRATA 1
Procurement Data Sheet for
Low-voltage AC Drives (IEC)
Revision history
| VERSION | DATE | PURPOSE
| 1.01 | June 2022 | Errata 1
| 1.01 | September 2021 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-736D Data Sheet for
Low-voltage AC Drives (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
S-736D Data Sheet for
Low-voltage AC Drives (IEC)
Introduction
The purpose of this procurement data sheet is to define customer specific requirements for the procurement of low-voltage AC drives in accordance with IOGP S-736 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the customer for technical evaluation purposes. Additional customer supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-736), information requirements specification (IOGP S-736L) and quality requirements specification (IOGP S-736Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Procurement Data Sheet
Row | S-736D Procurement Data Sheet for Low-voltage AC Drives (IEC) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General
7 | 7.2 | Manufacturer : | input data |  | input data
8 | 7.2 | Package supplier : | input data |  | input data
9 |  | Order status : | select |  | select | [5 empty] | select | for enquiry | for purchase
10 | 7.2 | Model number : | input data |  | input data
11 |  | Project Requirements
12 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
13 | 5.9.2.3 | Project country : | input data |  | input data
14 | 5.9.2.3 | Project region : | input data |  | input data
15 |  | Environmental conditions
16 | 5.9.2.3 | Location/area : | select |  | select | [5 empty] | select | onshore | offshore – fixed | offshore – floating | marine (ship)
17 | 5.9.2.1.1, Table 12 | Location environment : | indoor conditioned |  | indoor conditioned | [5 empty] | select | indoor conditioned | indoor unconditioned | outdoor unconditioned
18 | Table 14 | Seismic spectral response acceleration at short period (SDS) in accordance with ACSE 7 : | not applicable |  | not applicable
19 | Table 14 | Seismic activity zone in accordance with IEC 60721-2-6 : | not applicable |  | not applicable | [5 empty] | select | not applicable | Zone 1 | Zone 2 | Zone 3 | Zone 4
20 | Table 12 | Minimum ambient temperature (operation) : | input data | °C | input data | °C
21 | Table 12 | Maximum ambient temperature (operation) : | input data | °C | input data | °C
22 | Table 12 | Maximum relative humidity (operation) : | input data | % | input data | %
23 | Table 12 | Temperature at which relative humidity is specified (operation) : | input data | °C | input data | °C
24 | Table 12 | Maximum altitude (operation) : | up to 1 000 | m | up to 1000 | m |  |  |  |  | select | up to 1 000 | greater than 1 000
25 | 5.9.2.3, 6.6.3.8.3 | Maximum sound pressure level at 1 m distance : | manufacturer standard |  | manufacturer standard | [5 empty] | select | manufacturer standard | other
26 | 5.9.1 ,5.9.2.3 | Additional or unusual conditions (storage and transportation) : | input data |  | input data
27 | 5.9.1 ,5.9.2.3, Table 12 | Additional or unusual conditions (operation) : | input data |  | input data
28 |  | Electrical system data
29 | 5.3.2.2 | Voltage : | select | V AC | select | V AC |  |  |  |  | select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | other
30 | 5.3.2.2 | Frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
31 | 5.4.1.5.2 | Minimum short circuit current : | input data | kA | input data | kA
32 | 5.4.1.5.2 | Maximum symmetrical fault current : | input data | kA | input data | kA
33 | 5.4.1.5.2 | Power supply quality : | class 2 |  | class 2
34 | 5.4.1.5.2 | EMC application environment : | second |  | second | [5 empty] | select | first | second
35 | 5.15, 5.4.1.5.2 | AC power distribution system - compatibility : | select |  | select | [5 empty] | select | TN-C | TN-S | TN-C-S | TT | IT
36 | 5.4.1.5.2, Table 12 | Overvoltage category : | III |  | III | [5 empty] | select | III | IV
37 |  | BDM/CDM
38 |  | General
39 | Clause 1 | Application : | select |  | select | [5 empty] | select | agitator | centrifugal compressor | centrifugal fan | centrifugal pump | extruder | positive displacement pump | reciprocating compressor | reciprocating pump | screw pump
40 | 5.2.3 | BDM configuration : | select |  | select | [5 empty] | select | VSI | VSI with PWM | CSI | LCI
41 | 5.2.3 | Converter pulses : | 6 |  | 6 | [5 empty] | select | 6 | 12 | 18 | 24
42 | 5.3.5 | Control supply : | select |  | select | [5 empty] | select | drive internal | external - direct | external - via internal control transformer
43 | 5.3.5 | Internal control transformer rating : | input data | kVA | input data | kVA
44 | 5.2.3, 5.4.1.4.1.2 a), 5.4.1.4.1.2 b), 5.4.1.4.1.3 a), 5.4.1.4.1.3 b), 5.4.1.4.1.3 c), 5.4.1.4.1.1 | Dynamic braking required : | not required |  | not required | [5 empty] | select | not required | required-resistive braking (chopper) | required-regenerative braking (AFE)
45 | 5.3.6.3.4.1 | Output filter type : | not applicable |  | not applicable | [5 empty] | select | not applicable | output reactor | common mode filter | dv/dt filter | sine wave filter
46 |  | Drive parameter setting list : | not required |  | not required | [5 empty] | select | not required | required
47 | 7.5.2 | Certification (additional) : | not applicable |  | not applicable | [5 empty] | select | not applicable | DNV-GL | Lloyds | ABS/USCG | other
48 |  | BDM/CDM output ratings
49 | 5.3.3.1 | Continuous rated output current : | input data | A | input data | A
50 | 5.3.3.1, 5.3.3.3 | Overcurrent capability : | input data | p.u/min | input data | p.u/min
51 |  | BDM/CDM performance
52 | 5.4.1.5.1 | Drive operation : | two quadrants |  | two quadrants | [5 empty] | select | two quadrants | four quadrants
53 | 5.4.1.5.1 | Control type : | select |  | select | [5 empty] | select | volts/hertz | sensorless vector | flux vector | sensorless flux vector | field oriented | sensorless field oriented
54 | 5.10 | Converter duty class : | II |  | II | [5 empty] | select | I | II | III | IV | V
55 |  | Interface/ports
56 | 5.4.4.2.6 | Communication protocol : | select |  | select | [5 empty] | select | Profinet | Profibus | EtherNet/IP | Modbus TCP | Modbus RTU | other
57 |  | Analog input
58 | 5.4.4.2.2 | Number of channels (voltage signal) : | 2 |  | 2 | [5 empty] | select | not applicable | 1 | 2
59 | 5.4.4.2.2 | Number of channels (current signal) : | 2 |  | 2 | [5 empty] | select | not applicable | 1 | 2
60 |  | Analog output
61 | 5.4.4.2.3 | Number of channels (voltage signal) : | 1 |  | 1 | [5 empty] | select | not applicable | 1 | 2
62 | 5.4.4.2.3 | Number of channels (current signal) : | 2 |  | 2 | [5 empty] | select | not applicable | 1 | 2
63 |  | Digital input
64 | 5.4.4.2.4 | Number of channels : | input data |  | input data
65 | 5.4.4.2.4 | PTC thermistor input : | 1 |  | 1 | [5 empty] | select | not applicable | 1 | 2
66 |  | Digital output
67 | 5.4.4.2.5 | Number of channels : | input data |  | input data
68 |  | Cooling
69 | 5.2.4.1, 5.2.4.3 | Cooling type : | forced air cooled |  | forced air cooled | [5 empty] | select | forced air cooled | water cooled | manufacturer standard
70 | 5.2.4.3 | Water inlet temperature : | input data | °C | input data | °C
71 |  | Enclosure
72 |  | Dimensions
73 | 5.9.2.2.2 | Height : | input data | mm | input data | mm
74 | 5.9.2.2.2 | Length : | input data | mm | input data | mm
75 | 5.9.2.2.2 | Depth : | input data | mm | input data | mm
76 | 5.9.2.2.2 | Weight : | input data | kg | input data | kg
77 | 5.9.2.2.2 | Front access clearance dimensions for operation and maintenance : | input data | mm | input data | mm
78 | 5.9.2.2.2 | Side clearance for ventilation (if required) : | input data | mm | input data | mm
79 | 5.9.2.2.2 | Rear clearance for ventilation (if required) : | input data | mm | input data | mm
80 |  | General
81 | 5.9.2.1.1 | Cable entry location : | select |  | select | [5 empty] | select | top | bottom | both top & bottom
82 | 5.9.2.2.2 | Mounting arrangement : | select |  | select | [5 empty] | select | wall | floor
83 | 5.9.2.1.1 | Degree of protection (with doors and/or covers closed) : | IP2X |  | IP2X | [5 empty] | select | IP2X | other
84 | 5.3.5 | Space heaters : | select |  | select | [5 empty] | select | required | not required
85 | 5.3.2.4, 5.3.3.3 | Local main disconnect and overcurrent protection device : | not required |  | not required | [5 empty] | select | required | not required
86 | 5.9.2.1.1 | Cable entry type : | select |  | select | [5 empty] | select | removable - undrilled plate | multi cable transit (MCT)
87 | 5.9.2.1.1 | Gland plate material : | select |  | select | [5 empty] | select | manufacturer standard | non-magnetic plate
88 |  | Motor
89 | 5.3.6.3.3.1 | Power rating : | input data | kW | input data | kW
90 | 5.3.6.3.3.1 | Voltage : | input data | V | input data | V
91 | 5.3.6.3.3.1 | Rated speed : | input data | rpm | input data | rpm
92 | 5.14 | Hazardous area classification : | select |  | select | [5 empty] | select | Zone 1 | Zone 2 | Zone 21 | Zone 22 | Division 1 | Division 2 | non-hazardous
93 | 5.3.6.3.6 | Minimum continuous operating speed : | input data | rpm | input data | rpm
94 | 5.3.6.3.6 | Maximum continuous operating speed : | input data | rpm | input data | rpm
95 | 5.3.6.3.3.1 | Starting torque : | input data | Nm | input data | Nm
96 | 5.4.1.4.1.2 a), 5.4.1.4.1.2 b), 5.4.1.4.1.3 a), 5.4.1.4.1.3 b), 5.4.1.4.1.3 c) | Moment of inertia of the load : | input data | kg·m² | input data | kg·m²
97 | 5.3.6.3.4.1 | Motor cable length : | input data | m | input data | m
98 |  | Transformer
99 |  | Converter transformer
100 | 5.3.6.2.1 | Transformer required : | not required |  | not required | [5 empty] | select | not required | required
101 | 5.3.6.2.1, 5.3.6.2.2 | Transformer rating : | input data | kVA | input data | kVA
102 | 5.3.6.2.1, 5.3.6.2.2 | Transformer voltage ratio : | input data |  | input data
103 | 5.3.6.2.1 | Transformer type : | dry type |  | dry type | [5 empty] | select | dry type | liquid filled
104 |  | Input transformer
105 | 5.3.6.2.1 | Transformer required : | not required |  | not required | [5 empty] | select | not required | required
106 | 5.3.6.2.1, 5.3.6.2.2 | Transformer rating : | input data | kVA | input data | kVA
107 | 5.3.6.2.1, 5.3.6.2.2 | Transformer voltage ratio : | input data |  | input data
108 | 5.3.6.2.1 | Transformer type : | dry type |  | dry type | [5 empty] | select | dry type | liquid filled
109 |  | Output transformer
110 | 5.3.6.2.1 | Transformer required : | not required |  | not required | [5 empty] | select | not required | required
111 | 5.3.6.2.1, 5.3.6.2.2 | Transformer rating : | input data | kVA | input data | kVA
112 | 5.3.6.2.1, 5.3.6.2.2 | Transformer voltage ratio : | input data |  | input data
113 | 5.3.6.2.1 | Transformer type : | dry type |  | dry type | [5 empty] | select | dry type | liquid filled
Note on C4: Indicate the unique tag number for the equipment.
Note on C5: A functional description of the tag.
Note on C7: Specify the name of the BDM or BDM/CDM manufacturer.
Note on C8: Specify the name of the entity who is responsible for the design and supply of the complete package (system integrator, if different from the OEM).
Note on C9: Advise the order status. This allows both the purchaser and the manufacturer to define values more accurately as they become available. (Default - select)
Note on C10: Supplier to advise the model number of the BDM/CDM.
Note on C12: Select CAS level as applied in IOGP S-736Q, Annex A. CAS A reflects the highest risk and associated extent of verification. CAS D is the lowest.
Note on C13: Advise the country for the final installation of the BDM/CDM to enable the manufacturer to provide the required product marking and certification for the region.
Note on C14: Geographic location of the project within a country which will determine the applicability of local regulatory requirements.
Note on C16: Select the location/area where the LV AC drive is to be installed. Purchaser to additionally specify pitch and roll requirements in the ‘Additional notes’ column, if the location/area selected is either offshore-floating or marine (ship). (Default-select)
Note on C17: Select environmental service conditions in accordance with Table 12. (Default - indoor conditioned)
Note on C18: Where seismic certification in accordance with ASCE 7 is required, specify the SDS value as defined in ASCE 7 for the location where the drive is used. Where seismic certification is not required, state ‘not applicable’.
Note on C19: Where seismic certification in accordance with IEC 60068-3-3 is required, specify the seismic activity zone as defined in IEC 60721-2-6 for the location where the drive is used. Where seismic certification is not required, select ‘not applicable’.
Note on C20: Specify the minimum ambient temperature expected during operation.
Note on C21: Specify the maximum ambient temperature expected during operation.
Note on C22: Specify the maximum relative humidity expected during operation.
Note on C23: Specify the temperature at which relative humidity is specified while in operation.
Note on C24: Select the installation altitude above mean sea level. For altitudes greater than 1 000 m, specify the altitude value in the ‘Additional notes’ column. (Default - up to 1 000 )
Note on C25: Select 'other' if not manufacturer standard and specify in the ’Additional notes’ column, the acceptable limit of maximum sound pressure level dB(A) measured at one metre distance in any direction from the source. (Default - manufacturer standard)
Note on C26: Specify additional or unusual conditions expected during storage and transportation (e.g. salt laden, H2S, dust, vibrations, snow, ice).
Note on C27: Specify additional or unusual conditions expected during operation (e.g. salt laden, H2S, dust, vibrations).
Note on C29: Specify the input supply voltage for the BDM/CDM in accordance with IEC 61800-2, 5.3.2.2. For other voltages at the input of CDM, specify the value in the ‘Additional notes’ column. (Default - select)
Note on C30: Select the supply frequency in accordance with IEC 61800-2, 5.3.2.2. (Default - select)
Note on C31: Specify the minimum short-circuit current of the supply system.
Note on C32: Specify the maximum fault current of the supply system in accordance with IEC 61800-2, 5.4.1.5.2.
Note on C33: Select the input power supply quality in accordance with IEC 61000-2-4. (Default - class 2)
Note on C34: Specify the application environment for EMC in accordance with IEC 61800-3. First environment generally applies to domestic and commercial premises. Second environment applies to industrial networks. (Default - second)
Note on C35: Select the applicable type of earthing system of the main power supply to the drive in accordance with IEC 61800-5-1. EMC filters connected to earth on the line side are prohibited in an IT earthing system. (Default - select).
Note on C36: Specify the overvoltage category in accordance with IEC 61800-5-1. Default is category III and aligns with the default in IOGP S-560. (Default - III)
Note on C39: Select the intended application of the BDM/CDM unit. Any other application or specific information is mentioned in the ‘Additional notes’ column. (Default - select)
Note on C40: Select the required BDM configuration for the drive or let the manufacturer select based on the application mentioned. (Default - select)
Note on C41: Select the number of pulses for the converter design. Converter transformer should be used in converters with pulses more than 6. (Default - 6)
Note on C42: Select the source of control supply, whether the wiring uses drive internal control voltage or uses an external supply (directly or via internal control transformer). Specify the control voltage of circuit in the ‘Additional notes’ column.(Default-select)
Note on C43: Specify the internal control supply transformer kVA rating. Specify the voltage transformation details in the ‘Additional notes’ column.
Note on C44: Select how the braking is intended and how the regenerative energy is handled, using a braking chopper with resistor or an active infeed converter (AIC). (Default - not required)
Note on C45: Select the type of output filter in accordance with design of BDM/CDM. (Default – not applicable)
Note on C46: Select whether a drive parameter setting list is required as defined in IOGP S-736L. (Default - not required)
Note on C47: Select the certification requirement according to project. Specify any other certification requirement in the ‘Additional notes’ column. (Default - not applicable)
Note on C49: Specify the continuous rated output current without overload for the BDM/CDM at the maximum ambient air temperature.
Note on C50: Specify the overcurrent capability of the BDM/CDM in accordance with IEC 61800-2, Table 8.
Note on C52: Select the number of quadrants that the drive can perform its operation. (Default - two quadrants)
Note on C53: Select the drive control method to ensure desired speed and torque regulation of motor as per application. Some control types need feedback sensors (encoders, etc.) to achieve control and such motors have sensor mounting provisions. (Default - select)
Note on C54: Duty class to be specified in accordance with IEC 60146-1-1. Default is class II. 110 % overload is applicable for variable torque application and 150 % overload is applicable for constant torque application. (Default - II)
Note on C56: Select from among the listed (most commonly used) protocols. Any other protocol should be mentioned in the ‘Additional notes’ column. Redundant communication cards, if required, should be mentioned in the ‘Additional notes’ column. (Default - select)
Note on C58: Select the number of channels of analog inputs (voltage signal) required in the BDM/CDM. Specify whether the voltage signal is 0-10 V or -10 V to +10 V in the ‘Additional notes’ column. (Default - 2)
Note on C59: Select the number of channels of analog inputs (current signal) required in the BDM/CDM. Specify whether the current signal is 4-20 mA or 0-20 mA in the ‘Additional notes’ column. (Default - 2)
Note on C61: Select the number of channels of analog outputs (voltage signal) required in the BDM/CDM. Specify whether the voltage signal is 0-10 V or -10 V to +10 V in the ‘Additional notes’ column. (Default - 1)
Note on C62: Select the number of channels of analog outputs (current signal) required in the BDM/CDM. Specify whether the current signal is 4-20 mA or 0-20 mA in the additional notes’ column. (Default - 2)
Note on C64: Specify the number of digital inputs provided in the BDM/CDM. 6 digital inputs are generally provided by most suppliers. Specify control voltage, current rating, input type (sink or source) in the ‘Additional notes’ column.
Note on C65: Select the number of PTC thermistor input required in the drive. Specify in the ‘Additional notes’ column if any externally powered thermistor relay unit is required as interface for the drive. (Default - 1)
Note on C67: Specify the number of DOs provided in the BDM/CDM. 2 DOs and 3 relay outputs are generally provided by most suppliers. Specify relay (control voltage, contact rating), opto-coupler (control voltage, sink or source) in the ‘Additional notes’ column.
Note on C69: Select the type of cooling for the BDM/CDM. Specify the type of water cooling medium (fresh water / sea water) in the ’Additional notes’ column. (Default - forced air cooled)
Note on C70: Specify the water temperature at the inlet of the drive heat exchanger.
Note on C73: Specify the height of the BDM/CDM enclosure. For BDM/CDM mounted within cabinet, specify the height of the cabinet. Total height including the cooling fans and louvers to be indicated.
Note on C74: Specify the length of the BDM/CDM enclosure. For BDM/CDM mounted within cabinet, specify the length of the cabinet.
Note on C75: Specify the depth of the BDM/CDM enclosure. For BDM/CDM mounted within cabinet, specify the depth of the cabinet.
Note on C76: Specify the total weight of the BDM/CDM enclosure.
Note on C77: Specify the front access clear dimension in mm, required for operation and maintenance.
Note on C78: Specify the side clear dimension in mm for ventilation (if required).
Note on C79: Specify the rear clear dimension in mm for ventilation (if required).
Note on C81: Select the power cable entry for the BDM/CDM enclosure. (Default - select)
Note on C82: Select the mounting arrangement of the BDM/CDM, whether wall mounted, within a floor-mounted cabinet or self-standing floor mounting. (Default - select)
Note on C83: Select ingress protection rating in accordance with IEC 60529 for BDM with doors closed in normal operation. (Default - IP2X).
Note on C84: Select whether space heaters are required within the BDM/CDM cabinet based on the variation in ambient temperature. Specify the supply voltage rating of the heaters in the ‘Additional notes’ column. (Default - select)
Note on C85: Select whether a local main disconnect and overcurrent protection device is required within the cabinet. (Default - not required)
Note on C86: Select the type of cable entry required for the cabinet (gland plate or MCT). (Default - select)
Note on C87: Select the gland plate / MCT material type considering the type of power cable (1C or 3C). (Default - select)
Note on C89: Specify the kW rating of the motor driven from the BDM/CDM. In case the motor is sufficiently de-rated, the shaft power required by driven equipment can be mentioned in the ‘Additional notes’ column.
Note on C90: Specify the rated operating voltage of the motor fed from the BDM/CDM.
Note on C91: Specify the rated speed of the motor fed from the BDM/CDM.
Note on C92: Select the area classification of the motor (fed from the BDM/CDM) in accordance with IEC 60079-10, API RP 505 or API RP 500. (Default - select)
Note on C93: Specify the minimum continuous motor operating speed required by the driven equipment (minimum speed from the operating speed range).
Note on C94: Specify the maximum continuous motor operating speed required by the driven equipment (maximum speed from the operating speed range).
Note on C95: Specify the starting torque required to drive the motor.
Note on C96: Specify the moment of inertia (MR²) of the load for dynamic braking application.
Note on C97: Specify the approximate motor cable length (from the BDM/CDM to the motor) to evaluate the requirement of output component (e.g. reactor, filters).
Note on C100: Select whether a transformer is required before the CDM (converter transformer). (Default - not required)
Note on C101: Specify the rating of the converter transformer, if any.
Note on C102: Specify the voltage ratio of the converter transformer.
Note on C103: Select whether the type of transformer is dry type or liquid filled type. (Default - dry type)
Note on C105: Select whether the input transformer is required before the CDM (other than converter transformer). This could be a step-down transformer. (Default - not required)
Note on C106: Specify the rating of the input transformer, if any.
Note on C107: Specify the voltage ratio of the input transformer.
Note on C108: Select whether the type of transformer is dry type or liquid filled type. (Default - dry type)
Note on C110: Select whether transformer is required at the output of converter.
Note on C111: Specify the rating of the output transformer, if any.
Note on C112: Specify the voltage ratio of the output transformer.
Note on C113: Select whether the type of transformer is dry type or liquid filled type. (Default - dry type)

## Supplement
Row |  | S-736D Procurement Data Sheet for Low-voltage AC Drives (IEC) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
9
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
S-736D Procurement Data Sheet for
Low-voltage AC Drives (IEC)
Guidance on the use of this procurement data sheet
To be used in conjunction with :
IOGP S-736 Supplementary Specification to IEC 61800-2 Low-voltage AC Drives.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data