## Front & Preliminaries
|  |  |  | SPECIFICATION | September
|  |  |  | S-727L | 2021
Information Requirements for
Metal-Enclosed Low-Voltage
Power Circuit Breaker Switchgear
(IEEE Std C37.20.1)
Revision history
| VERSION | DATE | PURPOSE
| 1 | September 2021 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-727L Information Requirements for
Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear
(IEEE Std C37.20.1)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
S-727L Information Requirements for
Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear
(IEEE Std C37.20.1)
Introduction
The purpose of this information requirements specification (IRS) is to define information requirements for the procurement of metal-enclosed low-voltage power circuit breaker switchgear in accordance with IOGP S-727 for application in the petroleum and natural gas industries. The IRS defines the information requirements, including format, timing and purpose, for information to be provided by the supplier. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the specification (IOGP S-727), procurement data sheet (IOGP S-727D) and quality requirements specification (IOGP S-727L) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification

## Instructions
S-727L Information Requirements for
Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear
(IEEE Std C37.20.1)
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS Structure Contents
| 1 | 'Front & Preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes / No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information Submission Abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS .
Column K — 'Translation Required' (Yes / No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable Formats
Column F — 'CFIHOS Discipline Document Type Code' relates to the CFIHOS discipline document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3 below. Metadata listed below are as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The document master to which this revision is related |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification |  |  | The Export Control Rule that is applicable for the document revision (e.g., ECCN, EAR). |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
| Security classification |  |  | Indicates internal Owner-Operator access restriction applicable for the document |  |  | TBA
Table 3 — Supplier Deliverable Metadata

## Requirements
S-727L Information Requirements for Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear (IEEE Std C37.20.1)
Requirements
Column | Heading - Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Information Deliverable Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S727-IR-20 | Supplier master information schedule |  | Information Deliverables List | No | For Acceptance |  | WAO | Yes |  | No
S727-IR-21 | Delivery schedule |  | Delivery/Production Schedule | Yes | For Information |  | WAO | No |  | No
S727-IR-22 | Progress report | Required for CAS A, CAS B, CAS C | Progress Report | - | - |  | WAO (Monthly) | - |  | No
S727-IR-23 | Quality plan | Required for CAS A, CAS B | Quality Plan | - | - |  | WAO | - |  | No
S727-IR-24 | Sub-vendor delivery schedule | Required for CAS A, CAS B | Sub-Supplier List | - | - |  | WAO | - |  | No
S727-IR-25 | Inspection and test plan for complete package |  | Inspection and Test Plan (ITP) | No | For Information |  | WAO | No |  | No
S727-IR-26 | Handling, lifting, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No |  | No
S727-IR-27 | Non-conformance records |  | Non-conformance records | No | For Acceptance |  | WPTD | Yes |  | No
S727-IR-28 | Concession requests |  | Concession request | Yes | For Acceptance |  | WPTF | Yes |  | No
S727-IR-29 | Pre-production planning (minutes of meeting) | Required for CAS A, CAS B | Minutes of meeting | - | - |  | WAO | No |  | No
Technical Information Deliverables
S727-IR-30 | Wiring Diagram |  | Wiring Diagram | No | For Information |  | WAO | Yes |  | No | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings.
S727-IR-31 | Single Line Diagram |  | Single Line Diagram | No | For Acceptance |  | WAO | Yes |  | No | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings.
S727-IR-32 | Schematic Diagram |  | Schematic Diagram | No | For Acceptance |  | WAO | Yes |  | No | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings.
S727-IR-33 | Name Plate Drawing |  | Name Plate Drawing | No | For Information |  | WAO | Yes |  | No | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings.
S727-IR-34 | General Arrangement Drawing |  | General Arrangement Diagram | Yes | For Information |  | WAO | Yes |  | No | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings.
S727-IR-35 | Detailed Drawing |  | Detailed Drawing | No | For Information |  | WAO | Yes |  | No | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings.
S727-IR-36 | Equipment Specification Sheet |  | Equipment Specification | No | For Information |  | WAO | Yes |  | No | Part of the drawing submittal package.
S727-IR-56 | Communication Network Overview |  | General Diagram | Yes | For Information |  | - | No |  | No | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings.
S727-IR-37 | Communication Block Diagram |  | Block Diagram | No | For Information |  | WAO | Yes |  | No | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings.
S727-IR-38 | Cable Size Calculation | Required for CAS A, CAS B, CAS C | Cable Size Calculation | - | - |  | WAO | - |  | No
S727-IR-61 | CT Burden Calculations | Required for CAS A, CAS B, CAS C | Instrument Calculations | - | - |  | WAO | - |  | No
S727-IR-39 | Heat Dissipation Calculation & Loads | Required for CAS A, CAS B, CAS C | Heat Dissipation Calculation & Loads | - | - |  | WAO | - |  | No
S727-IR-40 | Reliability & Availability Calculations and Obsolescence Plan | Required for CAS A, CAS B | Reliability, Availability and Safety Integrity Level Calculation | - | - |  | WAO | - |  | No
S727-IR-41 | Certificate Of Conformance | Required for CAS A, CAS B, CAS C | Certificate Of Conformance | - | - |  | WAO | - |  | No | UL 1558 listing
S727-IR-42 | Type Test Certificate |  | General Certificate | Yes | For Information |  | WAI | No |  | No | Arc Resistance certifications
S727-IR-43 | Regulatory Compliance Certificate |  | Regulatory Compliance Certificate | No | For Information |  | WPTD | Yes |  | No | ABS or USCG.
S727-IR-44 | Application Software |  | Application Software | No | For Information |  | WPTD | Yes |  | No | Only when required by the datasheet. This includes configuration files
S727-IR-45 | Bill Of Materials |  | Bill Of Materials | No | For Information |  | WAO | Yes |  | No | PDF is acceptable for approval drawings as part of the drawing submittal package. Native format is required for the as built drawings.
S727-IR-46 | Spare Part List |  | Spare Part List | No | For Information |  | WAO | Yes |  | No
S727-IR-47 | Commissioning Instruction |  | Commissioning Instruction | No | For Information |  | WAO | Yes |  | No
S727-IR-48 | Installation Manual |  | Installation Manual | No | For Information |  | WPTD | No |  | No | Installation Manual index, if required, should be provided in first revision of the document. When index agreed, Installation manual content shall be provided in subsequent revision of the document.
S727-IR-49 | Maintenance Manual |  | Maintenance Manual | No | For Information |  | WPTD | No |  | No | Maintenance Manual index, if required, should be provided in first revision of the document. When index agreed, Maintenance manual content shall be provided in subsequent revision of the document.
S727-IR-50 | Operating Manual |  | Operating Manual | No | For Information |  | WPTD | Yes |  | No | Operating Manual index, if required, should be provided in first revision of the document. When index agreed, Operating manual content shall be provided in subsequent revision of the document.
S727-IR-51 | Factory Acceptance Test (FAT) Procedure |  | Factory Acceptance Test (FAT) Procedure | No | For Acceptance |  | WPTT | No |  | No
S727-IR-52 | Routine Test Procedure |  | Routine Test Procedure | No | For Information |  | WPTT | Yes |  | No
S727-IR-53 | Factory Acceptance Test (FAT) Records |  | Factory Acceptance Test (FAT) Records | No | For Acceptance |  | WAT | No |  | No
S727-IR-54 | Packing List |  | Packing List | No | For Information |  | WPTD | No |  | No
Purchase Order Specific Information Requirements
Note on F20: Guidance Note: CAS A: For Information, CAS B: For Information, CAS C: For Information, CAS D: - (N/A)
Note on F21: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Information, CAS C: - (N/A), CAS D: - (N/A)
Note on F22: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Information, CAS C: - (N/A), CAS D: - (N/A)
Note on F23: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
Note on F27: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Information, CAS C: - (N/A), CAS D: - (N/A)
Note on F29: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
Note on F30: Guidance Note: Drawing approval required prior to the start of manufacturing.
Note on F31: Drawing approval required prior to the start of manufacturing.
Note on F32: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing, CAS C: For Acceptance (before start of manufacturing, CAS D: For Information
Note on F33: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Acceptance (before start of manufacturing), CAS D: For Information
Note on F34: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
Note on F35: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
Note on F36: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
Note on F37: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information
Note on F38: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: - (N/A)
Note on I38: Required as built: CAS A: Yes, CAS B: Yes, CAS C: Yes, CAS D: No
Note on F39: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: - (N/A)
Note on I39: Required for as built: CAS A: Yes, CAS B: Yes, CAS C: Yes, CAS D: No
Note on F40: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: - (N/A)
Note on I40: Required as built: CAS A: Yes, CAS B: Yes, CAS C: Yes, CAS D: No
Note on F41: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Information, CAS C: - (N/A), CAS D: - (N/A)
Note on E42: Guidance note: CAS A: Yes, CAS B: Yes, CAS C: Yes, CAS D: No
Note on F42: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing) CAS C: For Information CAS D: - (N/A)
Note on E43: Guidance note: CAS A: Yes, CAS B: Yes, CAS C: Yes, CAS D: N/A
Note on F43: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: - (N/A)
Note on F44: Guidance Note: CAS A: For Acceptance (before start of manufacturing) CAS B: For Acceptance (before start of manufacturing) CAS C: For Information CAS D: For Information
Note on F46: Guidance Note: CAS A: For Acceptance (before start of manufacturing), CAS B: For Acceptance (before start of manufacturing), CAS C: For Information, CAS D: For Information

## Definitions
S-727L Information Requirements for Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear (IEEE Std C37.20.1)
Definitions
Column | Heading - Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Discipline Document Type Code — CFIHOS discipline document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Deliverables
S727-IR-20 | Supplier master information schedule | Schedule of specific information deliverables developed by the Supplier and accepted by the Purchaser to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description, b. unique identification (code/number) in the Supplier's format unless agreed otherwise in the contract, c. planned submission arrangements including; purpose, formats, timing, frequency. Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S727-IR-21 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by supplier/sub-supplier. Schedule details typically include: a. Contractual milestones, b. Activity start/completion dates, durations, dependencies (Calendar Dates), c. Critical path and float, d. Outsourced services and equipment, e. Information deliverable submission dates identifying any execution activity dependencies. Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. NOTE: Schedule development tools, formats and submission protocols follow the supplier's standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S727-IR-22 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. NOTE: The frequency and scope of the progress report may also be modified by the terms and conditions in the purchase order |  | PDF | CFIHOS-70000300
S727-IR-23 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] |  | PDF
S727-IR-24 | Sub-vendor delivery schedule | Definition of processes, products or services that will be externally provided and the controls to be applied by the supplier to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . NOTE: ISO 9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. |  | Native
S727-IR-25 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated supplier, purchaser and independent party conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. This document will include dimensional, painting, general arrangement, component placement, wiring, clearances, cable entries, cleanliness, and functional testing. |  | PDF | CFIHOS-70000180
S727-IR-26 | Handling, lifting, shipping, storage and preservation procedure | Definition of practices to be followed during the storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container(s), b. special packing/unpacking/handling and lifting requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning, e. drawings shall be provided indicating size of shipping splits, center of gravity, weight, identification, and packing list of contents. NOTE: Copies of applicable lifting procedures are included in the delivery documentation which accompanies shipments of equipment. | (IOGP S-727, 7.20.2, 7.20.5, 7.20.6, 7.20.7) | PDF | CFIHOS-70000154
S727-IR-27 | Non-conformance records | Details of non-conformances raised by or to the supplier/sub-suppliers against technical requirements during manufacturing prior to or during the delivery of the products or services. Non-conformance is managed by the supplier in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. NOTE: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the purchaser in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S727-IR-28 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000389
S727-IR-29 | Pre-production planning (minutes of meeting) | Minutes of meeting from a pre-production planning. Items to be covered during this meeting includes ITP, point of contact for supplier and third party inspection company, overall quality process, and inspection schedule. |  | PDF | CFIHOS-70000223
Technical Information Deliverables
S727-IR-30 | Wiring Diagram | Diagram providing information on the circuitry of an object. Mandatory content of information: a. graphical symbols representing the objects; b. graphical symbols representing the connections among objects; c. reference designations; d. terminal designations; e. signal level conventions (applicable to logic signals); f. information necessary to trace paths and circuits (signal designations, location references); g. supplementary information necessary for the understanding of functions; h. point to point wiring details. Optional content of information: Technical data; Reference to other documents; Information about wiring performance; Cable and cable core identification. | (IOGP S-727, 7.1.3.3, 7.1.2.2.4, 7.1.2.5, 7.1.2.5.3, 7.1.3.3.5, 7.1.3.5.6, 7.1.3.5.7, 7.1.4.1.7, 7.1.5.2.5, 7.11.8, 7.15.12, 7.15.13, 7.15.16, 7.15.17, 7.15.18, 7.15.20, 7.16, 7.17, 7.18.1, 7.18.3, 7.18.5, 7.18.6) | Native | CFIHOS-70000268
S727-IR-31 | Single Line Diagram | A diagram depicting the major equipment items (motors, switchboards, transformers etc.) and their relationships within the facility electrical distribution system including details of fault levels, current ratings, fixed or withdrawable equipment unit type, and voltage ratings. | (IOGP S-727, 7.11.8.3, 7.11.8.4, 7.15.1, 7.15.7, 7.16.1.2, 7.16.3.1, 7.17.2, 7.17.3) | Native | CFIHOS-70000371
S727-IR-32 | Schematic Diagram | A pictorial representation of the main elements and functions of a control circuit for electrical equipment with input/output sources (switches, relays etc.) and their relationships, details logic functions of the circuit and individual schematics for each unit type and designation. | (IOGP S-727, 7.1.2.5.2, 7.1.3.3.2, 7.1.3.5.6, 7.1.3.5.7, 7.1.4.1.7, 7.1.5.2.5, 7.11.8, 7.15.1, 7.15.12, 7.15.13, 7.15.16, 7.15.17, 7.15.18, 7.15.20, 7.15.4, 7.15.5, 7.15.7, 7.16.1, 7.16.2, 7.16.3, 7.17, 7.18.1, 7.18.3, 7.18.5, 7.18.6, 7.19.6, 7.8.2) | Native | CFIHOS-70000328
S727-IR-33 | Name Plate Drawing | A drawing that depicts the layout, font size, and lettering information for the identification of equipment tag names that will be illustrated on nameplates that will be installed on the individual equipment items. This would include the material of the nameplate and fastening method. | (IOGP S-727, 7.1.4.1, 7.1.5.2.6, 7.13.1) | Native
S727-IR-34 | General Arrangement Drawing | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. Document may contain the following information: a. main dimensions, b. interface connections, c. weight, d. center of gravity, e. withdrawal/installation and maintenance space, f. installation and mounting details, g. lifting arrangement, h. shipping split details, i. elevation views, j. equipment/component cross sectional views. | (IOGP S-727, 7.1.1.8, 7.1.2.5.2, 7.11.8.3.2, 7.14, 4.2, 7.1.1.11, 7.1.1.3.2, 7.1.1.5, 7.1.1.8, 7.1.3.14, 7.1.4.1.8, 7.1.5, 7.11.8, 7.12.1, 7.15.7, 7.17, 7.19.6, 7.19.7, 7.8.2) | Native | CFIHOS-70000153
S727-IR-35 | Detailed Drawing | Drawing or detail illustrating parts of a construction or a component, generally enlarged, and including specific information about the form and construction or about the assembly and joints. Also supports other documents where a cross-sectional view, side view or part list is necessary for clarity. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. These details may be part of another drawing or included in a document. The details necessary include: bus bar splices or connections, bus bar torqueing requirements, cable termination hole patterns, cable gland plate locations, floor mounting details including hold down bolt locations and sizes, side views of bus duct and cable bus connections, views for ventilation covers or filter locations, arc resistance construction installation details (space above, cable entry, plenum requirements), other details for regulatory compliance certificates (tilt and roll requirements, drip shield, hand rails, guard rails, seismic installation details). | (IOGP S-727, 7.1.1.8, 7.1.3.3.2 , 7.1.3.3.5, 7.11.8.3.2, 7.1.1.11, 7.1.1.3, 7.1.1.5, 7.1.1.8, 7.1.1.9, 7.1.2.2.4, 7.1.2.5, 7.1.3.3.5, 7.1.3.5.6, 7.1.3.5.7, 7.1.5.2.5, 7.11.8, 7.12.1, 7.15.12, 7.15.13, 7.15.17, 7.15.18, 7.15.20, 7.15.8, 7.16.1.4, 7.16.3.1, 7.17, 7.19.8) | Native | CFIHOS-70000116
S727-IR-36 | Equipment Specification Sheet | A specification or drawing that describes the physical equipment and technical details for the purpose of procurement or fabrication. It Compliments the datasheet. This includes, but is not limited to, details such as: a. all busing details including ratings, plating, and insulation requirements; b. space heater requirements; c. incoming and outgoing cable requirements; d. shipping split arrangements; e. voltage and current ratings including ambient conditions; f. specific application requirements (arc resistance construction features, marine/offshore, regulatory, etc.); g. incomer type and details; h. metering, protective relaying, and overload type details; i. communication, networking, and CBM requirements; k. dimensional data needed to perform arc flash incident energy calculations (IEEE1584): - between each phase of the horizontal bus; - between each phase of the vertical bus; - between each phase of conductors terminating on the line side of the unit overcurrent protection devices (for each rating provided); - size of the unit (this can be the smallest unit provided). | (IOGP S-727 Table 1, Table 2, 4.1, 4.2, 5.3, 5.4, Table 5, 7.1.1.3.3, 7.1.2.5.2, 7.14, 7.1.1.11, 7.1.1.3.2, 7.1.1.3.3, 7.1.1.9, 7.1.2.2.4, 7.1.2.5, 7.1.5, 7.1.6.1, 7.1.6.2, 7.4, 7.15, 7.16.1.2, 7.16.1, 7.16.2, 7.16.3, 7.17, 7.18.4, 7.8.2) | PDF | CFIHOS-70000399
S727-IR-56 | Communication Network Overview | The communication overview is a general description of the information flowing through the interconnected network between the devices. Mandatory content of information includes architecture drawings and major equipment items e.g. protocol converters, data aggregators, controllers, etc. | (IOGP S-727 7.1.3.3.5, 7.17.1, 7.1.3.3.5, 7.11.8.3.1, 7.15.15, 7.17.1, 7.19.5.1, 7.19.5.2, 7.19.5.3) | PDF | CFIHOS-70000118
S727-IR-37 | Communication Block Diagram | The communication block diagram depicts the interconnected networks, cables and connections. Mandatory content of information includes: a. direction of main interfaces between communication equipment items; b. denomination of incoming and outgoing communication circuits; c. communication protocol designations and details (e.g. routers, hubs, ports, switches). | (IOGP S-727 7.1.3.3.5, 7.17.1, 7.1.3.3.5, 7.11.8.3.1, 7.15.15, 7.17.1, 7.19.5.1, 7.19.5.2, 7.19.5.3) | Native | CFIHOS-70000237
S727-IR-38 | Cable Size Calculation | Calculations required for sizing of power cables internal to the LV switchgear (e.g. cable connections from incoming breaker to main bus, internal transformer feed, transition section, etc.). This would be required if a temperature rise test for the specific application is not available. | (IOGP - S-727, 7.1.1.3.3, 7.12, 6.3.1.1) | PDF | CFIHOS-70000034
S727-IR-61 | CT Burden Calculations | CT burden calculations must include metering and relaying devices burden ratings for all devices associated with each circuit. | (IOGP S-727, 7.16.3.3) | PDF
S727-IR-39 | Heat Dissipation Calculation & Loads | This document contains the calculation by the supplier to arrive at the heat load produced by the LV Switchgear to enable HVAC sizing and includes load factors and type of load provided to the supplier to produce accurate calculation. | (IOGP S-727, Annex B) | PDF
S727-IR-40 | Reliability & Availability Calculations and Obsolescence Plan | Demonstrates starting and operating reliability / availability of purchased equipment (e.g. mean time between failure data) calculations. This also provides details of the equipment obsolescence plan. | (IOGP S-727, 4.3.1, 4.3.2, 4.4.1, 4.4.2, 4.4.3) | PDF | CFIHOS-70000312
S727-IR-41 | Certificate Of Conformance | A statement of conformity where attestation is performed by the person or body that is independent of the person or organization that provides the object, and of user interests in that object (third party). This includes the UL 1558 certification (listing mark). | (IOGP S-727, 4.1, 7.1.5, 7.1.6.1, 7.1.6.2) | PDF | CFIHOS-70000013
S727-IR-42 | Type Test Certificate | The results of test performed to provide evidence that the design meets the arc resistance construction requirements of IEEE C37.20.7-2017, including the methodology used to achieve the arc resistant rating. When specified, type test shall be independently verified by a third party and supported by a Certificate of Conformance. This may also be included in the UL 1558 certificate of conformance. NOTE: UL witnessing of the manufacturers' arc resistance tests does not satisfy this requirement. | (IOGP S-727, 6.2.1 6.2.2, 6.2.3, 6.2.4, 7.1.5.12, 7.1.5.2, 7.1.5.3, 7.1.5.4, 7.1.6.1, 7.19.6) | PDF | CFIHOS-70000013
S727-IR-43 | Regulatory Compliance Certificate | A document certifying conformity to local regulations which accompanies shipment of equipment and/or goods. e.g., Official certificate issued by manufacturer. This would include USCG, ABS, or DNV type certifications or similar designations. | (IOGP S-727, 7.1.6.2) | PDF | CFIHOS-70000079
S727-IR-44 | Application Software | A computer program designed for a specific task or use including configuration, monitoring, diagnostics, and operations of control, protective, and communication devices within the LV switchgear. Examples include trip units, condition based monitoring, microprocessor relays, power quality and metering devices. | (IOGP S-727, 7.19.5.1, 7.19.5.2, 7.19.5.3) | Native | CFIHOS-70000012
S727-IR-45 | Bill Of Materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, and material designations. NOTE: When agreed, it includes details of sub-suppliers. | (IOGP S-727, 4.2, 7.4, 7.1.2.5.2, 7.1.3.14, 7.1.3.5.6, 7.1.3.5.7, 7.1.5.7, 7.11.8.3.1, 7.11.8.4.2, 7.15, 7.16.1, 7.16.2, 7.16.3, 7.17, 7.18, 7.19, 7.8.2) | Native | CFIHOS-70000028
S727-IR-46 | Spare Part List | Table containing a list of items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for later use. Mandatory content of information: a. item reference number (BOM); b. quantity; c. part number; d. part name. | (IOGP S-727, 7.1.5.7) | PDF | CFIHOS-70000374
S727-IR-47 | Commissioning Instruction | Instruction providing information on the commissioning of the product. Instructions for commissioning are provided especially for large and highly complex products and for large industrial installations. The purpose of such instructions is to provide the user with the information needed for initial setting-up of the product. These instructions should contain information on how to download the configuration program, software operating instructions, identify the specific checks / tests to be performed before connection to the power system before first operation. NOTE: Unless otherwise agreed, can be delivered as part of manufacturers' standard Installation, operation and maintenance manual or as a standalone document | (IOGP S-727, 7.1.2.5.2, 7.20.5) | PDF
S727-IR-48 | Installation Manual | Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. NOTE: Unless otherwise agreed, can be delivered as part of manufacturers' standard Installation, operation and maintenance manual or as a standalone document. | (IOGP S-727, 7.1.2.5.2, 7.14, 4.3.2, 4.4.2, 7.1.2.5.2, 7.1.3.14, 7.1.5.10, 7.1.5.11, 7.1.5.5, 7.1.5.6, 7.1.5.7, 7.11.8.2, 7.11.8.3, 7.11.8.3.2, 7.15, 7.16.1.2, 7.16.1.4, 7.16.2.3, 7.16.2.6, 7.16.3.1, 7.16.3.5, 7.16.3.7, 7.17, 7.18, 7.19, 7.20) | PDF | CFIHOS-70000181
S727-IR-49 | Maintenance Manual | Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package supplier. Additional information should include obsolesce guidance such can be found in IEC 62402 (an example of an obsolescence management guide). NOTE: Unless otherwise agreed, can be delivered as part of manufacturers' standard Installation, operation and maintenance manual or as a standalone document. | (IOGP S-727, 7.1.2.5.2, 7.14, 4.3.2, 4.4.2, 7.1.2.5.2, 7.1.5.10, 7.1.5.11, 7.1.5.5, 7.1.5.6, 7.1.5.7, 7.11.8.2, 7.11.8.3, 7.11.8.3.2, 7.15, 7.16.1.2, 7.16.1.4, 7.16.2.3, 7.16.2.6, 7.16.3.1, 7.16.3.5, 7.17, 7.18, 7.19, 7.20) | PDF | CFIHOS-70000206
S727-IR-50 | Operating Manual | Description of methods of operating a piece of equipment or process unit, including but not limited to instructions, procedures, drawings, tables, etc. for the operation - energization, switching and isolation. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. This normally includes the cut sheets and technical specification details for the components supplied as part of the LV switchgear assembly. This would also include time current curves (TCC) for the protective devices that can be utilized in the electrical protection coordination studies by others. NOTE: Unless otherwise agreed, can be delivered as part of manufacturers' standard installation, operation and maintenance manual or as a standalone document. | (IOGP S-727, 7.1.2.5.2 7.14, 7.1.2.2.4, 7.1.2.5.1, 7.1.2.5.2, 7.1.2.5.3, 7.1.5, 7.11.8.2, 7.11.8.3.1, 7.11.8.4, 7.11.8.4.1, 7.11.8.4.2, 7.11.8.4.3, 7.15.10, 7.15.12, 7.15.14, 7.15.15, 7.15.16, 7.15.17, 7.15.18, 7.15.3, 7.15.5, 7.15.7, 7.15.8, 7.15.9, 7.16.1.2, 7.16.1.4, 7.16.2.3, 7.16.2.6, 7.16.3, 7.17, 7.18, 7.19, 7.20.6, 7.8.2) | PDF | CFIHOS-70000228
S727-IR-51 | Factory Acceptance Test (FAT) Procedure | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document shall include all testing activities and their acceptance criteria according to applicable standards, specifications and requirements,. to document the condition of the equipment as tested from factory. Test set-up and test equipment is shall be defined. Suppliers standard (routine) test procedures should be used as far as possible. This will include all the functional tests as specific in the technical specification. | (IOGP S-727, 6.3.1.2, 6.3.1.3, 6.3.5.1, 6.3.5.3, 6.3.5.4, 7.1.2.5.2, 7.11.8.3.2, 7.4, 7.11.8.2, 7.11.8.3, 7.11.8.4, 7.12.1, 7.15.12, 7.15.17, 7.15.18, 7.16.2.3, 7.17, 7.19.6, 7.8.2.2, 7.8.2.3, 7.8.2.4) | PDF
S727-IR-52 | Routine Test Procedure | Procedure documenting the manufacturers' recommended testing activities and acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Procedure to define test set-up and test equipment. | (IOGP S-727, 6.3.1.2, 7.11.8.3.2, 7.11.8, 7.12.1, 7.15.12, 7.15.17, 7.15.18, 7.16.2.3, 7.17.1, 7.17.10, 7.17.11, 7.17.12, 7.17.14, 7.17.2, 7.17.3, 7.17.9, 7.19.6.1, 7.19.6.2, 7.19.6.3, 7.8.2) | PDF
S727-IR-53 | Factory Acceptance Test (FAT) Records | The FAT report will be used to verify that the equipment has been tested according to FAT procedure and to demonstrate technical acceptability of the equipment to meet the requirements of this specification. This document shall include all testing activities and their acceptance criteria according with the FAT procedure, to applicable standards, specifications and requirements to document the condition of the equipment as tested from factory. Test set-up and test equipment shall be defined. All equipment that was disconnected to facilitate the AC dielectric tests (Clause 6.3.2) and reconnected afterwards shall be documented in the FAT report. This documentation also includes the punch list or deficiency list that contains all the items that require replacement/repair activity that are identified during the FAT. These items, depending on the degree of severity or impact to the operability of the equipment, may create a hold point prior to the release for shipment. | (IOGP S-727, 6.3.1, 6.3.1.3, 6.3.3, 6.3.4, 6.3.5, 6.4, 7.1.2.5.2, 6.3.1.1, 6.3.1.2, 6.3.1.3, 7.17.6) | PDF
S727-IR-54 | Packing List | A detailed list of the equipment being packaged and shipped. | (IOGP S-727, 7.19.1, 7.19.2, 7.19.3, 7.19.4) | PDF | CFIHOS-70000269
Purchase Order Specific Information Requirements

## Back Cover
Month XXXX

## Drop-down Lists (hidden)
Requirements Sheet Drop-down Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col K
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Sheet Drop-down Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
-
Name | Definition | Example | Identifier / Mandatory / Optional | CFIHOS unique id |  | (Period) | Long description
Document number | The document master to which this revision is related | Example : KC01-71-990-KW-T-YP-0002-000 | Identifier | CFIHOS-10000154 |  | WAD | Weeks After Delivery
Document revision code | A code used to identify the content of a document at a certain point in time. | Example: 001 | Identifier | CFIHOS-10000162 |  | WAI | Weeks After Inspection
Document title | A description, in a short and concise manner, of the content of the document | Example : Laydown Area & Pipe Rack North / South | Mandatory | CFIHOS-10000168 |  | WAO | Weeks After Order
Document revision date | The date the document was revised | Example : 01-01-2006 | Mandatory | CFIHOS-10000076 |  | WAO (Monthly) | Weeks After Order Monthly
Originator company | The name of the company who has generated the document revision | Example : Engineering and co Ltd | Mandatory | CFIHOS-10000077 |  | WAT | Weeks After Test
Document revision author | The name of the person who created the document revision | Example : John Stephen | Optional | CFIHOS-10000078 |  | WPTD | Weeks Prior To Delivery
Document revision approver | The name (or the User ID) of the person who has approved the document revision | Example : Marc Brown | Optional | CFIHOS-10000079 |  | WPTF | Weeks Prior to Fabrication
Document revision file name | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. | Example : P-36-03-D-8120-01-D-01.pdf | Optional | CFIHOS-10000080 |  | WPTT | Weeks Prior To Test
Originator document number | The unique identifier for the Document according to the originator document numbering scheme. | Example : ECO-001-0045-978 | Optional | CFIHOS-10000160
Originator document revision code | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. | Example : 00013 | Optional | CFIHOS-10000081
Document status code | The status of the document revision | Example : as built | Mandatory | CFIHOS-10000083
ISO language code | The primary language that the document revision is written in. | Example : EN (English) | Optional | CFIHOS-10000147
Discipline document type short code | At alternate way of identifying uniquely a combination of discipline and document type | Example : MP6067 | Mandatory | CFIHOS-10000207
Project code | The code that identifies the project the document revision refers to. | Example : FPSO B23 | Optional | CFIHOS-10000161
Document revision comment | Any additional comment / explanation for a document revision. | Example : Does not include package A-1001 | Optional | CFIHOS-10000085
Plant code | The plant that the document revision is related to. | Example : 6000 | Mandatory | CFIHOS-10000005
Export control classification | The Export Control Rule that is applicable for the document revision (e.g., ECCN, EAR). | Example : Controlled Content | Optional | CFIHOS-10000086
Transmittal number | The transmittal through which this document revision was communicated. | Example : FFDF-2007-0071-TE-SH-KW-01149 | Optional | CFIHOS-10000087
Security classification | Has been removed from latest version of CFIHOS. I know the Document Working Group were looking at this but believe it is a mistake it has been removed.
Drop-down name​ | Drop-down value​ | Definition​ | CFIHOS ID​
document format​ | Native​ | A native file is the default file format that a software application is designed to work with.​ | CFIHOS-60000835​
document format​ | PDF​ | It is a universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable & indexed. ​ | CFIHOS-60000933​
document format​ | Hardcopy​ | A permanent reproduction, or copy of a data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ | CFIHOS-10000123​
DO NOT USE THE TAB FROM THIS TEMPLATE
USE THE TAB FROM THE JAMA EXPORT
REFER TO JIP33-MAN-GL-05 FOR THE TEMPLATE FORMATTING
Note on K3: Chris Mitchell:
Note on L3: Chris Mitchell: