## Front & Preliminaries
[5 empty] | SPECIFICATION | November
[5 empty] | S-741D | 2021
Procurement Data Sheet for
DC Uninterruptible Power Supplies
(UPS) and Batteries (NEMA PE 5)
Revision history
| VERSION |  | DATE | PURPOSE
| 1 |  | November 2021 | Issued for Use
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-741D Data Sheet for
DC Uninterruptible Power Supplies (UPS)
and Batteries (NEMA PE 5)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
S-741D Data Sheet for
DC Uninterruptible Power Supplies (UPS)
and Batteries (NEMA PE 5)
Introduction
The purpose of this procurement data sheet is to define buyer specific requirements for the procurement of DC UPS and associated batteries in accordance with the following standards, for application in the petroleum and natural gas industries.
a) Chargers: NEMA PE-5 -1997, Utility Type Battery Chargers
b) Batteries:
1) Battery sizing standards:
— IEEE 485, Recommended Practice for Sizing Lead-Acid Batteries for Stationary Applications
— IEEE 1115, Recommended Practice for Sizing Nickel Cadmium Batteries for Stationary Applications
2) Battery performance standards:
— IEC 60896-22, Stationary lead-acid batteries – Part 22: Valve regulated types – Requirements
— IEC 60896-11, Stationary lead-acid batteries – Part 11: Vented types – General requirements and methods of tests
— IEC 62259, Secondary cells and batteries containing alkaline or other non-acid electrolytes – Nickel-cadmium prismatic secondary single cells with partial gas recombination
— IEC 60623, Secondary cells and batteries containing alkaline or other non-acid electrolytes – Vented nickel-cadmium prismatic rechargeable single cells
— IEC 62620, Secondary cells and batteries containing alkaline or other non-acid electrolytes – Secondary lithium cells and batteries for use in industrial applications
This procurement data sheet defines application specific requirements, attributes and options specified by the purchaser for the supply of the equipment. This procurement data sheet may also include fields for supplier-provided information attributes subject to purchaser’s technical evaluation. Additional purchaser supplied documents may also be incorporated or referenced in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
Information, inspection and testing
Purchaser quality and information requirements are respectively defined under the Inspection and testing section and the Documentation section of the procurement data sheet worksheet.
Quality management system
The supplier quality management system shall conform to ISO 9001, ISO 29001, API Specification Q1 or an equivalent quality management system standard.
Order of precedence
The order of precedence (highest authority listed first) of the documents shall be:
a) regulatory requirements;
b) contract documentation (e.g. purchase order);
c) purchaser defined requirements (procurement data sheet);
d) NEMA PE 5, IEEE / IEC battery standards listed above.
JIP33 Specification for Procurement Documents Procurement Data Sheet

## Procurement Data Sheet
Row | S-741D Procurement Data Sheet for DC Uninterruptible Power Supplies (UPS) and Batteries (NEMA PE 5) | [6 empty] | Issue
2 | NEMA PE 5 Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Applicable to : | select |  | select | [5 empty] | select | proposal | purchase
4 |  | General
5 | 6.3 | UPS configuration : | select |  | select | [5 empty] | select | Figure 1 - Single | Figure 2 - Single - with standby | Figure 3 - Duplicate paralleled - dual battery | Figure 4 - Duplicate paralleled - single battery | other
6 | 4.5, 8.6, Annex A.1 | Electrical installation code : | select |  | select | [5 empty] | select | NFPA 70 (NEC) | CSA 22.1 Part 1 (CEC) | other
7 |  | Site conditions
8 | 7.4 | Maximum altitude : | 1000 m (3300 ft) |  | 1000 m (3300 ft) | [5 empty] | select | 1000 m (3300 ft) | other
9 | 7.7 | ASCE/SEI 7-16 compliant seismic design : | not required |  | not required | [5 empty] | select | not required | required
10 | 7.7 | Site location : | input data |  | input data
11 | 7.7 | Seismic certificate : | not applicable |  | not applicable | [5 empty] | select | not applicable | required | not required
12 |  | Application/operating environment : | select |  | select | [5 empty] | select | onshore | offshore-fixed | offshore-floating | marine (ship) | other
13 | 7.7 | Environmental contamination : | not required |  | not required | [5 empty] | select | salt-laden | H2S | salt-laden and H2S | not required | other
14 | A.2 | Certification (marine/offshore) : | not required |  | not required | [5 empty] | select | USCG/ABS | DNV | not required | other
15 |  | Electrical characteristics
16 |  | Input
17 | 4.1, 8.4 Table 1, Table 2 | Rated input voltage : | select | V AC | select | V AC |  |  |  |  | select | 120 | 208 | 240 | 480 | 600 | other
18 | 8.4 | Number of phases : | select |  | select | [5 empty] | select | 3 | 1
19 | 4.3, 4.4, 8.4, 9.1.7 | Rated input current : | input data | A | input data | A
20 | 4.2, 8.4 | Frequency : | 60 | Hz | 60 | Hz |  |  |  |  | select | 60 | 50
21 | 4.13 | System fault current : | input data | kA (SYM) | input data | kA (SYM)
22 |  | Output
23 | 5.1, 5.2, Table 4, Table 5 | Nominal DC output voltage : | select | V DC | select | V DC |  |  |  |  | select | 24 | 48 | 125 | 250 | other
24 | 8.4 | Rated DC output current : | input data | A DC | input data | A DC
25 |  | Maximum load voltage tolerance (% of nominal VDC) : | 112 | % | 112 | % |  |  |  |  | select | 112 | other
26 |  | Minimum load voltage tolerance (% of nominal VDC) : | 80 | % | 80 | % |  |  |  |  | select | 80 | other
27 |  | Rectifier/charger
28 | Annex A.2 | Certification : | UL 1012 |  | UL 1012 | [5 empty] | select | UL 1012 | CSA 22.2 NO 107.2-01 | other
29 |  | AC input isolation (see 'ITEM 1' on attached figures) : | circuit breaker |  | circuit breaker | [5 empty] | select | circuit breaker | fused switch | not required
30 |  | DC output isolation (see 'ITEM 2' on attached figures) : | circuit breaker |  | circuit breaker | [5 empty] | select | circuit breaker | fused switch | not required
31 | 5.6, 7.1, 7.4 | Maximum ambient temperature (rectifier/charger) : | 122/50 | °F/°C | 122/50 | °F/°C |  |  |  |  | select | 122/50 | 149/65 | other
32 | 7.1 | Minimum ambient temperature (rectifier/charger) : | 32/0 | °F/°C | 32/0 | °F/°C |  |  |  |  | select | 32/0 | -40/-40 | other
33 |  | Full load heat rejection rate : | input data | BTU/HR | input data | BTU/HR
34 |  | Recharging time : | 8 | hours | 8 | hours |  |  |  |  | select | 8 | other
35 | 5.14.1 Table 6, 5.4 | Battery eliminator (output filter) : | required |  | required | [5 empty] | select | required | not required
36 | 5.6 | Temperature compensated battery charging and sensor : | not required |  | not required | [5 empty] | select | not required | required (zone 2 / CI/D2 device) | required (unclassified)
37 |  | Automatic equalizing charge : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | required | not required
38 |  | DC UPS enclosure
39 |  | Enclosure, NEMA rating : | NEMA 1 |  | NEMA 1 | [5 empty] | select | NEMA 1 | NEMA 1 gasketed | other
40 | 8.2 | Enclosure accessibility : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | via tools | lock and key
41 | 8.3 | UPS enclosure mounting : | select |  | select | [5 empty] | select | wall-mount | free-standing
42 | 7.6 | Lifting provisions : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | lifting base | lifting eyes | other
43 | 8.1.1, 8.1.2 | Rectifier/charger ventilation class : | class 1 |  | class 1 | [5 empty] | select | class 1 | class 2
44 | 8.2 | Cooling fans replaceable when rectifier/charger on-line : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | required | manufacturer's standard
45 | 8.8.2 | Air inlet dust filters : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | not required | required
46 |  | Space heater : | not required |  | not required | [5 empty] | select | required | not required
47 | 8.6.2 | Rectifier/charger AC cable entry : | top |  | top | [5 empty] | select | top | bottom | side
48 | 8.6.3 | Rectifier/charger DC cable entry : | bottom |  | bottom | [5 empty] | select | bottom | top | side
49 | 8.6.2, 8.6.3 | Cable entry type : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | gland plate
50 |  | Battery disconnect / isolation
51 |  | Internal battery disconnect (see 'ITEM 3' on attached figures) : | select |  | select | [5 empty] | select | circuit breaker | fused switch | not required
52 | 6.5 | Battery under-voltage protection : | not required |  | not required | [5 empty] | select | required | not required
53 |  | Batteries
54 |  | Batteries : | select |  | select | [5 empty] | select | required | not required
55 | 5.1, Table 3, Table 4, Table 5 | Battery type : | select |  | select | [5 empty] | select | lead acid valve regulated (VRLA) - AGM | lead acid valve regulated (VRLA) - Gel | lead acid vented | nickel cadmium - partial gas recombination | nickel cadmium vented | lithium iron phosphate | other
56 |  | Battery configuration : | select |  | select | [5 empty] | select | 1 x 100 % | 2 x 100 % | 2 x 50 % | not applicable | other
57 | Table 5 | Battery sizing standard : | select |  | select | [5 empty] | select | IEEE 485 (lead acid) | IEEE 1115 (nickel cadmium) | consult battery manufacturer for lithium iron phosphate | other
58 | Table 5 | Battery performance standard : | select |  | select | [5 empty] | select | IEC 60896-22 (valve-regulated lead-acid) | IEC 60896-11 (vented lead-acid) | IEC 62259 (nickel cadmium - partial gas recombination) | IEC 60623 (vented nickel cadmium) | IEC 62620 (Lithium Iron Phosphate - consult battery manufacturer) | other
59 |  | Battery design life : | 10 | years | 10 | years |  |  |  |  | select | 10 | 20 | other
60 |  | Duty cycle description/diagram : | select |  | select | [5 empty] | select | attached diagram | see Supplement tab (tabular form) | not provided (see continuous load and backup time)
61 |  | Continuous load current : | input data | A DC | input data | A DC
62 |  | Backup time : | 30 | min | 30 | min |  |  |  |  | select | 30 | 60 | 120 | other
63 | Table 5 | Battery ambient temperature : | 25 | °C | 25 | °C |  |  |  |  | select | 25 | other
64 |  | Battery design margin : | 1 |  | 1 | [5 empty] | select | 1.00 | 1.10 | 1.15 | other
65 |  | Battery aging factor : | 1.25 |  | 1.25 | [5 empty] | select | 1.25 | other
66 |  | Battery rated capacity : | input data | Ah | input data | Ah
67 | 5.1, Table 5 | Battery float voltage : | input data | V/cell | input data | V/cell
68 | 5.1, Table 5 | Battery equalize voltage : | input data | V/cell | input data | V/cell
69 |  | Battery mounting : | rack mount |  | rack mount | [5 empty] | select | rack mount | cabinet (integral to charger) | cabinet (remote from charger) | battery box | other
70 |  | Battery spill containment : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | corrosion resistant tray | absorbent pad | not required
71 |  | Remote battery cabinet lockable : | not applicable (for rack mount) |  | not applicable (for rack mount) | [5 empty] | select | required | not required | not applicable (for rack mount)
72 |  | Deferred delivery : | not required |  | not required | [5 empty] | select | required | not required
73 |  | Battery monitoring and testing system
74 |  | Online battery monitoring : | not required |  | not required | [5 empty] | select | required | not required
75 |  | Battery capacity testing : | not required |  | not required | [5 empty] | select | not required | provisions for load bank testing | online load testing
76 |  | DC panelboard
77 |  | DC distribution panelboard : | not required |  | not required | [5 empty] | select | required | not required
78 |  | Certification : | not applicable |  | not applicable | [5 empty] | select | UL 67 | CSA 22.2 NO 29 | other(s) | not required | not applicable
79 |  | Enclosure type : | not applicable |  | not applicable | [5 empty] | select | NEMA 1 | NEMA 1 gasketed | not applicable | other
80 |  | Number of circuits : | input data |  | input data
81 |  | Main circuit breaker : | not applicable |  | not applicable | [5 empty] | select | required | not required | not applicable
82 |  | Branch circuit protection : | not applicable |  | not applicable | [5 empty] | select | circuit breakers | fuses | not applicable
83 |  | Controls monitoring and communications
84 | 6.1 | User interface : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | HMI | LED (indicators and meters)
85 | 6.1 | Indication (base level includes system normal, AC failure, DC failure, high Vdc, low Vdc, positive(+) ground fault, negative(-) ground fault) : | base level |  | base level | [5 empty] | select | base level | base level + additional
86 |  | Metering (base level includes DC amps/volts) : | base level |  | base level | [5 empty] | select | base level | base level + additional
87 | 6.9 | Supervisory (common) alarm : | 1 |  | 1 | [5 empty] | select | 1 | 2
88 |  | Communications interface : | not required |  | not required | [5 empty] | select | ethernet (RJ-45) | fiber | wireless (WiFi) | RS485 | other | not required
89 |  | Communication protocol : | not required |  | not required | [5 empty] | select | Modbus RTU (RS-485) | Modbus TCP/IP | Profibus (RS-485) | IEC61850 | other | not required
90 |  | Tagging and nameplates
91 | 8.4 | Additional nameplate information : | not required |  | not required | [5 empty] | select | not required | required (list in Supplement tab)
92 |  | Inspection and testing
93 | 9.2 | Production tests : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | NEMA PE 5 9.2 | not required
94 |  | Functionality tests : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | required-not witnessed | required - witnessed
95 |  | Full load heat run duration : | manufacturer's standard | hours | manufacturer's standard | hours |  |  |  |  | select | manufacturer's standard | 6 | 12 | 24 | other | not required
96 |  | Battery capacity test (purchaser site) : | not required |  | not required | [5 empty] | select | vented lead acid per IEEE 450 | VRLA per IEEE 1188 | nickel cadmium per IEEE 1106 | other battery type/standard | not required
97 |  | Shipping
98 | 7.6 | Packaging : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | NEMA PE 5 7.6 | other
99 |  | Documentation (PDF Format)
100 |  | Product data sheets (rectifier/charger, DC panel, batteries and accessories) : | select |  | select | [5 empty] | select | required - proposal | not required
101 | 9.1 | Type test certificate per NEMA PE 5, 9.1, items a to s : | not required |  | not required | [5 empty] | select | not required | required - proposal
102 | A.2 | Certifications (see rows 14 and 28) : | not required |  | not required | [5 empty] | select | not required | required - proposal
103 | 10.1, Table 10 | Rectifier/charger general arrangement drawings : | required - proposal + design approval + as-built |  | required - proposal + design approval + as-built | [5 empty] | select | required - proposal + design approval + as-built | not required
104 |  | Battery rack general arrangement drawings : | required - proposal + design approval + as-built |  | required - proposal + design approval + as-built | [5 empty] | select | required - proposal + design approval + as-built | not required
105 |  | Wiring and interconnection drawings : | required - design approval + as-built |  | required - design approval + as-built | [5 empty] | select | required - design approval + as-built | not required
106 |  | Battery sizing calculations : | required - design approval + as-built |  | required - design approval + as-built | [5 empty] | select | required - design approval + as-built | not required
107 |  | Battery gas evolution calculations (as applicable) : | required - design approval + as-built |  | required - design approval + as-built | [5 empty] | select | required - design approval + as-built | not required
108 |  | Test reports (as per 'Inspection and Testing', see rows 93, 94, 95 and 96) : | required - after test |  | required - after test | [5 empty] | select | required - after test | not required
109 | 10.1, Table 10 | Instruction manuals for rectifier/charger (as per NEMA PE 5 Table 10) and batteries : | required - prior to delivery |  | required - prior to delivery | [5 empty] | select | required - prior to delivery | not required
110 | Annex A.3 | Maintenance manual (rectifier/charger and batteries) : | required - prior to delivery |  | required - prior to delivery | [5 empty] | select | required - prior to delivery | not required
111 | Annex A.3 | Handling and storage instructions : | required - shipment |  | required - shipment | [5 empty] | select | required - shipment | not required
Note on C3: Select the stage of procurement for which this data sheet is being issued.
Note on C5: Select the UPS configuration. Refer to Figure 1 to Figure 4 tabs. If 'other' is selected, provide the configuration diagram.
Note on C6: Select the applicable local installation code. If 'other' is selected, enter the installation code in the 'Additional notes' column.
Note on C8: Select the site maximum altitude. The default value is ≤ 1000 m (3300 ft). If 'other' is selected, use the 'Additional notes' column to indicate the value (if the value greater than 1000 m (3300 ft)).
Note on C9: Select if seismic design is required per ASCE/SEI 7-16. Purchaser to include the seismic design basis / requirements reference document number within the 'Additional notes' column.
Note on C10: If a seismic design is required, provide the site physical address or latitude and longitude to determine the seismic acceleration.
Note on C11: Indicate if a seismic certificate by a third party is required.
Note on C12: Select the operating environment for the DC UPS. If 'other' is selected, enter details in the 'Additional notes' column.
Note on C13: Select the contaminant exposure to the DC UPS. If 'other' is selected, enter the contaminant exposure in the 'Additional notes' column.
Note on C14: Select the certification requirements (in addition to NRTL or ACO). If 'other' is selected, enter the additional certification in the 'Additional notes' column.
Note on C17: Select the rated input voltage. If 'other' is selected, specify the value in 'Additional notes' column. If 50Hz is selected, indicate in 'Additional notes' column applicable 50Hz voltage from NEMA PE 5, Table 2.
Note on C18: Select the number of phases for the input power supply.
Note on C19: Supplier to provide the rated input current of the rectifier/charger.
Note on C20: Select the input voltage frequency.
Note on C21: Specify the input system RMS symmetrical fault current level at the point of connection.
Note on C23: Select the nominal voltage of the DC rectifier/charger and the battery. If 'other' is selected, specify the value in the 'Additional notes' column.
Note on C24: For new rectifier/charger installations, supplier to provide rated DC output current based on the load and battery recharge requirements. For a replacement rectifier/charger, purchaser to provide rectifier/charger rated DC output current.
Note on C25: Maximum range of nominally rated voltage for design in which the battery is equalized while connected to the load; voltages do not include transient events. See IEEE 946, Table 2.
Note on C26: Minimum range of nominally rated voltage for design in which the battery is equalized while connected to the load; voltages do not include transient events. See IEEE 946, Table 2.
Note on C28: Select the certification requirements. If 'other' is selected, enter the required certification in the 'Additional notes' column. Manufacturers may propose an alternate certification.
Note on C29: Indicate protection / disconnection means on the input to the rectifier/charger. See Figure 1 to Figure 4, 'ITEM 1'.
Note on C30: Indicate protection / disconnection means on the output of the rectifier/charger. See Figure 1 to Figure 4, 'ITEM 2'.
Note on C31: Specify the maximum operating ambient temperature. The default value is 122 °F (50 °C). If 'other' is selected, enter the required temperature in the 'Additional notes' column.
Note on C32: Specify the operating minimum ambient temperature. the default value is 32 °F (0 °C). If 'other' is selected, enter the required temperature in the 'Additional notes' column.
Note on C33: Supplier to indicate the full load heat rejection rate. Use 'Additional notes' column if unit other than BTU/HR is used.
Note on C34: The time to recharge to 90 % capacity a discharged battery within the specified hours while supplying the full DC load. Full load to be determined by the duty cycle description/diagram. Longer recharge times may reduce cost.
Note on C35: Select if the rectifier/charger is required to supply the load with the battery disconnected. The battery eliminator provides additional filtering when the battery is disconnected.
Note on C36: Temperature compensation is generally required for VRLA batteries or when rectifiers/chargers and batteries are not located within the same ambient conditions.
Note on C37: If required, the equalize charge is automatically applied after power interruption.
Note on C39: If 'other' is selected, specify the value in the 'Additional notes' column.
Note on C40: A means to limit access into the enclosure to qualified personnel.
Note on C41: Select the UPS mounting option. Purchaser to verify the mounting weight if 'wall-mount' is selected.
Note on C42: Select the DC UPS lifting and handling requirements. This may be required for larger free-standing units. If 'other' is selected, enter the required lifting provisions in the 'Additional notes' column.
Note on C43: Purchaser to specify the ventilation class - class 1 for natural convection and radiation or class 2 for rectifier/chargers that allow the use of fans or cooling devices.
Note on C44: If rectifier/charger cooling fans are required (Class 2), purchaser to indicate whether fans should be replaceable with the rectifier/charger online without exposure to unguarded energized components.
Note on C45: Select the air inlet filter requirement. Dust particle filter size to be manufacturer's standard.
Note on C46: If condensation or high humidity is expected in the environment of operation, a space heater should be considered. Space heater to include necessary controls (e.g. thermostat and indicator).
Note on C47: Select the rectifier/charger AC input cable entry. The AC cable entry is to be as near as possible to the AC connection terminals.
Note on C48: Select the rectifier/charger DC input cable entry. The DC cable entry is to be as near as possible to the DC connection terminals.
Note on C49: Select whether the cable gland plate is required. If required, the purchaser can provide information on pre-drilled holes and non-magnetic material requirements.
Note on C51: Select the requirement for the battery disconnect internal to the DC UPS according to UPS configuration selected.
Note on C52: If a circuit breaker is selected for 'internal battery disconnect', the battery under-voltage protection can be selected to isolate battery on minimum voltage or to prevent damage to battery.
Note on C54: If required, supplier to include batteries in their scope of supply.
Note on C55: Select the battery type suitable for the application and the environment.
Note on C56: Select the configuration of the battery. If 'other' is selected, enter the required configuration in the 'Additional notes' column.
Note on C57: Select the battery sizing standard based upon the battery type. If 'other' is selected, indicate the battery sizing standard in the 'Additional notes' column.
Note on C58: Select the battery performance standard based upon the battery type. If 'other' is selected, indicate the battery performance standard in the 'Additional notes' column.
Note on C59: Purchaser to specify the design life of the batteries. The 10 years default is based on typical lead acid battery. Longer life may be achieved or selected by different battery technologies. Use the 'Additional notes' column for 'other'.
Note on C60: Provide a description/diagram of the battery duty cycle (for continuous, non-continuous, and momentary loads with desired output current for specified duration). Refer to IEEE 485 or IEEE 1115 for additional guidance.
Note on C61: If the duty cycle description/diagram is not provided, specify the continuous load current.
Note on C62: If the duty cycle description/diagram is not provided, specify the battery backup time in minutes. If 'other' is selected, specify the value in the 'Additional notes' column.
Note on C63: Select the battery ambient temperature. If 'other' is selected, specify the value in the 'Additional notes' column.
Note on C64: Design margin (as used in battery sizing standards) to allow for future growth and less than optimum operating conditions. If 'other' is selected, specify the value in the 'Additional notes' column.
Note on C65: Battery aging factor to maintain the battery capacity throughout its service life. If 'other' is selected, specify the value in the 'Additional notes' column.
Note on C66: Supplier to indicate the battery rated capacity. Purchaser to indicate the battery rated capacity (for information) in case the battery is not included in the scope.
Note on C67: Supplier to provide the battery float voltage in V/cell.
Note on C68: Supplier to provide the battery equalize voltage in V/cell.
Note on C69: If batteries are included in scope, select the battery installation arrangement. If 'other' is selected, specify the value in the 'Additional notes' column.
Note on C70: Spill containment is typically provided for vented lead acid batteries.
Note on C71: When a remote battery cabinet is provided, lock measures can be selected.
Note on C72: If a long lead time is required between the build of the UPS and the installation of the battery, indicate the length of time in the 'Additional notes' column.
Note on C74: If battery monitoring system is selected, purchaser to provide details of functionality (monitored parameters such as: per cell voltages, temperatures, impedances) in the Supplement tab.
Note on C75: Select provisions for load bank testing if the supplier is to provide connections for external load bank provided by others. Select 'online load testing' if the supplier is to provide a rectifier/charger capable of using connected load to test batteries.
Note on C77: If required, supplier to include a panelboard(s) in their scope of supply. Panelboard may be standalone or integrated in the rectifier/charger cabinet.
Note on C78: If a panelboard is included in the scope, select the certification standard. If 'other(s)' is selected, enter the required certification in the 'Additional notes' column. Manufacturers may propose an alternate certification.
Note on C79: If a panelboard is included in the scope, select the enclosure type. The typical enclosure type is NEMA 1. If 'other' is selected, specify the value in the 'Additional notes' column.
Note on C80: If a panelboard is included in scope, indicate the number of DC circuits. Refer to project documents for individual circuit ratings.
Note on C81: If a panelboard is included in the scope, indicate if a main circuit breaker is required.
Note on C82: If a panelboard is included in the scope, indicate if branch circuit protection is provided by circuit breakers or fuses.
Note on C84: Indicate the type of user interface to be provided. User interfaces typically provide unit status, metering, alarms and indication, controls or mimic displays.
Note on C85: Minimum status indicators to be integrated into the HMI or as discrete LEDs as noted. If 'base level + additional' is selected, list the additional indications in the 'Additional notes' column.
Note on C86: Minimum metering to be integrated into the HMI or as discrete meters as noted. If 'base level + additional ' is selected list the additional metering in the 'Additional notes' column.
Note on C87: Common supervisory alarm contact (Form C), minimum.
Note on C88: Select the communication media type. If 'other' is selected, specify the details in the 'Additional notes' column.
Note on C89: Specify the communication protocol (e.g. modbus, modbus TCP/IP, profibus). If 'other' is selected, specify the value in the 'Additional notes' column.
Note on C91: Use the Supplement tab to specify additional nameplate requirements not included in NEMA PE 5, paragraph 8.4, for example additional customer or project specific information.
Note on C93: Purchaser to select the required production test. If NEMA PE 5, 9.2 is selected tests are inclusive of items a to d. If witnessing is required, purchaser to specify in the "Additional Notes" column.
Note on C94: Purchaser to indicate additional production tests such as: functionality of controls, meters, indicators and alarms.
Note on C95: Purchaser to specify the full load heat run test duration in hours. If 'other' is selected, specify the test hours in the 'Additional notes' column.
Note on C96: Load test is at the purchaser's site. If required, the load test should be in the scope of service. If other than lead acid or nickel cadmium battery, customer and supplier to agree on the test procedure. Use the 'Additional notes' column for 'other'.
Note on C98: Purchaser to select required packaging for shipment. If 'other' is selected record in the 'Additional notes' column. Examples include weatherproof packaging and special crating.
Note on C100: This is the manufacturer's product data sheet.
Note on C101: Supplier to include type test certificate with proposal as per NEMA PE 5 9.1 items a to s if specified.
Note on C102: Purchaser to indicate the certification documents required (e.g. rectifier/charger certification, additional certifications (marine/offshore)). Use the 'Additional notes' column to list the documents.
Note on C103: Dimensional information for rectifier/charger cabinet(s), weights, cable connection locations, etc. Use the 'Additional notes' column to indicate the timing for deliverables, i.e. number of weeks after order (design approval) and prior to delivery (as-built).
Note on C104: Dimensional information for battery rack/cabinet(s), weights, cable connection locations, etc. Use the 'Additional notes' column to show the timing for deliverables, i.e. number of weeks after order (design approval) and prior to delivery (as-built).
Note on C105: Wiring and interconnect drawings are to define customer connections and interfaces. Use the 'Additional notes' column to indicate the timing for deliverables, i.e. number of weeks after order (design approval) and prior to delivery (as-built).
Note on C106: Supplier to provide a copy of the calculations used to size the battery. Use the 'Additional notes' column to indicate the timing for deliverables, i.e. number of weeks after order (design approval) and prior to delivery (as-built).
Note on C107: Supplier to provide a copy of the calculations used determine the gas evolution. Use the 'Additional notes' column to indicate the timing for deliverables, i.e. number of weeks after order (design approval) and prior to delivery (as-built).
Note on C108: Supplier to submit the completed test reports. Use the 'Additional notes' column to indicate the timing for deliverables, i.e. number of weeks after test.
Note on C109: Rectifier/charger and battery installation and instruction manuals. Use the 'Additional notes' column to indicate the timing for deliverables, i.e. number of weeks prior to delivery.
Note on C110: Indicate the type of maintenance procedures, tools and schedule to properly maintain the rectifier/charger and batteries. Use the 'Additional notes' column to indicate the timing for deliverables, i.e. number of weeks prior to delivery.
Note on C111: Use the 'Additional notes' column to indicate the timing for deliverables, i.e. number of weeks prior to delivery.

## Figure 1
S-741D — Figure 1

## Figure 2
S-741D — Figure 2

## Figure 3
S-741D — Figure 3

## Figure 4
S-741D — Figure 4

## Supplement
Row | S-741D Procurement Data Sheet for DC Uninterruptible Power Supplies (UPS) and Batteries (NEMA PE 5) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
9
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Guidance
S-741D Procurement Data Sheet for
DC Uninterruptible Power Supplies (UPS) and Batteries (NEMA PE 5)
Guidance on the use of this procurement data sheet
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data

## Back Cover
Month XXXX
Copy for SC Approval